## Comparison of Data to BAA
Comparison of Spreadsheet Data to Installation Profile Table in the Broad Agency Announcement (BAA) Full Proposal Instructions
Data Field | Value in BAA Instructions | Value in Current Spreadsheet | Comments
PV Project Capacity (kW-AC) | 1200 | 1200 | N/A
Total Peak Demand (kW-AC) | 24000 | 23965 | N/A
(Peak) Critical Load (kW-AC) | 4400 | 4410 | N/A
Portion of Critical Load Requiring Ride-Through (kW-AC) | 2000 | 2000 | N/A
Total Annual Electricity Cost (not including PV costs) | $7.1 million | $7.1 million | N/A
Note: By applying the electricity bill components in this spreadsheet to the hourly installation electricity consumption
in the spreadsheet, total annual electricity cost should be nearly the same as in the BAA full proposal instructions.
Awardees can assume that PV production will be purchased at the same rate as conventional grid electricity.

## NASCorpusChristi
Time stamp | Gross Total Electricity Consumption (kWh) of Critical and Non-Critical Loads Combined (sum of net, utility invoiced consumption and output from the existing 1,200 kW-AC PV system) | Modeled PV Output (kWh), from 1,200 kW-AC Project at the Installation | Real-Time Energy Price ($/MWh), future volatile scenario | Real-Time Energy Price ($/MWh), current scenario | Day-Ahead Energy Price ($/MWh), future volatile scenario | Day-Ahead Energy Price ($/MWh), current scenario | Responsive Reserve ($/MWh), current and future volatile scenarios | Non-Spinning Reserve Price ($/MWh), current and future volatile scenarios | Regulation Down Price ($/MWh), current and future volatile scenarios | Regulation Up Price ($/MWh), current and future volatile scenarios
2018-01-01 | 7918.2042 | -0.048233 | 15.48 | 24.1 | 33.9 | 23.23 | 3.11 | 0.49 | 9.96 | 2.45
2018-01-01 01:00 | 7914.4042 | -0.048233 | 15.18 | 22.07 | 30.56 | 21.82 | 2.25 | 0.01 | 2.11 | 1.85
2018-01-01 02:00 | 7900.1542 | -0.048233 | 15.11 | 21.11 | 21.62 | 20.16 | 2 | 0.01 | 1.5 | 1
2018-01-01 03:00 | 7819.4042 | -0.048233 | 15.05 | 20.23 | 20.33 | 20 | 1.75 | 0.47 | 1.5 | 1
2018-01-01 04:00 | 7827.9542 | -0.048233 | 15.12 | 20.43 | 21.44 | 20.24 | 1.75 | 0.47 | 1.5 | 1
2018-01-01 05:00 | 8742.7341 | -0.048233 | 15.44 | 19.8 | 21.64 | 21.45 | 1.75 | 0.47 | 2.87 | 1.75
2018-01-01 06:00 | 8757.5041 | -0.048233 | 15.68 | 19.71 | 21.73 | 24.35 | 2.25 | 0.5 | 9.11 | 22
2018-01-01 07:00 | 7785.7431 | 9.5191 | 16.63 | 19.8 | 22.04 | 24.06 | 3.25 | 1 | 35 | 40.4
2018-01-01 08:00 | 8035.5598 | 322.484 | 16.86 | 19.44 | 22.56 | 25.48 | 3.01 | 1 | 3.5 | 3.01
2018-01-01 09:00 | 8809.5475 | 375.282 | 17.04 | 19.24 | 31.02 | 24.94 | 2.91 | 1 | 3.01 | 2.91
2018-01-01 10:00 | 9352.5676 | 657.993 | 17.14 | 20.12 | 31.58 | 28 | 3.11 | 1 | 3.01 | 3.1
2018-01-01 11:00 | 8588.551 | 783.58 | 17.68 | 21.06 | 31.51 | 25.06 | 4.02 | 0.9 | 11.03 | 4.02
2018-01-01 12:00 | 9817.4913 | 823.679 | 17.27 | 20.13 | 29.59 | 23.71 | 4.02 | 0.9 | 24 | 3.1
2018-01-01 13:00 | 8615.2735 | 578.709 | 17.49 | 19.82 | 22.48 | 23.26 | 3.71 | 0.9 | 3.01 | 3
2018-01-01 14:00 | 9717.0068 | 560.433 | 17.5 | 19.6 | 22.17 | 24 | 3.45 | 0.9 | 3.45 | 3
2018-01-01 15:00 | 9765.6339 | 517.525 | 17.51 | 19.41 | 23.53 | 23.22 | 2.9 | 0.5 | 2.61 | 2.23
2018-01-01 16:00 | 8393.0685 | 110.809 | 17.5 | 19.23 | 33.3 | 22.95 | 3.01 | 0.5 | 1 | 1.75
2018-01-01 17:00 | 8342.2122 | 20.276 | 18.89 | 19.73 | 43.93 | 42 | 3.46 | 0.5 | 0.51 | 2
2018-01-01 18:00 | 9421.0991 | -0.048233 | 20.61 | 20.61 | 39.22 | 35 | 23.42 | 0.5 | 3 | 23.42
2018-01-01 19:00 | 9425.3191 | -0.048233 | 19.25 | 19.63 | 33.73 | 24.98 | 25.56 | 0.5 | 3 | 24.56
2018-01-01 20:00 | 8480.6042 | -0.048233 | 18.97 | 19.37 | 32.23 | 24.29 | 6.38 | 0.5 | 1 | 3
2018-01-01 21:00 | 9494.9491 | -0.048233 | 18.06 | 18.06 | 31.45 | 23.24 | 5.69 | 0.5 | 2.59 | 3
2018-01-01 22:00 | 8479.6542 | -0.048233 | 17.84 | 18.54 | 22.39 | 20.18 | 4.5 | 0.5 | 3.29 | 3
2018-01-01 23:00 | 8442.6042 | -0.048233 | 16.8 | 16.8 | 22.22 | 17.9 | 3.68 | 0.01 | 15 | 3
2018-01-02 | 8494.8542 | -0.048233 | 17.01 | 17.02 | 32.72 | 17.48 | 3.15 | 0.01 | 14.03 | 2.11
2018-01-02 01:00 | 8455.9042 | -0.048233 | 16.82 | 16.82 | 22.31 | 17.48 | 2.25 | 0.01 | 2.61 | 2.04
2018-01-02 02:00 | 8389.4042 | -0.048233 | 16.82 | 16.83 | 32.78 | 17.07 | 1.77 | 0.01 | 1.57 | 1.11
2018-01-02 03:00 | 9173.1741 | -0.048233 | 8.12 | 8.12 | 32.75 | 16.54 | 1.75 | 0.45 | 1 | 1
2018-01-02 04:00 | 9196.3841 | -0.048233 | 1.82 | 1.82 | 22.85 | 15.81 | 1.75 | 0.45 | 1 | 1
2018-01-02 05:00 | 9283.9491 | -0.048233 | 15.19 | 15.19 | 21.78 | 15.81 | 1.75 | 0.45 | 3.46 | 1.75
2018-01-02 06:00 | 8427.4042 | -0.048233 | 16.96 | 16.96 | 30.77 | 15.95 | 2.5 | 0.45 | 10 | 549.3306
2018-01-02 07:00 | 8551.5372 | 5.6181 | 18.18 | 18.48 | 33.17 | 17.12 | 20.39 | 0.97 | 50.1462 | 43.58
2018-01-02 08:00 | 8753.6601 | 229.379 | 17.89 | 17.89 | 33.08 | 18.53 | 4.77 | 0.97 | 2.61 | 4.77
2018-01-02 09:00 | 10021.8564 | 354.39 | 19.08 | 19.08 | 31.61 | 21.79 | 5.5 | 0.97 | 1 | 3.5
2018-01-02 10:00 | 9736.2595 | 272.682 | 19.84 | 19.84 | 31.58 | 23.51 | 5.01 | 1.05 | 1 | 4.16
2018-01-02 11:00 | 9651.1484 | 220.008 | 19.76 | 19.76 | 31.55 | 24.06 | 5.74 | 0.97 | 35 | 4
2018-01-02 12:00 | 9082.7743 | 467.815 | 19.78 | 19.78 | 29.91 | 24.8 | 5 | 0.97 | 32.41 | 3.3
2018-01-02 13:00 | 9766.361 | 1026.38 | 19.64 | 19.84 | 24.99 | 24.14 | 3.92 | 0.97 | 1.29 | 3
2018-01-02 14:00 | 10793.321 | 865.636 | 18.09 | 19.94 | 23.51 | 24.89 | 3.06 | 0.97 | 3.11 | 2.82
2018-01-02 15:00 | 9196.8417 | 148.886 | 17.5 | 20.63 | 23.72 | 22.32 | 2.11 | 0.5 | 2.61 | 1.7
2018-01-02 16:00 | 10343.5165 | 100.281 | 17.56 | 21.62 | 31.96 | 23.91 | 1.78 | 0.5 | 0.68 | 1.11
2018-01-02 17:00 | 10188.7965 | 16.627 | 19.47 | 22.66 | 38.22 | 50.78 | 2.8 | 0.5 | 0.51 | 2
2018-01-02 18:00 | 10247.1641 | -0.048233 | 21 | 28.13 | 35.76 | 30.58 | 31.36 | 0.5 | 3 | 29.36
2018-01-02 19:00 | 9296.6542 | -0.048233 | 19.85 | 22.31 | 34.1 | 29.85 | 20 | 0.5 | 3 | 16.69
2018-01-02 20:00 | 9141.8042 | -0.048233 | 19.06 | 21 | 36.41 | 27.22 | 20 | 0.5 | 1 | 3
2018-01-02 21:00 | 9921.1691 | -0.048233 | 18.32 | 20.17 | 31.2 | 23.71 | 3.87 | 0.5 | 1 | 3
2018-01-02 22:00 | 8692.4542 | -0.048233 | 17.16 | 19.71 | 21.91 | 18.3 | 41 | 0.5 | 9.11 | 3
2018-01-02 23:00 | 8597.4542 | -0.048233 | 16.95 | 18.64 | 21.71 | 14.77 | 40 | 0.01 | 14.93 | 2.32
2018-01-03 | 8430.2542 | -0.048233 | 16.77 | 17.55 | 21.55 | 11.14 | 2.25 | 0.01 | 12.83 | 1.75
2018-01-03 01:00 | 9283.9491 | -0.048233 | 16.16 | 16.16 | 20.06 | 9.16 | 1.61 | 0.01 | 1 | 1.11
2018-01-03 02:00 | 9219.5941 | -0.048233 | 9.23 | 9.23 | 20.4 | 9.66 | 1.61 | 0.01 | 0.5 | 1
2018-01-03 03:00 | 9247.0241 | -0.048233 | 7.25 | 7.25 | 19.68 | 13.03 | 1.61 | 0.45 | 1 | 0.11
2018-01-03 04:00 | 9493.8941 | -0.048233 | 15.72 | 18.04 | 19.16 | 16.97 | 1.61 | 0.45 | 1 | 1
2018-01-03 05:00 | 9328.0042 | -0.048233 | 16.09 | 18.91 | 20.46 | 21.03 | 1.61 | 0.45 | 3.46 | 1.5
2018-01-03 06:00 | 12221.0691 | -0.048233 | 17.8 | 21.29 | 22.4 | 24.06 | 2.11 | 0.5 | 13.5 | 35.43
2018-01-03 07:00 | 11892.8057 | 3.7428 | 18.77 | 23.31 | 22.41 | 24.11 | 3.26 | 1 | 20 | 40.06
2018-01-03 08:00 | 12227.9107 | 154.485 | 83.75 | 83.75 | 29.71 | 26.68 | 3.44 | 1 | 3.46 | 3.44
2018-01-03 09:00 | 13742.1462 | 212.731 | 46.11 | 46.11 | 32.3 | 25.13 | 3.29 | 0.97 | 3.01 | 3
2018-01-03 10:00 | 12935.58 | 393.4 | 19.68 | 21.76 | 29.02 | 25.21 | 3.39 | 0.99 | 2 | 3.34
2018-01-03 11:00 | 13443.545 | 885.1 | 49.19 | 49.19 | 29.16 | 25.36 | 3.25 | 0.82 | 11.41 | 3.25
2018-01-03 12:00 | 14886.8697 | 605.777 | 55.93 | 55.93 | 29.06 | 26.72 | 2.15 | 0.82 | 3.01 | 2.07
2018-01-03 13:00 | 14377.0125 | 221.5 | 111.29 | 111.29 | 22.1 | 27 | 1.61 | 0.82 | 2.67 | 1
2018-01-03 14:00 | 13437.8251 | 588.275 | 16.17 | 40.08 | 21.92 | 27.68 | 1.61 | 0.82 | 2 | 1
2018-01-03 15:00 | 13013.579 | 381.146 | 89 | 89 | 22.09 | 26.38 | 1.75 | 0.5 | 2 | 1
2018-01-03 16:00 | 11549.149 | 332.999 | 92.52 | 92.52 | 30.5 | 26.24 | 2 | 0.5 | 0.59 | 1
2018-01-03 17:00 | 11271.9198 | 29.1787 | 17.45 | 27.18 | 39.17 | 42.19 | 2 | 0.5 | 0.4 | 1.11
2018-01-03 18:00 | 11087.4042 | -0.048233 | 111.96 | 111.96 | 31.21 | 37.24 | 5.02 | 0.5 | 2 | 19.46
2018-01-03 19:00 | 10880.3042 | -0.048233 | 19.33 | 30.26 | 29.05 | 27.58 | 4.88 | 0.5 | 3.46 | 4
2018-01-03 20:00 | 10626.6542 | -0.048233 | 154.95 | 154.95 | 30.88 | 25.5 | 4 | 0.5 | 1 | 3
2018-01-03 21:00 | 11577.5191 | -0.048233 | 18.72 | 27.28 | 23.38 | 25.28 | 3.38 | 0.5 | 1 | 3
2018-01-03 22:00 | 11121.7591 | -0.048233 | 17.53 | 23.72 | 22.08 | 24.3 | 3.01 | 0.5 | 9.03 | 2.82
2018-01-03 23:00 | 9446.7542 | -0.048233 | 63.95 | 63.95 | 21.83 | 21.91 | 2.25 | 0.01 | 11.98 | 2
2018-01-04 | 9149.4042 | -0.048233 | 16.87 | 29.38 | 20.75 | 21.48 | 2.11 | 0.01 | 10.18 | 1.55
2018-01-04 01:00 | 9959.1491 | -0.048233 | 16.81 | 27.68 | 17.06 | 20.92 | 1.11 | 0.01 | 2.16 | 1.11
2018-01-04 02:00 | 9868.4191 | -0.048233 | 16.6 | 36.28 | 13.07 | 21.04 | 1 | 0.01 | 1 | 1
2018-01-04 03:00 | 8804.5542 | -0.048233 | 16.72 | 25.3 | 13.07 | 22.3 | 1.3 | 0.5 | 1 | 1
2018-01-04 04:00 | 9001.2042 | -0.048233 | 17.19 | 23.72 | 17.67 | 22.9 | 1.61 | 0.5 | 1 | 1.25
2018-01-04 05:00 | 11054.2391 | -0.048233 | 17.94 | 20.99 | 18.54 | 24.92 | 2.25 | 0.5 | 3.11 | 2.25
2018-01-04 06:00 | 12007.0042 | -0.048233 | 22.56 | 22.56 | 31.72 | 44.51 | 3 | 0.5 | 15.09 | 3
2018-01-04 07:00 | 14169.9026 | 9.1873 | 109.79 | 109.79 | 27.94 | 35.64 | 37.02 | 1 | 14.49 | 37.02
2018-01-04 08:00 | 14367.7338 | 371.705 | 114.11 | 114.11 | 23.27 | 30.41 | 16.09 | 10 | 1.21 | 16.08
2018-01-04 09:00 | 14508.8653 | 681.479 | 33.64 | 33.64 | 23.24 | 28.52 | 4.54 | 1 | 1 | 4.3
2018-01-04 10:00 | 13047.8168 | 908.544 | 20.09 | 32.58 | 24.34 | 26.23 | 5 | 1 | 1 | 4.44
2018-01-04 11:00 | 14269.3075 | 1050.41 | 39.48 | 39.48 | 24.1 | 25.16 | 4.75 | 1 | 3.11 | 3.16
2018-01-04 12:00 | 12871.626 | 1090.08 | 18.56 | 30.31 | 23.26 | 25.45 | 3.63 | 1 | 2.61 | 2.61
2018-01-04 13:00 | 13957.1225 | 1006.5 | 66.25 | 66.25 | 23.79 | 24.29 | 2.5 | 1.02 | 2.61 | 2.17
2018-01-04 14:00 | 11415.4384 | 462.251 | 65.15 | 65.15 | 23.86 | 24.12 | 1.75 | 1 | 2.61 | 1.5
2018-01-04 15:00 | 11760.5587 | 186.449 | 59.89 | 59.89 | 24.65 | 23.32 | 2 | 0.5 | 2.61 | 1
2018-01-04 16:00 | 11490.0915 | 208.082 | 16.79 | 22.66 | 33.7 | 25.31 | 2 | 0.5 | 1.26 | 0.68
2018-01-04 17:00 | 10198.7233 | 1.4982 | 17.48 | 22.9 | 42.79 | 36.72 | 2.2 | 0.5 | 0.61 | 1.26
2018-01-04 18:00 | 10173.5042 | -0.048233 | 19.52 | 28.97 | 50.44 | 35.21 | 20 | 0.5 | 2.01 | 16.04
2018-01-04 19:00 | 10026.2542 | -0.048233 | 18.97 | 19.86 | 38.5 | 29.5 | 20 | 0.5 | 3 | 11.86
2018-01-04 20:00 | 9892.3042 | -0.048233 | 17.9 | 19.59 | 33.49 | 24.69 | 5 | 0.5 | 1 | 3
2018-01-04 21:00 | 9662.4042 | -0.048233 | 17.55 | 18.63 | 33.26 | 24.75 | 5 | 0.5 | 1.04 | 2.71
2018-01-04 22:00 | 9412.5542 | -0.048233 | 16.55 | 20.12 | 24.35 | 22.63 | 4.7 | 0.5 | 3.06 | 3
2018-01-04 23:00 | 9238.7042 | -0.048233 | 15.47 | 21.08 | 24.31 | 20.38 | 3.11 | 0.01 | 3 | 2.61
2018-01-05 | 9035.4042 | -0.048233 | 15.33 | 20.29 | 37.68 | 19.71 | 2.13 | 0.01 | 3 | 1.85
2018-01-05 01:00 | 8948.0042 | -0.048233 | 15.76 | 19.35 | 33.97 | 19.54 | 2 | 0.01 | 3.01 | 1
2018-01-05 02:00 | 9904.2891 | -0.048233 | 15.75 | 20.11 | 28.7 | 19.43 | 2 | 0.01 | 2.11 | 1
2018-01-05 03:00 | 8933.7542 | -0.048233 | 16.03 | 19.97 | 19.09 | 20.02 | 2 | 0.47 | 1 | 0.01
2018-01-05 04:00 | 9119.0042 | -0.048233 | 16.88 | 20.64 | 35.55 | 21.02 | 2 | 0.47 | 2 | 1
2018-01-05 05:00 | 11155.5191 | -0.048233 | 17.97 | 21.49 | 39.45 | 23.04 | 2 | 0.48 | 3.5 | 2
2018-01-05 06:00 | 12863.5641 | -0.048233 | 20.56 | 21.68 | 36.29 | 35.46 | 4.31 | 0.47 | 11.3 | 13.75
2018-01-05 07:00 | 12520.9542 | -0.048233 | 21.1 | 24.11 | 38.15 | 33.91 | 100.8141 | 58.3073 | 16.57 | 102.5962
2018-01-05 08:00 | 14038.2162 | 31.3661 | 19.5 | 22.86 | 32.92 | 27.52 | 45.66 | 58.3073 | 2.61 | 45.66
2018-01-05 09:00 | 14267.0182 | 116.24 | 19.47 | 21.74 | 35.82 | 25.74 | 20.7 | 15 | 2.56 | 17.54
2018-01-05 10:00 | 14182.2996 | 149.938 | 19.43 | 20.67 | 36.23 | 24.25 | 5 | 7.02 | 2.3 | 3.1
2018-01-05 11:00 | 13853.3084 | 363.098 | 17.24 | 17.24 | 33.41 | 24.03 | 4.35 | 0.97 | 57.6962 | 1.01
2018-01-05 12:00 | 14062.8145 | 248.682 | 17.72 | 17.72 | 30.16 | 24.18 | 3.43 | 0.97 | 57.6962 | 1
2018-01-05 13:00 | 14036.4743 | 531.715 | 17.96 | 20.29 | 28.56 | 24.43 | 2.68 | 0.97 | 11.11 | 1
2018-01-05 14:00 | 12507.3869 | 210.343 | 17.7 | 18.73 | 24.13 | 24.02 | 2.11 | 1 | 3.46 | 1
2018-01-05 15:00 | 11006.2525 | 204.529 | 13.75 | 13.75 | 28.9 | 23.25 | 2 | 0.61 | 3.11 | 1
2018-01-05 16:00 | 11905.0177 | 123.377 | 15.7 | 15.7 | 38.42 | 23.49 | 2 | 0.74 | 1 | 0.71
2018-01-05 17:00 | 11804.9405 | 30.5171 | 16.31 | 16.31 | 46.12 | 35.05 | 2 | 0.74 | 0.61 | 1
2018-01-05 18:00 | 11684.0741 | -0.048233 | 20.81 | 22.51 | 43.85 | 30.83 | 5.73 | 0.74 | 9.7 | 13.77
2018-01-05 19:00 | 10416.7042 | -0.048233 | 18.93 | 18.93 | 43.33 | 27.16 | 5.64 | 0.97 | 10 | 14.03
2018-01-05 20:00 | 11281.0641 | -0.048233 | 18.7 | 19.23 | 45.25 | 26.38 | 4.76 | 0.74 | 1 | 3
2018-01-05 21:00 | 11091.1641 | -0.048233 | 18.52 | 19.62 | 36.83 | 24.52 | 3.87 | 0.65 | 3 | 3
2018-01-05 22:00 | 9560.7542 | -0.048233 | 17.93 | 19.33 | 29.75 | 23.1 | 2.68 | 0.85 | 9.71 | 1.01
2018-01-05 23:00 | 9197.8542 | -0.048233 | 16.23 | 19.94 | 29.33 | 23.47 | 2.61 | 0.01 | 11.03 | 1
2018-01-06 | 10041.4391 | -0.048233 | 15.01 | 19.97 | 40.82 | 20.12 | 2.61 | 0.01 | 13.27 | 1
2018-01-06 01:00 | 8937.5542 | -0.048233 | 14.39 | 19.44 | 39.53 | 19.74 | 1.89 | 0.01 | 3.01 | 1
2018-01-06 02:00 | 9778.7441 | -0.048233 | 13.53 | 15.68 | 36.15 | 19.77 | 1.89 | 0.01 | 2.61 | 1
2018-01-06 03:00 | 9866.3091 | -0.048233 | 9.75 | 9.75 | 36.15 | 20.18 | 1.61 | 0.3 | 1.75 | 1
2018-01-06 04:00 | 9147.5042 | -0.048233 | 14.61 | 15.36 | 32.77 | 20.72 | 1.89 | 0.39 | 1.78 | 1
2018-01-06 05:00 | 10232.4042 | -0.048233 | 15.66 | 32.33 | 39.97 | 23.83 | 1.89 | 0.46 | 3.01 | 1
2018-01-06 06:00 | 12126.7042 | -0.048233 | 17.88 | 19.67 | 42.29 | 34.18 | 2.79 | 0.46 | 2.61 | 2.79
2018-01-06 07:00 | 13168.8542 | -0.048233 | 20.58 | 27.78 | 44.21 | 36.81 | 35.79 | 15 | 10 | 35.79
2018-01-06 08:00 | 15074.4882 | 68.6144 | 19.23 | 30.69 | 40.58 | 32.18 | 9.18 | 7.12 | 3 | 6.42
2018-01-06 09:00 | 14051.0985 | 140.63 | 19.53 | 26.97 | 41.25 | 30.43 | 4.24 | 2 | 1 | 4.07
2018-01-06 10:00 | 15793.4207 | 127.067 | 20.19 | 26.82 | 40.56 | 37.55 | 2.76 | 1.2 | 1.65 | 2.76
2018-01-06 11:00 | 15663.7432 | 155.15 | 20.45 | 25.22 | 41.78 | 34.79 | 2.5 | 1.2 | 2.37 | 2.5
2018-01-06 12:00 | 16092.6229 | 175.671 | 18.75 | 23.32 | 40.18 | 32.48 | 2.25 | 1 | 2.61 | 2.25
2018-01-06 13:00 | 14812.4152 | 162.016 | 17.9 | 22.7 | 36.45 | 31.38 | 1.61 | 1 | 3.11 | 1.61
2018-01-06 14:00 | 13813.3418 | 110.215 | 17.68 | 21.18 | 34.41 | 33.7 | 2 | 1 | 3.01 | 2
2018-01-06 15:00 | 11693.5424 | 105.992 | 17.77 | 20.9 | 35.72 | 31.45 | 1.61 | 0.97 | 2.61 | 1.08
2018-01-06 16:00 | 11127.565 | 80.2263 | 19.04 | 22.85 | 42.63 | 35.85 | 1.61 | 0.95 | 1 | 1
2018-01-06 17:00 | 11054.632 | 9.4548 | 24.25 | 24.25 | 52.09 | 64.68 | 2.26 | 0.95 | 1 | 1.94
2018-01-06 18:00 | 11075.0542 | -0.048233 | 24.29 | 27.52 | 47.44 | 58.79 | 32.55 | 1.25 | 3.5 | 31.55
2018-01-06 19:00 | 10896.4542 | -0.048233 | 36.89 | 36.89 | 42.8 | 47.23 | 26.08 | 1.55 | 8.14 | 21.92
2018-01-06 20:00 | 12051.2141 | -0.048233 | 37.07 | 37.07 | 40.73 | 40.37 | 4.1 | 0.95 | 1 | 3
2018-01-06 21:00 | 11856.0391 | -0.048233 | 18.75 | 31.86 | 40.3 | 34.72 | 4 | 0.95 | 1.82 | 3
2018-01-06 22:00 | 11511.0541 | -0.048233 | 18.54 | 30.52 | 33.12 | 29.26 | 3 | 0.95 | 11.33 | 2.61
2018-01-06 23:00 | 10288.4542 | -0.048233 | 17.71 | 28.84 | 33.03 | 33.99 | 3 | 0.01 | 3.11 | 2.18
2018-01-07 | 11353.8591 | -0.048233 | 17.49 | 29.86 | 53.69 | 46.88 | 2 | 0.01 | 2.61 | 1.11
2018-01-07 01:00 | 10274.2042 | -0.048233 | 16.98 | 29.42 | 47.39 | 47.34 | 1.61 | 0.01 | 1.67 | 1.55
2018-01-07 02:00 | 10290.3542 | -0.048233 | 16.77 | 29.35 | 43.66 | 46.24 | 1.74 | 0.01 | 1 | 1.61
2018-01-07 03:00 | 11323.2641 | -0.048233 | 15.68 | 30.03 | 42.18 | 51.55 | 1.79 | 0.46 | 0.5 | 1.11
2018-01-07 04:00 | 10426.2042 | -0.048233 | 14.78 | 34.69 | 42.31 | 52.57 | 1.75 | 0.46 | 1 | 1.61
2018-01-07 05:00 | 12043.8291 | -0.048233 | 16.65 | 34.45 | 47.05 | 58.68 | 2 | 0.46 | 2.49 | 1.81
2018-01-07 06:00 | 11299.2542 | -0.048233 | 20.02 | 33.87 | 51.08 | 93.49 | 3.99 | 0.46 | 14.05 | 3.99
2018-01-07 07:00 | 11275.0003 | 1.4213 | 75.34 | 75.34 | 44.38 | 97.58 | 25.01 | 1 | 12.43 | 30.55
2018-01-07 08:00 | 12584.6804 | 122.607 | 69.41 | 69.41 | 42.83 | 142.48 | 24.97 | 11.32 | 2.99 | 15.22
2018-01-07 09:00 | 12407.0287 | 71.2168 | 69.24 | 69.24 | 45.53 | 100.72 | 98.9741 | 11.75 | 1 | 89.5762
2018-01-07 10:00 | 10918.4203 | 108.074 | 37.37 | 37.37 | 51.95 | 56.2 | 51.77 | 11.75 | 2 | 45.75
2018-01-07 11:00 | 10693.7244 | 127.552 | 17.06 | 35.59 | 49.69 | 44.94 | 20.79 | 1 | 2 | 3
2018-01-07 12:00 | 11680.1202 | 132.204 | 15.32 | 29.17 | 48.56 | 34.16 | 3.5 | 1 | 2.61 | 2.61
2018-01-07 13:00 | 10149.1065 | 128.27 | 14.89 | 24.66 | 50.14 | 28.24 | 3 | 1 | 2 | 2.25
2018-01-07 14:00 | 10795.9258 | 123.105 | 14.26 | 22.1 | 47.04 | 28.69 | 3 | 1 | 3.11 | 1.61
2018-01-07 15:00 | 10540.2212 | 141.731 | 14.53 | 21.14 | 45.61 | 28.35 | 3 | 0.75 | 3.19 | 1
2018-01-07 16:00 | 9578.906 | 106.059 | 15.87 | 21.01 | 54.63 | 27.37 | 2.56 | 0.75 | 1.61 | 1
2018-01-07 17:00 | 10729.8912 | 33.513 | 17.29 | 21.48 | 74.68 | 41.33 | 3.41 | 0.97 | 1 | 2
2018-01-07 18:00 | 9839.1042 | -0.048233 | 20.97 | 25.42 | 61.69 | 48.16 | 20 | 1.04 | 3 | 16
2018-01-07 19:00 | 10033.8542 | -0.048233 | 21.05 | 25.43 | 59.39 | 41.93 | 25.75 | 1.45 | 3 | 25.75
2018-01-07 20:00 | 11021.5341 | -0.048233 | 18.71 | 24.42 | 53.93 | 34.41 | 19.79 | 0.99 | 1.61 | 16.54
2018-01-07 21:00 | 9761.2042 | -0.048233 | 19.12 | 22.93 | 58.72 | 31.54 | 7.6 | 0.82 | 2 | 3
2018-01-07 22:00 | 10737.7391 | -0.048233 | 20.43 | 21.17 | 53.03 | 27.33 | 5.1 | 0.82 | 3.01 | 2.25
2018-01-07 23:00 | 10541.5091 | -0.048233 | 17.13 | 21.67 | 60 | 38.25 | 2.65 | 0.01 | 3 | 1.65
2018-01-08 | 9403.0542 | -0.048233 | 16.76 | 20.38 | 56.32 | 46.8 | 2.11 | 0.01 | 3 | 1.11
2018-01-08 01:00 | 9448.6542 | -0.048233 | 16.87 | 19.36 | 59.99 | 46.48 | 2 | 0.01 | 2.11 | 1
2018-01-08 02:00 | 10563.6641 | -0.048233 | 16.99 | 19.08 | 54.31 | 46.37 | 2.01 | 0.01 | 2.13 | 1
2018-01-08 03:00 | 10546.7841 | -0.048233 | 17.02 | 18.82 | 54.26 | 47.06 | 2.01 | 0.47 | 2.11 | 1
2018-01-08 04:00 | 10485.5941 | -0.048233 | 17.26 | 19.15 | 54.59 | 46.69 | 2 | 0.46 | 2 | 1
2018-01-08 05:00 | 10564.7191 | -0.048233 | 18.48 | 18.48 | 59.18 | 47.96 | 2.25 | 0.47 | 2.31 | 2
2018-01-08 06:00 | 10663.8891 | -0.048233 | 906.7411 | 19.12 | 76.63 | 77.25 | 3.58 | 0.47 | 9.11 | 17.74
2018-01-08 07:00 | 9550.724 | 1.3937 | 31.55 | 19.83 | 68.16 | 89.22 | 454.0078 | 83.3173 | 4.06 | 464.3806
2018-01-08 08:00 | 9655.5302 | 120.716 | 20.43 | 20.43 | 62.66 | 69.06 | 111.5841 | 70.6273 | 2.75 | 108.8862
2018-01-08 09:00 | 9363.1953 | 117.995 | 20.91 | 20.91 | 61.1 | 45.43 | 27.46 | 13.56 | 2.11 | 23.83
2018-01-08 10:00 | 10061.266 | 115.745 | 29.69 | 18.69 | 57.15 | 36.45 | 7.63 | 2 | 2.11 | 4
2018-01-08 11:00 | 8733.1087 | 125.746 | 18.71 | 18.71 | 57.91 | 26.91 | 4.01 | 2 | 3.28 | 2.9
2018-01-08 12:00 | 8654.6966 | 138.207 | 20.29 | 20.29 | 52.38 | 23.67 | 3.41 | 1.61 | 3.5 | 2.31
2018-01-08 13:00 | 8546.5866 | 157.407 | 18.76 | 19.6 | 50.14 | 21.52 | 3 | 1.2 | 3.46 | 2.11
2018-01-08 14:00 | 9593.173 | 234.055 | 17.89 | 19.34 | 47.35 | 20.63 | 2.58 | 1.2 | 3.46 | 2.31
2018-01-08 15:00 | 8815.7103 | 254.695 | 17.2 | 18.34 | 47.78 | 20.31 | 2.13 | 0.97 | 3.46 | 2
2018-01-08 16:00 | 8799.9165 | 114.07 | 17.04 | 18.74 | 52.88 | 21.14 | 2 | 0.97 | 2.31 | 1
2018-01-08 17:00 | 8805.2575 | 32.6921 | 17.08 | 19.68 | 69.27 | 29.72 | 2.35 | 0.97 | 1 | 2
2018-01-08 18:00 | 9929.6091 | -0.048233 | 18.67 | 21.95 | 63.57 | 29.71 | 25 | 1.67 | 3.5 | 17.36
2018-01-08 19:00 | 9925.3891 | -0.048233 | 18.6 | 20.22 | 55.84 | 28.33 | 15.87 | 1.42 | 3 | 15.87
2018-01-08 20:00 | 8789.3542 | -0.048233 | 18.04 | 18.82 | 53.86 | 26.08 | 7.44 | 1.27 | 1 | 3
2018-01-08 21:00 | 9700.6741 | -0.048233 | 17.01 | 19.09 | 52.51 | 25.02 | 5.23 | 1.27 | 2.45 | 3
2018-01-08 22:00 | 9659.5291 | -0.048233 | 18.1 | 18.93 | 50.44 | 23.46 | 4.11 | 1.11 | 3.11 | 2.5
2018-01-08 23:00 | 8577.5042 | -0.048233 | 16.59 | 16.59 | 47.5 | 20.77 | 3.2 | 0.01 | 10 | 3
2018-01-09 | 8503.4042 | -0.048233 | 16.14 | 18.55 | 41.81 | 19.32 | 3 | 0.01 | 3 | 2
2018-01-09 01:00 | 9393.6691 | -0.048233 | 13.21 | 20.79 | 39.73 | 18.9 | 1.62 | 0.01 | 2.11 | 1.61
2018-01-09 02:00 | 8463.5042 | -0.048233 | 12.44 | 20.09 | 39.93 | 18.78 | 1.61 | 0.01 | 2.11 | 1
2018-01-09 03:00 | 8544.2542 | -0.048233 | 4.32 | 18.34 | 40.09 | 18.8 | 1.61 | 0.46 | 2.11 | 0.54
2018-01-09 04:00 | 9913.7841 | -0.048233 | 10.14 | 16.2 | 39.95 | 18.99 | 1.61 | 0.46 | 2.11 | 1
2018-01-09 05:00 | 9916.0542 | -0.048233 | 4.84 | 17.68 | 48.16 | 22.05 | 1.61 | 0.46 | 2.61 | 1.61
2018-01-09 06:00 | 13238.0891 | -0.048233 | 11.65 | 21.18 | 53.75 | 38.93 | 2.61 | 0.47 | 9.04 | 2.61
2018-01-09 07:00 | 14259.8429 | 8.4388 | 13.02 | 27.33 | 53.55 | 39.59 | 30.58 | 9 | 14.95 | 41.8
2018-01-09 08:00 | 14554.4245 | 362.663 | 14.06 | 19.21 | 50.25 | 27.34 | 17.78 | 5.98 | 3 | 16.8
2018-01-09 09:00 | 15134.608 | 713.6 | 16.91 | 18.5 | 52.39 | 23.73 | 3.61 | 2.06 | 3 | 3.06
2018-01-09 10:00 | 13568.4776 | 772.608 | 15.33 | 21.88 | 45.64 | 23.03 | 2.61 | 1.78 | 2.56 | 2.41
2018-01-09 11:00 | 15533.725 | 1046.91 | 14.56 | 19.15 | 43.69 | 22.66 | 2.61 | 1 | 25.01 | 2.41
2018-01-09 12:00 | 13789.554 | 1135.32 | 14.38 | 15.85 | 39.13 | 22.25 | 3.48 | 1 | 29.87 | 2
2018-01-09 13:00 | 13264.9925 | 1055.15 | 13.82 | 14.65 | 36.82 | 22.21 | 2.28 | 1 | 3.5 | 2
2018-01-09 14:00 | 12201.6081 | 934.798 | 13.19 | 13.19 | 36.86 | 20.87 | 2.02 | 1 | 3.5 | 1.59
2018-01-09 15:00 | 11608.2561 | 607.217 | 12.26 | 12.26 | 38.34 | 19.28 | 2.51 | 0.97 | 3.48 | 1
2018-01-09 16:00 | 12106.2811 | 176.148 | 11.89 | 11.89 | 44.21 | 18.71 | 2.51 | 0.97 | 2.99 | 0.57
2018-01-09 17:00 | 10699.2733 | 46.393 | 11.81 | 11.81 | 65.73 | 27.44 | 2.51 | 0.97 | 1 | 1.79
2018-01-09 18:00 | 10534.5042 | -0.048233 | 15.33 | 15.33 | 49.94 | 22.39 | 18.97 | 1.5 | 3.11 | 18.97
2018-01-09 19:00 | 11606.0041 | -0.048233 | 13.02 | 13.02 | 45.5 | 21.84 | 40.83 | 1 | 27.15 | 40.83
2018-01-09 20:00 | 10363.5042 | -0.048233 | 12.09 | 12.09 | 42.48 | 19.56 | 3 | 1 | 1 | 2.11
2018-01-09 21:00 | 10171.6042 | -0.048233 | 11.86 | 11.86 | 40.03 | 19.55 | 3 | 1 | 3.01 | 2.11
2018-01-09 22:00 | 9818.2042 | -0.048233 | 11.77 | 11.77 | 38.86 | 12.48 | 4 | 1 | 3.98 | 3
2018-01-09 23:00 | 10469.7691 | -0.048233 | -0.1 | -0.1 | 36.31 | 8.28 | 3.46 | 0.01 | 52.6962 | 3
2018-01-10 | 10285.1441 | -0.048233 | -1.2 | -1.2 | 45.41 | 6.6 | 2.02 | 0.01 | 20.86 | 1.79
2018-01-10 01:00 | 9278.6042 | -0.048233 | -3.58 | -3.58 | 46.98 | 6.14 | 1.55 | 0.01 | 13.75 | 1.11
2018-01-10 02:00 | 9222.5542 | -0.048233 | -20.01 | -20.01 | 46.85 | 5.47 | 1.25 | 0.01 | 2.11 | 0.07
2018-01-10 03:00 | 10313.6291 | -0.048233 | -14.76 | -14.76 | 40.24 | 6.01 | 1.25 | 0.01 | 1.6 | 0.47
2018-01-10 04:00 | 9375.5042 | -0.048233 | -1.53 | -1.53 | 39.42 | 7.15 | 1.25 | 0.01 | 1.96 | 0.75
2018-01-10 05:00 | 10145.9542 | -0.048233 | -0.56 | -0.56 | 40.25 | 12.92 | 2.07 | 0.01 | 12.95 | 2.07
2018-01-10 06:00 | 12009.8542 | -0.048233 | 14.45 | 14.45 | 42.63 | 20.52 | 3.66 | 0.01 | 31.21 | 22
2018-01-10 07:00 | 14207.0092 | 10.3594 | 14.33 | 14.33 | 48.27 | 24.42 | 23.89 | 0.02 | 94.8234 | 90.8062
2018-01-10 08:00 | 14639.467 | 418.272 | 16.98 | 16.98 | 52.99 | 23.06 | 5.99 | 0.02 | 3.5 | 5.99
2018-01-10 09:00 | 15462.6455 | 769.536 | 18.48 | 18.48 | 48.31 | 25.79 | 23.54 | 0.02 | 3 | 22.54
2018-01-10 10:00 | 15437.853 | 998.036 | 19.56 | 20.06 | 45.43 | 23.62 | 29.03 | 0.3 | 2.5 | 28.51
2018-01-10 11:00 | 13982.119 | 1134.02 | 18.86 | 19.58 | 44.78 | 23.1 | 24.97 | 0.02 | 3.11 | 24.31
2018-01-10 12:00 | 14137.5675 | 1158.65 | 18.12 | 18.83 | 42.09 | 24.09 | 20.79 | 0.02 | 3 | 3.1
2018-01-10 13:00 | 14000.701 | 1119.58 | 17.65 | 19.75 | 37.09 | 29 | 2.91 | 0.02 | 3 | 2.51
2018-01-10 14:00 | 12812.498 | 1012.84 | 17.05 | 19.94 | 36.72 | 28.5 | 2.28 | 0.02 | 3.01 | 2.01
2018-01-10 15:00 | 13630.3183 | 799.733 | 16.75 | 24.09 | 37.29 | 30.24 | 1.61 | 0.01 | 3.11 | 0.86
2018-01-10 16:00 | 11586.3102 | 464.116 | 16.79 | 19.86 | 53.14 | 30.81 | 1.61 | 0.01 | 1 | 0.65
2018-01-10 17:00 | 11138.4956 | 54.7322 | 17.43 | 20.2 | 58.03 | 45.74 | 1.9 | 0.01 | 1 | 1.18
2018-01-10 18:00 | 12220.0141 | -0.048233 | 19.29 | 24.55 | 53.83 | 34.69 | 37.09 | 0.01 | 3.26 | 36.89
2018-01-10 19:00 | 10810.0042 | -0.048233 | 19.35 | 19.82 | 53.08 | 25.05 | 21.3 | 0.01 | 3 | 19.3
2018-01-10 20:00 | 11688.2941 | -0.048233 | 19.12 | 19.46 | 44.9 | 23 | 5 | 0.01 | 1.21 | 3
2018-01-10 21:00 | 10115.5542 | -0.048233 | 18.52 | 20.69 | 42.1 | 22.15 | 4.94 | 0.01 | 3.01 | 3
2018-01-10 22:00 | 9857.1542 | -0.048233 | 16.79 | 16.79 | 39.11 | 18.81 | 28.1 | 0.01 | 3.5 | 3
2018-01-10 23:00 | 9586.4042 | -0.048233 | 15.61 | 15.61 | 38.33 | 17.68 | 2.51 | 0.01 | 20.54 | 22
2018-01-11 | 9546.5042 | -0.048233 | 2.34 | 2.34 | 50.24 | 3.73 | 1.61 | 0.01 | 10.6 | 0.88
2018-01-11 01:00 | 10614.3041 | -0.048233 | -0.39 | -0.39 | 50.21 | 2.18 | 1.3 | 0.01 | 15 | 0.01
2018-01-11 02:00 | 9385.0042 | -0.048233 | -0.57 | -0.57 | 47.04 | 1.91 | 1.58 | 0.01 | 1 | 0.01
2018-01-11 03:00 | 10363.2141 | -0.048233 | -0.74 | -0.74 | 46.21 | 1.85 | 1.61 | 0.01 | 0.94 | 0.01
2018-01-11 04:00 | 9520.8542 | -0.048233 | -0.64 | -0.64 | 46.82 | 2.56 | 1 | 0.01 | 1 | 0.46
2018-01-11 05:00 | 10759.6542 | -0.048233 | 2.45 | 2.45 | 43.82 | 6.33 | 2.11 | 0.01 | 15 | 2.11
2018-01-11 06:00 | 13744.4891 | -0.048233 | 17.71 | 17.71 | 45.36 | 19.4 | 50 | 0.01 | 112.7434 | 50
2018-01-11 07:00 | 13307.7225 | 10.1289 | 17.24 | 17.24 | 49.74 | 19.87 | 37.17 | 0.02 | 28.91 | 37.17
2018-01-11 08:00 | 15222.1983 | 405.624 | 16.76 | 16.76 | 53.64 | 20.34 | 23.11 | 0.02 | 2.11 | 20.96
2018-01-11 09:00 | 16031.4392 | 749.677 | 18.11 | 18.11 | 51.07 | 21.74 | 23.7 | 0.02 | 2.11 | 4.53
2018-01-11 10:00 | 16395.6569 | 969.907 | 18.66 | 18.66 | 49.58 | 22.49 | 24.13 | 0.02 | 2 | 3.51
2018-01-11 11:00 | 14426.2155 | 1116.49 | 19.35 | 20.24 | 47.67 | 23.8 | 20.49 | 0.02 | 29.6 | 4
2018-01-11 12:00 | 16100.2178 | 1156.87 | 63.13 | 18.01 | 46.39 | 25 | 3.11 | 0.02 | 3.01 | 2.75
2018-01-11 13:00 | 14323.8815 | 1106.77 | 21.9 | 21.9 | 43.42 | 24.63 | 2.62 | 0.02 | 2 | 2.26
2018-01-11 14:00 | 13304.997 | 1001.26 | 17.84 | 20.26 | 41.52 | 27.37 | 31.69 | 0.02 | 2 | 1.61
2018-01-11 15:00 | 12809.8693 | 782.073 | 17.34 | 18.89 | 44.09 | 27.42 | 2.02 | 0.01 | 2 | 1.04
2018-01-11 16:00 | 12284.2134 | 453.751 | 17.25 | 20.98 | 50.78 | 26.93 | 2.02 | 0.01 | 0.75 | 1
2018-01-11 17:00 | 13049.2776 | 59.9835 | 17.72 | 22.5 | 60.47 | 31.66 | 2 | 0.01 | 0.5 | 1
2018-01-11 18:00 | 11391.4042 | -0.048233 | 19.76 | 25.61 | 60.34 | 27.84 | 24.04 | 0.01 | 2 | 22.04
2018-01-11 19:00 | 12613.5291 | -0.048233 | 18.79 | 18.79 | 57.84 | 20.62 | 7.58 | 0.01 | 2 | 11.13
2018-01-11 20:00 | 11193.8042 | -0.048233 | 19.78 | 19.9 | 47.12 | 19.94 | 5.14 | 0.01 | 1 | 2.96
2018-01-11 21:00 | 10982.9042 | -0.048233 | 18.59 | 18.59 | 42.12 | 18 | 4.16 | 0.01 | 2 | 2.51
2018-01-11 22:00 | 10730.2042 | -0.048233 | 17.32 | 17.32 | 38.92 | 16.23 | 3.56 | 0.01 | 10.88 | 3
2018-01-11 23:00 | 10422.4042 | -0.048233 | 3.35 | 3.35 | 36.55 | 8.74 | 90.8241 | 0.01 | 3.01 | 2.01
2018-01-12 | 10189.6542 | -0.048233 | -0.23 | -0.23 | 12.52 | 6.36 | 40 | 0.01 | 11.56 | 1.24
2018-01-12 01:00 | 11313.7691 | -0.048233 | -0.3 | -0.3 | 8.5 | 5.28 | 1.61 | 0.01 | 13.53 | 1
2018-01-12 02:00 | 10019.6042 | -0.048233 | -0.49 | -0.49 | 3.58 | 5.83 | 1.61 | 0.01 | 2.11 | 0.01
2018-01-12 03:00 | 9919.8542 | -0.048233 | -0.43 | -0.43 | 3.49 | 9.27 | 1.5 | 0.3 | 1 | 0.01
2018-01-12 04:00 | 10036.7042 | -0.048233 | 10.16 | 10.16 | 4.47 | 14.58 | 1.5 | 0.3 | 1.18 | 0.01
2018-01-12 05:00 | 10813.8042 | -0.048233 | 18.6 | 18.6 | 37.03 | 18.35 | 1.61 | 0.3 | 2.99 | 1.61
2018-01-12 06:00 | 12359.4542 | -0.048233 | 18.28 | 18.28 | 64.31 | 23.14 | 3 | 0.3 | 15 | 22
2018-01-12 07:00 | 14688.5486 | 9.7949 | 29.45 | 23.48 | 54.47 | 24.76 | 25 | 1.48 | 8.61 | 25
2018-01-12 08:00 | 15363.4924 | 397.552 | 21.7 | 24.33 | 44.84 | 24.58 | 7.5 | 1 | 3 | 5.5
2018-01-12 09:00 | 14224.7794 | 733.452 | 20.14 | 25.82 | 41.91 | 24.74 | 3.6 | 1 | 1.32 | 3.6
2018-01-12 10:00 | 16093.2274 | 944.244 | 19.68 | 23.9 | 45.6 | 24.33 | 3.11 | 1 | 2.11 | 3.07
2018-01-12 11:00 | 14863.2155 | 1077.49 | 18.8 | 24.75 | 45.01 | 27.74 | 3.65 | 0.97 | 3.5 | 3.26
2018-01-12 12:00 | 17198.821 | 1116.2 | 17.55 | 26.57 | 42.27 | 25.3 | 2.12 | 0.97 | 3.44 | 1.97
2018-01-12 13:00 | 16698.1707 | 1078.65 | 17.24 | 32.58 | 40.57 | 28.46 | 2.11 | 0.97 | 3.46 | 1.15
2018-01-12 14:00 | 15282.3692 | 909.658 | 17 | 27.69 | 39.87 | 26.67 | 2.11 | 1 | 2.61 | 1
2018-01-12 15:00 | 14637.2156 | 575.138 | 16.97 | 22.9 | 40.76 | 26.59 | 2.11 | 0.51 | 2.11 | 1
2018-01-12 16:00 | 12738.3115 | 335.749 | 16.91 | 20.71 | 46.71 | 27.55 | 2.11 | 0.5 | 1 | 0.16
2018-01-12 17:00 | 12153.892 | 17.5705 | 17.17 | 19.84 | 64.1 | 44.15 | 2.11 | 0.5 | 1 | 1
2018-01-12 18:00 | 13230.7041 | -0.048233 | 19.32 | 21.69 | 50.89 | 31.69 | 29.25 | 0.5 | 3 | 27.26
2018-01-12 19:00 | 13112.5441 | -0.048233 | 18.84 | 22.49 | 49.79 | 24.08 | 22.29 | 0.5 | 3 | 22.29
2018-01-12 20:00 | 12750.6791 | -0.048233 | 17.91 | 22.5 | 42.88 | 22.57 | 3.26 | 0.5 | 1 | 3
2018-01-12 21:00 | 12561.8341 | -0.048233 | 17.7 | 20.88 | 43.73 | 21.49 | 3.11 | 0.5 | 3 | 2.51
2018-01-12 22:00 | 11996.3541 | -0.048233 | 17.12 | 19.88 | 38.8 | 21.34 | 26 | 0.5 | 3.87 | 2.11
2018-01-12 23:00 | 11554.3091 | -0.048233 | 16.1 | 22.31 | 35.41 | 20.42 | 25 | 0.01 | 15 | 1.25
2018-01-13 | 11531.0991 | -0.048233 | 14.02 | 21.55 | 13.55 | 19.39 | 3 | 0.01 | 2.99 | 0.01
2018-01-13 01:00 | 11428.7641 | -0.048233 | 12.97 | 19.7 | 12.89 | 18.36 | 2.11 | 0.01 | 3.01 | 0.46
2018-01-13 02:00 | 11270.5141 | -0.048233 | 8.86 | 19.64 | 11.46 | 17.98 | 2.11 | 0.01 | 2.11 | 0.01
2018-01-13 03:00 | 10107.0042 | -0.048233 | 14.13 | 19.59 | 11.32 | 17.89 | 2 | 0.3 | 1 | 0.01
2018-01-13 04:00 | 11409.7741 | -0.048233 | 15.11 | 19.51 | 13.52 | 18.43 | 2 | 0.3 | 1 | 0.01
2018-01-13 05:00 | 12294.9191 | -0.048233 | 18.29 | 19.65 | 36.65 | 20.84 | 2.24 | 0.3 | 3.83 | 1
2018-01-13 06:00 | 14119.0141 | -0.048233 | 19.69 | 19.69 | 54.43 | 25.21 | 4 | 0.3 | 8.63 | 16.8
2018-01-13 07:00 | 13544.3957 | 1.2586 | 20.9 | 20.9 | 58.93 | 24.88 | 25.5 | 1 | 6.89 | 25.3
2018-01-13 08:00 | 15344.5084 | 77.5577 | 19.85 | 19.85 | 58.59 | 23.96 | 14.71 | 1 | 1.55 | 14.71
2018-01-13 09:00 | 14231.7923 | 189.834 | 18.1 | 20.84 | 49.88 | 24.43 | 5.3 | 0.97 | 1.25 | 4
2018-01-13 10:00 | 14315.226 | 298.659 | 19.54 | 21.21 | 55.95 | 26.24 | 4.7 | 0.97 | 2.09 | 3.5
2018-01-13 11:00 | 15676.1532 | 479.913 | 18.67 | 22.37 | 55.39 | 25.98 | 4.38 | 0.82 | 3.5 | 3.5
2018-01-13 12:00 | 14524.0883 | 956.514 | 18.34 | 23.63 | 52.14 | 25.76 | 3.91 | 0.82 | 3.5 | 3.3
2018-01-13 13:00 | 15883.4702 | 771.422 | 18 | 23.23 | 52.47 | 26.6 | 3.25 | 0.82 | 2.61 | 2.52
2018-01-13 14:00 | 12911.3417 | 422.886 | 17.76 | 24.42 | 49.73 | 28.39 | 3.01 | 0.82 | 2.11 | 2.43
2018-01-13 15:00 | 13514.4023 | 171.86 | 17.47 | 23.07 | 47.47 | 25.1 | 2.6 | 0.5 | 2 | 1.48
2018-01-13 16:00 | 13437.7513 | 213.205 | 17.09 | 22.52 | 55.36 | 26.45 | 2.63 | 0.5 | 1 | 0.47
2018-01-13 17:00 | 11721.0047 | 54.8997 | 17.64 | 23.05 | 64.68 | 38.1 | 3.18 | 0.5 | 0.72 | 1
2018-01-13 18:00 | 11532.0042 | -0.048233 | 19.44 | 29.64 | 60.37 | 30.84 | 23.88 | 0.5 | 3 | 20.53
2018-01-13 19:00 | 12444.7291 | -0.048233 | 18.27 | 29.92 | 59.49 | 25.07 | 30.12 | 0.5 | 3 | 30.12
2018-01-13 20:00 | 11013.3042 | -0.048233 | 17.04 | 33.68 | 58.77 | 23.68 | 7.13 | 0.5 | 1 | 3.11
2018-01-13 21:00 | 11854.9841 | -0.048233 | 154.24 | 154.24 | 49.24 | 23.42 | 6.1 | 0.5 | 2.72 | 2.96
2018-01-13 22:00 | 11321.1541 | -0.048233 | 15.37 | 25.52 | 49 | 21.5 | 5 | 0.5 | 3 | 1.9
2018-01-13 23:00 | 9924.6042 | -0.048233 | 14.14 | 25.84 | 44.49 | 21.25 | 4.74 | 0.01 | 3 | 2.51
2018-01-14 | 10862.2291 | -0.048233 | 828.0611 | 560.45 | 51.19 | 25.77 | 3.26 | 0.01 | 3 | 0.31
2018-01-14 01:00 | 9750.7542 | -0.048233 | 0 | 47.3 | 49.18 | 22.16 | 2.73 | 0.01 | 2.5 | 2.54
2018-01-14 02:00 | 9598.7542 | -0.048233 | 7.9 | 24.7 | 42.81 | 21.03 | 2.21 | 0.01 | 2.5 | 1.96
2018-01-14 03:00 | 10590.0391 | -0.048233 | 4.71 | 24.48 | 42.31 | 20.42 | 2.1 | 0.47 | 2.11 | 1.95
2018-01-14 04:00 | 10522.5191 | -0.048233 | 10.75 | 25.67 | 44.43 | 20.41 | 2.11 | 0.47 | 1 | 1.94
2018-01-14 05:00 | 9601.6042 | -0.048233 | 318.9557 | 274.63 | 52.38 | 20.65 | 3.25 | 0.47 | 2.31 | 3
2018-01-14 06:00 | 9757.4042 | -0.048233 | 17.53 | 23.17 | 58.49 | 22.03 | 15.5 | 0.48 | 12.77 | 15.5
2018-01-14 07:00 | 9929.3542 | -0.048233 | 23.73 | 24.49 | 57.52 | 22.85 | 30.25 | 0.82 | 15 | 32.22
2018-01-14 08:00 | 11183.3027 | 63.2869 | 18 | 29.59 | 56.2 | 24.3 | 20.14 | 0.82 | 3 | 20.1
2018-01-14 09:00 | 10299.9484 | 138.051 | 55.03 | 55.03 | 55.64 | 26.85 | 6.62 | 0.82 | 1.66 | 3.84
2018-01-14 10:00 | 11583.8167 | 257.921 | 17.7 | 33.12 | 50.08 | 29.72 | 6.78 | 0.82 | 1.75 | 3.25
2018-01-14 11:00 | 10394.7841 | 217.878 | 17.31 | 35.01 | 43.78 | 31.85 | 7.21 | 0.71 | 3.46 | 4.27
2018-01-14 12:00 | 10396.1027 | 203.266 | 16.51 | 39.13 | 42.66 | 27.5 | 5.03 | 0.61 | 3 | 3.25
2018-01-14 13:00 | 11467.6833 | 158.842 | 16.09 | 37.52 | 41.33 | 24 | 3.93 | 0.61 | 2.44 | 2.61
2018-01-14 14:00 | 11430.2403 | 209.351 | 15.71 | 34.16 | 39.8 | 24.4 | 3.37 | 0.61 | 3.01 | 2.75
2018-01-14 15:00 | 11464.0298 | 120.379 | 15.67 | 34.44 | 41.26 | 23.09 | 2.63 | 0.5 | 2.11 | 2
2018-01-14 16:00 | 11501.7331 | 77.1167 | 16.35 | 30.46 | 48.88 | 23.83 | 3.03 | 0.5 | 1 | 1
2018-01-14 17:00 | 10127.7425 | 9.7816 | 16.51 | 38.12 | 56.47 | 36.89 | 3.92 | 0.5 | 0.5 | 2
2018-01-14 18:00 | 9996.8042 | -0.048233 | 16.95 | 41.23 | 54.88 | 31.93 | 38.46 | 0.5 | 2.72 | 25
2018-01-14 19:00 | 10921.3091 | -0.048233 | 16.21 | 36.23 | 49.68 | 25.79 | 32.55 | 0.5 | 3 | 31.91
2018-01-14 20:00 | 9643.4042 | -0.048233 | 16.45 | 36.15 | 50.69 | 24.76 | 20 | 0.5 | 2.2 | 3.11
2018-01-14 21:00 | 9377.4042 | -0.048233 | 15.11 | 30.98 | 46.96 | 21.55 | 16.33 | 0.5 | 3 | 2.61
2018-01-14 22:00 | 9117.1042 | -0.048233 | 185.98 | 185.98 | 44.39 | 21.56 | 19.6 | 0.5 | 3 | 2.75
2018-01-14 23:00 | 8902.4042 | -0.048233 | -0.63 | 32.87 | 41.44 | 22.06 | 20 | 0.01 | 9.24 | 3.11
2018-01-15 | 9935.9391 | -0.048233 | -1.4 | 34.08 | 37.98 | 22.69 | 25.1 | 0.01 | 2.61 | 2.75
2018-01-15 01:00 | 8927.1042 | -0.048233 | -1 | 27.76 | 37.91 | 19.7 | 2 | 0.01 | 2.61 | 1.98
2018-01-15 02:00 | 8878.6542 | -0.048233 | -0.69 | 27.55 | 36.68 | 17.32 | 2 | 0.01 | 1.88 | 1.41
2018-01-15 03:00 | 8824.5042 | -0.048233 | 13.55 | 27.16 | 37.56 | 17.14 | 2 | 0.47 | 1 | 1.83
2018-01-15 04:00 | 8855.8542 | -0.048233 | 13.89 | 27.09 | 39.06 | 16.85 | 2 | 0.47 | 1 | 1.45
2018-01-15 05:00 | 8922.3542 | -0.048233 | 324.1857 | 279.86 | 45.26 | 15.55 | 2.05 | 0.47 | 3.03 | 2.05
2018-01-15 06:00 | 8998.3542 | -0.048233 | 17.09 | 31.56 | 81.73 | 19.44 | 21 | 0.47 | 13 | 100.1262
2018-01-15 07:00 | 10040.3841 | -0.048233 | 32.14 | 32.14 | 70.26 | 19.87 | 28.32 | 0.82 | 15 | 95.1262
2018-01-15 08:00 | 9119.7573 | 41.7445 | 34.8 | 34.8 | 59.04 | 21.43 | 25 | 0.82 | 1 | 16.56
2018-01-15 09:00 | 9531.9646 | 141.647 | 40.33 | 40.33 | 46.37 | 22.66 | 25 | 0.93 | 1 | 4.89
2018-01-15 10:00 | 9551.4596 | 245.168 | 21.8 | 21.96 | 46 | 22.8 | 23.5 | 0.93 | 1 | 5
2018-01-15 11:00 | 9689.4414 | 320.412 | 19.36 | 23 | 45.41 | 23.5 | 3.87 | 0.74 | 3.5 | 3.1
2018-01-15 12:00 | 9733.4729 | 265.761 | 17.37 | 24.8 | 40.48 | 23.37 | 2.67 | 0.65 | 3.11 | 2.67
2018-01-15 13:00 | 11163.051 | 491.091 | 17.06 | 26.95 | 38.75 | 23.22 | 2.11 | 0.65 | 3.46 | 2.11
2018-01-15 14:00 | 11509.7894 | 642.753 | 16.96 | 30.61 | 38.16 | 23.28 | 2.11 | 0.65 | 3.5 | 2.11
2018-01-15 15:00 | 10292.034 | 617.72 | 16.86 | 25.94 | 38.75 | 23.5 | 2.11 | 0.5 | 2.15 | 1.18
2018-01-15 16:00 | 10953.8675 | 83.8128 | 16.92 | 21.33 | 59.91 | 21.62 | 2 | 0.5 | 1.7 | 1.32
2018-01-15 17:00 | 10918.6309 | 50.4132 | 17.01 | 22.69 | 83.57 | 33.69 | 2 | 0.5 | 1 | 2
2018-01-15 18:00 | 11026.8091 | -0.048233 | 17.92 | 25.05 | 67.55 | 49.11 | 22.88 | 0.5 | 2.76 | 21.07
2018-01-15 19:00 | 10894.9341 | -0.048233 | 17.2 | 26.43 | 55.43 | 24.77 | 34.5 | 0.5 | 3.5 | 26.61
2018-01-15 20:00 | 9554.1042 | -0.048233 | 16.58 | 23.5 | 51.1 | 22.95 | 5.79 | 0.5 | 1 | 3.1
2018-01-15 21:00 | 10603.7541 | -0.048233 | 15.71 | 22.04 | 46.5 | 21 | 4.46 | 0.5 | 1.5 | 3
2018-01-15 22:00 | 10453.9441 | -0.048233 | 14.01 | 22.1 | 43.3 | 18.92 | 3.77 | 0.5 | 3.5 | 3.11
2018-01-15 23:00 | 10328.3991 | -0.048233 | 14.21 | 21.72 | 36.34 | 17.33 | 20.75 | 0.01 | 8.32 | 20.75
2018-01-16 | 10303.0791 | -0.048233 | 15.74 | 19.86 | 38.77 | 23.03 | 40 | 0.01 | 3.11 | 22
2018-01-16 01:00 | 10127.9491 | -0.048233 | 12.84 | 19.1 | 36.89 | 19.98 | 3 | 0.01 | 3.11 | 2.65
2018-01-16 02:00 | 10127.9491 | -0.048233 | 12.13 | 19.17 | 35.87 | 18.71 | 40 | 0.01 | 1 | 1.95
2018-01-16 03:00 | 9080.0542 | -0.048233 | 13.08 | 19.23 | 35.21 | 19.02 | 22 | 0.47 | 1 | 1.6
2018-01-16 04:00 | 10019.2841 | -0.048233 | 13.18 | 19.61 | 35.91 | 20.64 | 22 | 0.47 | 1 | 2.11
2018-01-16 05:00 | 10146.9391 | -0.048233 | 15.78 | 20.47 | 38.99 | 21.78 | 22 | 0.48 | 4 | 3
2018-01-16 06:00 | 10162.7641 | -0.048233 | 256.2557 | 20.15 | 52.91 | 24.39 | 20 | 0.5 | 15 | 36.86
2018-01-16 07:00 | 10227.4162 | 1.2334 | 93.79 | 21.31 | 58.61 | 24.75 | 50.38 | 1 | 9.11 | 93.4362
2018-01-16 08:00 | 10386.2978 | 114.832 | 45.14 | 20.71 | 52.76 | 25.01 | 22.45 | 1 | 2.53 | 20.01
2018-01-16 09:00 | 10831.1185 | 471.463 | 17.16 | 21.31 | 45.81 | 25.34 | 5.11 | 2 | 1 | 3.11
2018-01-16 10:00 | 10965.8029 | 448.126 | 16.99 | 22.63 | 50.6 | 24.91 | 6.61 | 1.82 | 1 | 3.32
2018-01-16 11:00 | 9660.3211 | 177.759 | 14.26 | 22.08 | 48.33 | 25.55 | 5.15 | 1 | 3.5 | 3.1
2018-01-16 12:00 | 10604.7672 | 155.912 | 13.74 | 22.01 | 45.63 | 26.15 | 4.66 | 1 | 3.46 | 2.53
2018-01-16 13:00 | 9518.6589 | 136.641 | 13.78 | 21.37 | 43.66 | 27.55 | 4 | 1 | 2 | 2.02
2018-01-16 14:00 | 9832.1856 | 110.669 | 13.57 | 21.26 | 41.48 | 28 | 3.58 | 1 | 2 | 2.53
2018-01-16 15:00 | 9999.7243 | 79.0256 | 17.26 | 21.43 | 44.26 | 28.24 | 4 | 0.97 | 2 | 1.61
2018-01-16 16:00 | 10022.0512 | 46.5276 | 16.58 | 21.78 | 53.14 | 29.03 | 4 | 0.97 | 0.51 | 1
2018-01-16 17:00 | 9934.3259 | 14.1852 | 20.95 | 22.04 | 62.02 | 40.88 | 3.25 | 0.97 | 0.51 | 2.74
2018-01-16 18:00 | 11175.5641 | -0.048233 | 31.26 | 26.75 | 60.74 | 40.49 | 25 | 0.97 | 2.72 | 16.42
2018-01-16 19:00 | 11267.3491 | -0.048233 | 35.02 | 24.11 | 57.9 | 30.74 | 25.12 | 0.97 | 3.5 | 16.25
2018-01-16 20:00 | 10022.4542 | -0.048233 | 21.84 | 22.35 | 56.88 | 26.59 | 7 | 0.97 | 1 | 4.14
2018-01-16 21:00 | 10937.1341 | -0.048233 | 21.25 | 21.25 | 54.96 | 25.14 | 6 | 0.97 | 1 | 3.11
2018-01-16 22:00 | 9784.0042 | -0.048233 | 17.33 | 19.94 | 57.8 | 23.79 | 5.11 | 0.97 | 14.11 | 3
2018-01-16 23:00 | 9688.0542 | -0.048233 | 17.21 | 18.34 | 46.2 | 22.8 | 4.07 | 0.01 | 4 | 3
2018-01-17 | 9624.4042 | -0.048233 | 17.29 | 18.13 | 37.37 | 20.46 | 4.07 | 0.01 | 3.5 | 3
2018-01-17 01:00 | 9574.0542 | -0.048233 | 15.25 | 15.25 | 34.77 | 19.8 | 4 | 0.01 | 3.5 | 2.61
2018-01-17 02:00 | 9558.8542 | -0.048233 | 16.77 | 17.17 | 33.39 | 19.68 | 3 | 0.01 | 2.99 | 1.23
2018-01-17 03:00 | 10672.3291 | -0.048233 | 15.86 | 16.8 | 16.76 | 19.4 | 3 | 0.47 | 1 | 1.16
2018-01-17 04:00 | 10870.6691 | -0.048233 | 15.58 | 17.01 | 33.62 | 19.84 | 3 | 0.47 | 1 | 1.25
2018-01-17 05:00 | 11821.2241 | -0.048233 | 17.14 | 18.96 | 33.24 | 21.45 | 3 | 0.47 | 2.99 | 3
2018-01-17 06:00 | 12448.7542 | -0.048233 | 17.1 | 20.83 | 38.68 | 25.88 | 4.08 | 0.48 | 112.7434 | 4.08
2018-01-17 07:00 | 13478.8294 | 1.2415 | 253.4457 | 21.32 | 40.37 | 24.55 | 20.01 | 1.51 | 25.02 | 35.72
2018-01-17 08:00 | 14328.4221 | 88.5496 | 687.3111 | 20.86 | 45.6 | 24.83 | 5.77 | 2.4 | 1.56 | 3
2018-01-17 09:00 | 14641.1995 | 103.789 | 20.61 | 21.57 | 47.86 | 24.33 | 5.73 | 5.61 | 1 | 3.93
2018-01-17 10:00 | 14362.461 | 102.38 | 21.42 | 21.42 | 54.95 | 24.73 | 5.41 | 5.61 | 1 | 3
2018-01-17 11:00 | 14886.5 | 484 | 17.12 | 21.49 | 48.35 | 24.9 | 5 | 2.4 | 27.24 | 3
2018-01-17 12:00 | 15504.303 | 865.319 | 16.47 | 22.52 | 46.33 | 25.5 | 4.8 | 1 | 3.11 | 3
2018-01-17 13:00 | 15205.5765 | 1007.87 | 15.71 | 22.34 | 44.54 | 25.73 | 3.25 | 1 | 2 | 2.9
2018-01-17 14:00 | 15673.9556 | 1007.83 | 7.11 | 22.95 | 40.76 | 26.57 | 3.25 | 1 | 2 | 2.49
2018-01-17 15:00 | 13601.207 | 790.06 | 14.18 | 21.81 | 42.33 | 25.9 | 4 | 1 | 2 | 1.43
2018-01-17 16:00 | 14363.2363 | 467.442 | 7.57 | 21.43 | 57.68 | 27.3 | 3.94 | 1 | 1.34 | 1.56
2018-01-17 17:00 | 13506.2976 | 71.1778 | 16.7 | 23.4 | 58.85 | 42.12 | 3.33 | 1 | 1 | 2
2018-01-17 18:00 | 12122.9042 | -0.048233 | 17.6 | 30.22 | 53.64 | 46.2 | 25 | 1.65 | 2.54 | 22.22
2018-01-17 19:00 | 11937.6542 | -0.048233 | 17.52 | 32.21 | 54.05 | 35 | 26.34 | 1.33 | 3.5 | 21.41
2018-01-17 20:00 | 11703.9542 | -0.048233 | 16.71 | 23.29 | 47.61 | 31.02 | 6.07 | 1.22 | 1 | 3.83
2018-01-17 21:00 | 12748.5691 | -0.048233 | 16.41 | 22.32 | 44.84 | 25.58 | 4.08 | 0.93 | 1 | 3
2018-01-17 22:00 | 12433.1241 | -0.048233 | 15.45 | 21.48 | 38.69 | 24.14 | 3.33 | 0.93 | 25 | 2.93
2018-01-17 23:00 | 10745.4042 | -0.048233 | 15.27 | 20.86 | 33.21 | 23.47 | 5 | 0.01 | 4 | 3
2018-01-18 | 10509.8042 | -0.048233 | 17.14 | 19.93 | 17.22 | 21.68 | 4.32 | 0.01 | 3.5 | 2
2018-01-18 01:00 | 11673.5241 | -0.048233 | 17.18 | 20.01 | 13.29 | 20.44 | 3.61 | 0.01 | 2.84 | 2
2018-01-18 02:00 | 10446.1542 | -0.048233 | 18.43 | 19.93 | 13.33 | 20.29 | 3 | 0.01 | 2.61 | 1.23
2018-01-18 03:00 | 10278.9542 | -0.048233 | 17.87 | 19.82 | 13.17 | 20.41 | 3 | 0.3 | 2 | 1.16
2018-01-18 04:00 | 11640.8191 | -0.048233 | 17.43 | 19.99 | 13.43 | 21.07 | 3.61 | 0.3 | 2 | 1.25
2018-01-18 05:00 | 12702.1491 | -0.048233 | 19.81 | 19.81 | 20.57 | 23.39 | 4 | 0.46 | 2.99 | 2.61
2018-01-18 06:00 | 13329.4042 | -0.048233 | 51.01 | 22.65 | 21.78 | 30.75 | 4.32 | 0.46 | 35 | 4.32
2018-01-18 07:00 | 15570.1069 | 9.3951 | 32.08 | 32.08 | 21.69 | 28.15 | 37.23 | 8.96 | 11.03 | 37.23
2018-01-18 08:00 | 15685.3623 | 393.642 | 33.76 | 30.62 | 21.82 | 28.04 | 24.08 | 2.61 | 1 | 24.01
2018-01-18 09:00 | 16316.8336 | 742.193 | 34.19 | 30.86 | 22.29 | 27.56 | 12.63 | 2.81 | 1 | 11.76
2018-01-18 10:00 | 14671.5634 | 989.751 | 35.08 | 35.08 | 23.36 | 29.03 | 7.33 | 2.5 | 1 | 5.19
2018-01-18 11:00 | 15950.1757 | 1158.65 | 20.7 | 25.12 | 24.38 | 27.97 | 4.74 | 7.1 | 112.7434 | 4.48
2018-01-18 12:00 | 14953.6175 | 1158.65 | 19.96 | 26.36 | 23.92 | 27.97 | 4.32 | 1.43 | 2.11 | 3.27
2018-01-18 13:00 | 16948.6488 | 1150.07 | 17.81 | 24.8 | 22.51 | 27.24 | 4.32 | 1 | 2.11 | 3
2018-01-18 14:00 | 15563.36 | 969 | 17.1 | 22.11 | 21.77 | 26.58 | 4.32 | 1 | 2.11 | 3
2018-01-18 15:00 | 13354.9855 | 758.754 | 16.82 | 21.55 | 22.27 | 26.37 | 3.79 | 0.97 | 2.11 | 2.61
2018-01-18 16:00 | 11348.9432 | 394.256 | 16.75 | 21.36 | 32.22 | 24.62 | 3.25 | 0.97 | 1.05 | 2.46
2018-01-18 17:00 | 12079.4954 | 78.7587 | 17.02 | 21.92 | 40.63 | 33.92 | 3.25 | 0.97 | 1 | 2.61
2018-01-18 18:00 | 10852.7542 | -0.048233 | 18.25 | 25.34 | 39.28 | 31.57 | 25 | 0.97 | 2.11 | 23.86
2018-01-18 19:00 | 11973.1441 | -0.048233 | 17.09 | 22.93 | 33.54 | 25.65 | 25 | 0.97 | 3.5 | 11.97
2018-01-18 20:00 | 10562.0542 | -0.048233 | 15.9 | 23.04 | 31.06 | 25.1 | 22.73 | 0.97 | 1 | 3.11
2018-01-18 21:00 | 10307.4542 | -0.048233 | 15.3 | 20.39 | 22.49 | 24.89 | 3.82 | 0.91 | 1.55 | 3
2018-01-18 22:00 | 10039.5542 | -0.048233 | 13.65 | 20.22 | 21.86 | 22.43 | 4.72 | 0.91 | 112.7434 | 2.74
2018-01-18 23:00 | 10791.5441 | -0.048233 | 8.99 | 19.66 | 17 | 21.25 | 25 | 0.01 | 10.03 | 2.61
2018-01-19 | 10727.1891 | -0.048233 | 7.53 | 19.76 | 19.19 | 18.4 | 30.83 | 0.01 | 7.92 | 1.14
2018-01-19 01:00 | 10636.4591 | -0.048233 | 6.39 | 18.91 | 19.43 | 16.02 | 3 | 0.01 | 3.5 | 2.61
2018-01-19 02:00 | 9396.4042 | -0.048233 | 5.93 | 18.36 | 18.42 | 15.04 | 3 | 0.01 | 2.5 | 2.11
2018-01-19 03:00 | 10468.7141 | -0.048233 | 6.87 | 17.96 | 18.47 | 15.12 | 2.91 | 0.25 | 1.5 | 2
2018-01-19 04:00 | 10655.4491 | -0.048233 | 7.83 | 18.26 | 18.99 | 17.38 | 3 | 0.25 | 1.5 | 2.11
2018-01-19 05:00 | 11744.2091 | -0.048233 | 14.43 | 19.47 | 21.4 | 20.74 | 3 | 0.25 | 3.5 | 3
2018-01-19 06:00 | 14445.0091 | -0.048233 | 14.82 | 22.28 | 32.38 | 29.02 | 6.14 | 0.25 | 35 | 14.21
2018-01-19 07:00 | 14353.0138 | 9.4356 | 16.44 | 23.73 | 33.75 | 28.29 | 32 | 0.71 | 10 | 34.22
2018-01-19 08:00 | 13683.8209 | 399.022 | 15.51 | 21.03 | 31.76 | 25.58 | 22 | 0.71 | 1 | 12.48
2018-01-19 09:00 | 14224.1761 | 755.817 | 16.28 | 23.61 | 32.02 | 24.42 | 23.82 | 0.7 | 1.26 | 4.09
2018-01-19 10:00 | 14345.4655 | 1002.49 | 15.59 | 21.68 | 35.11 | 23.1 | 4.66 | 0.7 | 2 | 3.75
2018-01-19 11:00 | 15796.1457 | 1158.65 | 13.07 | 20.16 | 35.17 | 22.47 | 6.35 | 0.65 | 3.01 | 3.1
2018-01-19 12:00 | 13961.8175 | 1158.65 | 15.18 | 19.63 | 32.59 | 23.01 | 4.32 | 0.65 | 3.01 | 3
2018-01-19 13:00 | 13688.2175 | 1158.65 | 14.37 | 16.72 | 30.7 | 22.91 | 4.32 | 0.65 | 2.5 | 2.05
2018-01-19 14:00 | 12504.147 | 1005.26 | 13.97 | 18.34 | 24.21 | 22.75 | 4.32 | 0.65 | 2.5 | 2.61
2018-01-19 15:00 | 13620.9373 | 797.841 | 12.35 | 18.24 | 30.7 | 23.2 | 23.47 | 0.5 | 2.5 | 1.43
2018-01-19 16:00 | 13061.6069 | 488.67 | 12.53 | 19.34 | 35.97 | 23.43 | 23.1 | 0.5 | 1.5 | 1.56
2018-01-19 17:00 | 11258.9143 | 81.4887 | 13.37 | 21.21 | 47.6 | 41.78 | 22.68 | 0.5 | 1 | 2.05
2018-01-19 18:00 | 12281.2041 | -0.048233 | 15.73 | 34.04 | 43.1 | 36.31 | 25.01 | 0.5 | 2.16 | 24.81
2018-01-19 19:00 | 10848.9542 | -0.048233 | 14.71 | 21.54 | 38.73 | 24.31 | 21.84 | 0.5 | 2.5 | 14.31
2018-01-19 20:00 | 11862.3691 | -0.048233 | 13.4 | 21.21 | 34.18 | 23.78 | 20.81 | 0.5 | 1 | 4.87
2018-01-19 21:00 | 10496.5042 | -0.048233 | 13.56 | 21.21 | 34.79 | 21.58 | 5.67 | 0.5 | 2.5 | 3.16
2018-01-19 22:00 | 10110.8042 | -0.048233 | 13.11 | 20.55 | 22.8 | 17.94 | 26 | 0.5 | 11.62 | 3
2018-01-19 23:00 | 9825.8042 | -0.048233 | 12.97 | 13.54 | 20.12 | 11.24 | 40 | 0.01 | 8.2 | 2.74
2018-01-20 | 9858.1042 | -0.048233 | 14.52 | 16.13 | 20.6 | 10.86 | 17.48 | 0.01 | 9.22 | 2.46
2018-01-20 01:00 | 9918.9042 | -0.048233 | 8.23 | 8.23 | 20.46 | 7.96 | 4.19 | 0.01 | 11.5 | 1.11
2018-01-20 02:00 | 9851.4542 | -0.048233 | 9.11 | 9.11 | 20.4 | 6.95 | 4.25 | 0.01 | 12 | 1
2018-01-20 03:00 | 10825.3041 | -0.048233 | 8.03 | 8.03 | 20.39 | 7.12 | 4.25 | 0.25 | 12 | 0.9
2018-01-20 04:00 | 10007.2542 | -0.048233 | 8.26 | 8.26 | 20.8 | 12.39 | 4.32 | 0.25 | 12 | 1.25
2018-01-20 05:00 | 10950.6042 | -0.048233 | 13.97 | 13.97 | 22.69 | 17.63 | 4.32 | 0.25 | 9.36 | 1.55
2018-01-20 06:00 | 14221.3491 | -0.048233 | 19.24 | 19.24 | 37.33 | 26.91 | 15.5 | 0.25 | 10 | 15.5
2018-01-20 07:00 | 14786.4527 | 8.595 | 19.64 | 20.24 | 38.08 | 24.72 | 32 | 0.66 | 15.36 | 32
2018-01-20 08:00 | 13933.1921 | 361.518 | 17.9 | 21.06 | 37.95 | 24.35 | 19 | 0.66 | 3.11 | 12.35
2018-01-20 09:00 | 14584.9121 | 505.539 | 18.6 | 21.84 | 35.74 | 24.52 | 19 | 0.66 | 1 | 5.81
2018-01-20 10:00 | 16164.001 | 762.328 | 20.3 | 21.4 | 35.31 | 23.8 | 19 | 0.66 | 1 | 4.86
2018-01-20 11:00 | 15903.0689 | 822.999 | 17.21 | 20.78 | 31.98 | 23.7 | 19 | 0.6 | 3.5 | 3.1
2018-01-20 12:00 | 16471.9787 | 1137.25 | 19.17 | 20.03 | 30.67 | 25 | 4.64 | 0.6 | 3.5 | 2.69
2018-01-20 13:00 | 15583.7985 | 745.373 | 17.72 | 19.8 | 29.6 | 25.68 | 4.46 | 0.6 | 2.67 | 2.98
2018-01-20 14:00 | 13271.2483 | 957.735 | 16.85 | 17.11 | 24.25 | 26.02 | 4.83 | 0.65 | 3.46 | 3
2018-01-20 15:00 | 12356.9768 | 585.344 | 16.08 | 19.18 | 29.99 | 26.11 | 4.5 | 0.5 | 3.5 | 2.81
2018-01-20 16:00 | 11930.5693 | 316.494 | 16.28 | 19.52 | 37.94 | 28.88 | 4.5 | 0.5 | 2 | 2.5
2018-01-20 17:00 | 12594.6691 | 76.075 | 19.53 | 21.33 | 47.92 | 39.62 | 5 | 0.5 | 0.71 | 2.45
2018-01-20 18:00 | 11244.1542 | -0.048233 | 19.48 | 23.8 | 41.93 | 33.11 | 29 | 0.5 | 3.5 | 28.8
2018-01-20 19:00 | 11073.1542 | -0.048233 | 17.33 | 24.18 | 38.1 | 23.74 | 24 | 0.5 | 10 | 17.18
2018-01-20 20:00 | 10872.7042 | -0.048233 | 16.93 | 23.02 | 39.5 | 25.1 | 5.1 | 0.5 | 1.24 | 3.1
2018-01-20 21:00 | 10661.8042 | -0.048233 | 13.9 | 24.01 | 32.96 | 22.63 | 5 | 0.5 | 3.27 | 2.44
2018-01-20 22:00 | 11367.5741 | -0.048233 | 16.74 | 33.83 | 30.56 | 18.58 | 33.45 | 0.5 | 23 | 2.18
2018-01-20 23:00 | 9948.3542 | -0.048233 | 13.59 | 22.16 | 23.2 | 15.88 | 28 | 0.01 | 37.5 | 22
2018-01-21 | 10904.4291 | -0.048233 | 7.63 | 22.26 | 22.18 | 17.04 | 26 | 0.01 | 25 | 3
2018-01-21 01:00 | 9782.1042 | -0.048233 | 14.39 | 22.38 | 22.21 | 15.89 | 35 | 0.01 | 12 | 2
2018-01-21 02:00 | 10656.5041 | -0.048233 | 13.93 | 22.04 | 22.37 | 13.64 | 35 | 0.01 | 12 | 1.31
2018-01-21 03:00 | 9542.7042 | -0.048233 | 14.74 | 21.72 | 22.4 | 13.22 | 24 | 0.25 | 11.36 | 1.2
2018-01-21 04:00 | 9806.8042 | -0.048233 | 15.27 | 21.83 | 22.45 | 14.64 | 24 | 0.25 | 11.7 | 1.36
2018-01-21 05:00 | 10308.4042 | -0.048233 | 14.85 | 21.93 | 25.21 | 16.75 | 24 | 0.25 | 12 | 3
2018-01-21 06:00 | 11847.5991 | -0.048233 | 14.73 | 24.05 | 40.78 | 20 | 36 | 0.25 | 52.6962 | 33.09
2018-01-21 07:00 | 11807.5091 | -0.048233 | 43.27 | 43.27 | 44.29 | 21.12 | 38 | 0.5 | 112.7434 | 38
2018-01-21 08:00 | 11950.8288 | 53.7998 | 14.66 | 23.19 | 39.79 | 20.83 | 25.01 | 0.51 | 12.84 | 5
2018-01-21 09:00 | 12141.2119 | 78.2577 | 14.83 | 24.42 | 39.69 | 22.3 | 22 | 0.51 | 3.11 | 4
2018-01-21 10:00 | 12119.2081 | 104.401 | 13.4 | 24.5 | 38.57 | 22.59 | 22 | 0.6 | 3.46 | 3.1
2018-01-21 11:00 | 12105.4804 | 132.389 | 12.48 | 25.83 | 35.38 | 23.08 | 4.07 | 0.5 | 112.7434 | 3.1
2018-01-21 12:00 | 12282.3976 | 136.083 | 13.85 | 23.04 | 32.92 | 22.77 | 25.01 | 0.5 | 12.58 | 3
2018-01-21 13:00 | 11141.9562 | 132.375 | 13.46 | 21.71 | 32.29 | 23.27 | 4.07 | 0.5 | 10 | 3
2018-01-21 14:00 | 12208.709 | 113.236 | 11.66 | 20.64 | 30.42 | 22.9 | 4 | 0.5 | 4.11 | 3
2018-01-21 15:00 | 10982.8379 | 124.882 | 9.14 | 16.81 | 31.27 | 22.51 | 3.5 | 0.5 | 3.5 | 2.65
2018-01-21 16:00 | 12401.9714 | 87.4231 | 9.35 | 20.82 | 38.61 | 22.88 | 3.25 | 0.5 | 3.37 | 2.61
2018-01-21 17:00 | 12152.9598 | 9.3931 | 10.6 | 23.28 | 49.16 | 28.9 | 3.5 | 0.5 | 3.01 | 3
2018-01-21 18:00 | 10768.2042 | -0.048233 | 16.07 | 19.66 | 44.53 | 27.48 | 27.55 | 0.5 | 16.33 | 27
2018-01-21 19:00 | 11788.5191 | -0.048233 | 17 | 20.86 | 40.47 | 21.67 | 23 | 0.5 | 19.8 | 17.07
2018-01-21 20:00 | 10416.7042 | -0.048233 | 20.72 | 20.72 | 37.95 | 20.51 | 31 | 0.5 | 10 | 3.98
2018-01-21 21:00 | 10112.7042 | -0.048233 | 18.59 | 18.59 | 35.24 | 20 | 26 | 0.5 | 14.76 | 4
2018-01-21 22:00 | 9820.1042 | -0.048233 | 13.72 | 13.72 | 32.86 | 17.73 | 31 | 0.5 | 12.26 | 3
2018-01-21 23:00 | 10478.2091 | -0.048233 | 10.52 | 10.52 | 30.44 | 15.8 | 31 | 0.01 | 52.6962 | 22
2018-01-22 | 9356.5042 | -0.048233 | 6.81 | 6.81 | 19.39 | 13.09 | 31 | 0.01 | 25.38 | 2.5
2018-01-22 01:00 | 10197.5791 | -0.048233 | 0.1 | 1.87 | 17.91 | 9.05 | 40 | 0.01 | 20.5 | 1.34
2018-01-22 02:00 | 8948.9542 | -0.048233 | -0.79 | 0.45 | 17.83 | 7.23 | 40 | 0.01 | 21.6 | 0.15
2018-01-22 03:00 | 8803.6042 | -0.048233 | -0.53 | -0.15 | 18 | 7.57 | 32 | 0.25 | 13.43 | 0.01
2018-01-22 04:00 | 9683.7941 | -0.048233 | -0.52 | -0.52 | 17.85 | 7.36 | 32 | 0.25 | 12.92 | 1
2018-01-22 05:00 | 8673.4542 | -0.048233 | -0.29 | -0.29 | 17.93 | 7.34 | 32 | 0.25 | 28.59 | 2
2018-01-22 06:00 | 8694.3542 | -0.048233 | 4.12 | 4.12 | 32.07 | 17.64 | 34 | 0.25 | 118.5734 | 36
2018-01-22 07:00 | 9545.5891 | -0.048233 | 5.21 | 5.21 | 37.47 | 18.9 | 38 | 0.5 | 63.0362 | 50
2018-01-22 08:00 | 8556.9668 | 42.3335 | 3.7 | 3.7 | 36.73 | 20.26 | 30 | 0.5 | 40 | 17.06
2018-01-22 09:00 | 9502.7577 | 78.3533 | 8.52 | 8.52 | 35.67 | 21.74 | 30 | 0.58 | 25.62 | 4
2018-01-22 10:00 | 9393.1798 | 104.488 | 16.17 | 16.17 | 34.38 | 22 | 30 | 0.61 | 14.37 | 3.74
2018-01-22 11:00 | 8337.4451 | 140.258 | 12.54 | 12.54 | 33.03 | 22.51 | 30 | 0.5 | 40 | 3.74
2018-01-22 12:00 | 8406.6421 | 136.097 | 15.29 | 15.29 | 31.09 | 22.27 | 3.41 | 0.5 | 40 | 3
2018-01-22 13:00 | 9347.7621 | 132.438 | 16.58 | 16.68 | 30 | 22.64 | 3.25 | 0.5 | 26.98 | 2.85
2018-01-22 14:00 | 9575.2876 | 241.102 | 15.18 | 15.18 | 23.95 | 22 | 3.22 | 0.5 | 23.58 | 2.23
2018-01-22 15:00 | 9548.7997 | 139.995 | 7.69 | 7.69 | 24.19 | 21.94 | 2.63 | 0.5 | 10.48 | 1.85
2018-01-22 16:00 | 10105.4578 | 256.633 | 9.53 | 9.53 | 33.15 | 23.05 | 3.03 | 0.5 | 3.11 | 1.29
2018-01-22 17:00 | 9094.1721 | 30.8127 | 16.5 | 16.5 | 38.5 | 35.03 | 3.25 | 0.5 | 1 | 2.42
2018-01-22 18:00 | 10106.8491 | -0.048233 | 19.8 | 19.8 | 37.24 | 38.62 | 24.18 | 0.5 | 3.11 | 23.63
2018-01-22 19:00 | 10084.6941 | -0.048233 | 20.92 | 20.92 | 34.46 | 29.89 | 27.6 | 0.5 | 13.93 | 24.08
2018-01-22 20:00 | 8986.9542 | -0.048233 | 19.72 | 20.93 | 33.45 | 26 | 12.39 | 0.5 | 1.23 | 3.95
2018-01-22 21:00 | 8847.3042 | -0.048233 | 18.74 | 20.26 | 31.87 | 24.98 | 7.38 | 0.5 | 1.61 | 3.01
2018-01-22 22:00 | 8711.4542 | -0.048233 | 17.42 | 19.43 | 23.94 | 23.56 | 4.55 | 0.5 | 40 | 3
2018-01-22 23:00 | 9529.7641 | -0.048233 | 16.46 | 19.28 | 19.77 | 23.09 | 3.5 | 0.01 | 22 | 3
2018-01-23 | 9403.1641 | -0.048233 | 15.63 | 19.27 | 20.32 | 21.43 | 2.29 | 0.01 | 2.03 | 2.11
2018-01-23 01:00 | 8449.2542 | -0.048233 | 16.01 | 19.18 | 20.19 | 19.98 | 1.61 | 0.01 | 2.33 | 1.52
2018-01-23 02:00 | 8363.7542 | -0.048233 | 15.85 | 19.53 | 19.67 | 20.11 | 2 | 0.01 | 1 | 2
2018-01-23 03:00 | 9192.1641 | -0.048233 | 16.52 | 19.8 | 19.67 | 19.7 | 2 | 0.4 | 0.5 | 1.78
2018-01-23 04:00 | 9679.5741 | -0.048233 | 15.99 | 19.9 | 20.17 | 20.51 | 2 | 0.3 | 0.5 | 1.9
2018-01-23 05:00 | 9830.5542 | -0.048233 | 16.58 | 21.07 | 20.36 | 25.02 | 2.11 | 0.47 | 2.99 | 2.11
2018-01-23 06:00 | 11737.2042 | -0.048233 | 18.18 | 27.47 | 34.85 | 43.02 | 3.53 | 0.5 | 8 | 3.53
2018-01-23 07:00 | 12473.4542 | -0.048233 | 21.48 | 23.1 | 34.47 | 40.34 | 33.22 | 8.66 | 24.31 | 33.02
2018-01-23 08:00 | 12359.6168 | 52.1229 | 22.86 | 28.82 | 33 | 30.65 | 26.05 | 8.22 | 2.61 | 18.4
2018-01-23 09:00 | 12624.5034 | 103.951 | 20.5 | 20.5 | 32.99 | 28.45 | 16.45 | 2.6 | 1 | 12.55
2018-01-23 10:00 | 13904.286 | 112.418 | 20.67 | 22 | 33.26 | 26.26 | 7.66 | 1.22 | 1 | 3.83
2018-01-23 11:00 | 13743.9302 | 321.422 | 18.23 | 21.75 | 32.79 | 25.03 | 6.9 | 0.97 | 3 | 3
2018-01-23 12:00 | 12762.2611 | 133.959 | 17.4 | 20.51 | 31.02 | 24.82 | 5 | 0.97 | 3 | 3
2018-01-23 13:00 | 12728.4857 | 169.406 | 16.69 | 19.52 | 31.08 | 24.27 | 3.85 | 0.97 | 2.61 | 3
2018-01-23 14:00 | 12703.6401 | 127.365 | 15.66 | 19.18 | 24.66 | 25 | 3.25 | 0.97 | 2.61 | 2.9
2018-01-23 15:00 | 11813.0109 | 87.1667 | 14.87 | 19.47 | 29.38 | 24.2 | 2.85 | 0.5 | 2.61 | 1.61
2018-01-23 16:00 | 10378.2092 | 72.4307 | 13.94 | 20.08 | 31.96 | 24.08 | 2.9 | 0.5 | 2.61 | 1
2018-01-23 17:00 | 11321.0386 | 32.8423 | 14.57 | 21.5 | 37.51 | 36.41 | 3.25 | 0.5 | 2.61 | 1
2018-01-23 18:00 | 10239.0542 | -0.048233 | 16.07 | 21.82 | 33.64 | 30.19 | 26.68 | 0.5 | 3 | 24.33
2018-01-23 19:00 | 11369.6841 | -0.048233 | 14.81 | 20.34 | 31.93 | 23.93 | 21.13 | 0.5 | 9.94 | 10.41
2018-01-23 20:00 | 10157.3542 | -0.048233 | 14.26 | 18.84 | 30.38 | 22.53 | 20 | 0.5 | 1.28 | 3.3
2018-01-23 21:00 | 11078.5041 | -0.048233 | 14.66 | 18.25 | 23.92 | 21.67 | 6.67 | 0.5 | 2.77 | 3.11
2018-01-23 22:00 | 10867.5041 | -0.048233 | 12.84 | 12.84 | 21.76 | 17.14 | 21 | 0.5 | 3.98 | 3.11
2018-01-23 23:00 | 9453.4042 | -0.048233 | 6.46 | 6.46 | 19.89 | 14.3 | 25 | 0.01 | 25 | 3
2018-01-24 | 10487.7041 | -0.048233 | 7.06 | 7.06 | 20.11 | 4.27 | 25 | 0.01 | 25 | 2.5
2018-01-24 01:00 | 9318.5042 | -0.048233 | 5.07 | 5.07 | 18.54 | 4.03 | 31 | 0.01 | 25 | 2.11
2018-01-24 02:00 | 9195.0042 | -0.048233 | 4.49 | 4.49 | 18.36 | 4.47 | 31 | 0.01 | 16.68 | 1.11
2018-01-24 03:00 | 9260.5542 | -0.048233 | 5.51 | 5.51 | 18.15 | 4.64 | 31 | 0.25 | 15.55 | 2
2018-01-24 04:00 | 10629.0741 | -0.048233 | 6.78 | 6.78 | 18.96 | 5.43 | 31 | 0.25 | 15.52 | 2
2018-01-24 05:00 | 11911.9541 | -0.048233 | 9.1 | 9.1 | 20.37 | 13.29 | 31 | 0.25 | 25 | 2.11
2018-01-24 06:00 | 14092.6391 | -0.048233 | 16.22 | 16.34 | 21.67 | 22.44 | 28 | 0.25 | 56.8662 | 35
2018-01-24 07:00 | 13432.9542 | -0.048233 | 15.84 | 15.84 | 21.69 | 23.14 | 39 | 0.5 | 53.6962 | 39
2018-01-24 08:00 | 15072.7868 | 42.0017 | 14.43 | 14.43 | 21.89 | 22.29 | 83.5441 | 0.5 | 3 | 3.85
2018-01-24 09:00 | 13780.528 | 112.819 | 17.36 | 19.61 | 29.95 | 23.19 | 25 | 0.5 | 2.11 | 3
2018-01-24 10:00 | 13600.4394 | 112.252 | 15.72 | 17.37 | 34.4 | 20.56 | 25 | 0.5 | 3 | 3
2018-01-24 11:00 | 13579.5546 | 187.268 | 14.94 | 19.83 | 34.93 | 21.23 | 28.31 | 0.5 | 10 | 3
2018-01-24 12:00 | 14063.6014 | 376.791 | 13.73 | 19.67 | 34.18 | 22.21 | 25 | 0.5 | 8.15 | 3
2018-01-24 13:00 | 13763.9173 | 538.334 | 13.02 | 22.86 | 30.75 | 23.2 | 25 | 0.5 | 2.89 | 2.61
2018-01-24 14:00 | 13410.0607 | 163.958 | 10.74 | 28.36 | 24.22 | 27.24 | 25 | 0.5 | 10.89 | 3
2018-01-24 15:00 | 13767.2837 | 144.558 | 12.14 | 28.16 | 28.63 | 29.64 | 3.8 | 0.5 | 3.5 | 2.11
2018-01-24 16:00 | 13727.5155 | 112.863 | 12.74 | 28.25 | 37.12 | 27.44 | 3.57 | 0.5 | 2.35 | 1.61
2018-01-24 17:00 | 12026.7258 | 37.7114 | 12.82 | 21.19 | 43.9 | 40.02 | 3.8 | 0.5 | 2.35 | 3
2018-01-24 18:00 | 11719.1542 | -0.048233 | 15.38 | 25.26 | 37.69 | 29.25 | 50 | 0.5 | 2.35 | 45
2018-01-24 19:00 | 11671.6542 | -0.048233 | 16.36 | 21.53 | 36.78 | 23.56 | 17.05 | 0.5 | 10 | 13.12
2018-01-24 20:00 | 12656.7841 | -0.048233 | 16.2 | 20.22 | 33.37 | 22 | 23 | 0.5 | 2.89 | 3.09
2018-01-24 21:00 | 12538.6241 | -0.048233 | 15.22 | 19.11 | 30.49 | 20.86 | 25 | 0.5 | 3.01 | 3
2018-01-24 22:00 | 10832.8042 | -0.048233 | 12.91 | 20.56 | 23.27 | 18.8 | 31.26 | 0.5 | 19.59 | 2.78
2018-01-24 23:00 | 10538.3042 | -0.048233 | -0.18 | 17.99 | 20.34 | 17.51 | 25 | 0.01 | 57.6962 | 22.02
2018-01-25 | 10529.7542 | -0.048233 | -0.44 | 17.47 | 19.6 | 16.59 | 29.62 | 0.01 | 34.42 | 3
2018-01-25 01:00 | 10379.6542 | -0.048233 | -0.63 | 16.78 | 19.42 | 16.6 | 2.11 | 0.01 | 12 | 2.11
2018-01-25 02:00 | 10316.0042 | -0.048233 | -0.71 | 17.16 | 17.52 | 17.03 | 2 | 0.01 | 1 | 2
2018-01-25 03:00 | 10195.3542 | -0.048233 | 1.28 | 19.43 | 17.31 | 17.69 | 2 | 0.45 | 1 | 2
2018-01-25 04:00 | 11530.0441 | -0.048233 | 4.53 | 19.16 | 17.32 | 19.19 | 2 | 0.45 | 1 | 2
2018-01-25 05:00 | 11333.4542 | -0.048233 | 8.13 | 18.8 | 17.61 | 20.17 | 2.89 | 0.45 | 12 | 2.89
2018-01-25 06:00 | 14620.1391 | -0.048233 | 12.82 | 21.82 | 23.31 | 32.71 | 3 | 0.45 | 22 | 19.87
2018-01-25 07:00 | 13850.5076 | 13.4817 | 16.71 | 22.52 | 30.95 | 29.4 | 25.63 | 1 | 13.04 | 26.34
2018-01-25 08:00 | 15991.7206 | 383.029 | 16.34 | 22.04 | 32.55 | 27.15 | 18.6 | 1.27 | 3.5 | 5.14
2018-01-25 09:00 | 16651.2528 | 676.178 | 19.53 | 22.22 | 28.76 | 26.9 | 5.44 | 1.75 | 3.46 | 3.52
2018-01-25 10:00 | 16974.4172 | 979.495 | 17.58 | 20.94 | 33.51 | 25.24 | 5.02 | 1.15 | 3.5 | 3.91
2018-01-25 11:00 | 15196.9695 | 1114.81 | 17.08 | 20.97 | 36.12 | 25.85 | 3.9 | 0.97 | 22 | 3
2018-01-25 12:00 | 16882.7957 | 1158.65 | 18.02 | 20.86 | 33.68 | 24.65 | 3 | 0.97 | 15 | 3
2018-01-25 13:00 | 14129.9485 | 1122.63 | 18.05 | 20.94 | 31.25 | 24.66 | 3 | 0.97 | 3.5 | 2.5
2018-01-25 14:00 | 13397.299 | 1016.42 | 17.31 | 20.48 | 29.03 | 22.9 | 3 | 0.97 | 11 | 2.24
2018-01-25 15:00 | 12830.8131 | 789.119 | 18.57 | 20.53 | 31.36 | 23.19 | 3 | 0.5 | 3.5 | 1.61
2018-01-25 16:00 | 12068.4361 | 458.617 | 17.56 | 20.02 | 33.88 | 23.12 | 2.35 | 0.5 | 3.19 | 1
2018-01-25 17:00 | 12530.9693 | 110.696 | 17.65 | 20.03 | 43.58 | 39.32 | 3 | 0.5 | 2.73 | 1.61
2018-01-25 18:00 | 12158.8241 | -0.048233 | 21.18 | 22.32 | 41.55 | 36.41 | 22.71 | 0.5 | 4.4 | 21.69
2018-01-25 19:00 | 10765.3542 | -0.048233 | 19.81 | 29.27 | 42.96 | 27.93 | 23 | 0.5 | 8.55 | 13.84
2018-01-25 20:00 | 11650.3141 | -0.048233 | 17.08 | 21.4 | 38.65 | 27.76 | 4.09 | 0.5 | 1 | 3.58
2018-01-25 21:00 | 11263.1291 | -0.048233 | 16.38 | 20.82 | 33.69 | 25.07 | 3.8 | 0.5 | 2.68 | 2.85
2018-01-25 22:00 | 10853.7891 | -0.048233 | 16 | 21.5 | 30.35 | 23.08 | 3.8 | 0.5 | 12.22 | 2.5
2018-01-25 23:00 | 10377.9841 | -0.048233 | 13.38 | 20.85 | 29.8 | 22.86 | 3 | 0.25 | 3.34 | 2.99
2018-01-26 | 9248.2042 | -0.048233 | 7.1 | 20.82 | 21.79 | 19.55 | 3 | 0.25 | 3.95 | 1.01
2018-01-26 01:00 | 10153.2691 | -0.048233 | 8.54 | 20.56 | 21.71 | 19.26 | 1.61 | 0.01 | 3.5 | 1.61
2018-01-26 02:00 | 9019.2542 | -0.048233 | 11.65 | 20.95 | 20.91 | 19.27 | 1.61 | 0.01 | 1 | 1
2018-01-26 03:00 | 9996.0741 | -0.048233 | 12.32 | 20.55 | 20.65 | 19.63 | 1.61 | 0.45 | 1 | 1
2018-01-26 04:00 | 10404.3591 | -0.048233 | 10.76 | 20.91 | 23.1 | 20.42 | 1.89 | 0.45 | 1 | 1
2018-01-26 05:00 | 10507.9042 | -0.048233 | 14.3 | 20.27 | 31.21 | 23.42 | 2 | 0.45 | 3.44 | 2
2018-01-26 06:00 | 12176.1042 | -0.048233 | 15.95 | 21.9 | 54.91 | 43.4 | 3 | 0.47 | 7.15 | 3
2018-01-26 07:00 | 13201.1715 | 1.97 | 16.54 | 23.49 | 47.25 | 35.83 | 28.52 | 1.25 | 16.98 | 28.32
2018-01-26 08:00 | 13291.506 | 113.059 | 16.07 | 23.38 | 41.4 | 30.56 | 16.43 | 1.61 | 3.5 | 12.08
2018-01-26 09:00 | 14789.2865 | 160.281 | 16.09 | 23.38 | 42.68 | 26.33 | 5.59 | 1.77 | 1.51 | 5
2018-01-26 10:00 | 13564.8239 | 660.762 | 16.04 | 22.09 | 50.45 | 25.47 | 4.46 | 0.97 | 2 | 3.98
2018-01-26 11:00 | 12761.521 | 381.18 | 16.57 | 21.39 | 50.39 | 24.42 | 3.8 | 0.8 | 25 | 3
2018-01-26 12:00 | 13010.326 | 1052.08 | 12.93 | 21.8 | 46.43 | 23.85 | 3.8 | 0.8 | 15.45 | 2.61
2018-01-26 13:00 | 12919.2685 | 1112.23 | 12.84 | 21.73 | 44.94 | 23.03 | 3 | 0.8 | 2.7 | 3
2018-01-26 14:00 | 13149.9768 | 976.433 | 12.52 | 21.41 | 41.69 | 22.42 | 3 | 0.8 | 3.01 | 2.92
2018-01-26 15:00 | 11382.5931 | 755.677 | 13.04 | 21.03 | 41.75 | 22.15 | 3 | 0.5 | 2.7 | 2.15
2018-01-26 16:00 | 11020.665 | 487.7 | 13.92 | 20.99 | 45.85 | 22.5 | 3 | 0.5 | 1 | 1.66
2018-01-26 17:00 | 10532.2976 | 110.629 | 15.7 | 21.09 | 57.41 | 29.11 | 3 | 0.5 | 1 | 2.22
2018-01-26 18:00 | 10354.0042 | -0.048233 | 162.41 | 22.57 | 51.78 | 32.35 | 20.7 | 0.5 | 2.23 | 19.57
2018-01-26 19:00 | 11449.8641 | -0.048233 | 20.81 | 22.86 | 47.44 | 30.06 | 19.73 | 0.5 | 2 | 19.28
2018-01-26 20:00 | 10224.8042 | -0.048233 | 21.75 | 22.34 | 44.76 | 28.27 | 4.07 | 0.5 | 1 | 3.81
2018-01-26 21:00 | 11086.9441 | -0.048233 | 20.51 | 22.05 | 40.97 | 25.88 | 3.8 | 0.5 | 1 | 2.66
2018-01-26 22:00 | 10673.3841 | -0.048233 | 14.57 | 21.93 | 37.5 | 23.04 | 3.8 | 0.5 | 3.5 | 2.61
2018-01-26 23:00 | 9281.4542 | -0.048233 | 13.35 | 21.75 | 40.02 | 22.77 | 3 | 0.01 | 3.42 | 3
2018-01-27 | 10256.6591 | -0.048233 | 14 | 21.82 | 31.24 | 21.6 | 3 | 0.25 | 3.5 | 2.21
2018-01-27 01:00 | 9145.6042 | -0.048233 | 15.97 | 21.21 | 15.32 | 20.88 | 2 | 0.01 | 3 | 1
2018-01-27 02:00 | 9057.2542 | -0.048233 | 14.24 | 20.96 | 13.89 | 20.81 | 2 | 0.01 | 1 | 0.01
2018-01-27 03:00 | 10056.2091 | -0.048233 | 13.17 | 21.2 | 13.91 | 21.4 | 2 | 0.25 | 1 | 0.01
2018-01-27 04:00 | 10492.9791 | -0.048233 | 12.41 | 21.63 | 17.23 | 22.36 | 2 | 0.25 | 1 | 0.21
2018-01-27 05:00 | 10570.6042 | -0.048233 | 11.78 | 20.95 | 30.21 | 23.66 | 2 | 0.25 | 2.78 | 2
2018-01-27 06:00 | 13705.4541 | -0.048233 | 22.53 | 22.53 | 38.07 | 44.34 | 3 | 0.25 | 4 | 3
2018-01-27 07:00 | 13040.9016 | 14.2648 | 54.37 | 25.95 | 41.92 | 34.01 | 39.96 | 10 | 3.11 | 39.96
2018-01-27 08:00 | 13507.1912 | 394.096 | 20.56 | 23.43 | 40.65 | 28.36 | 23.27 | 1.61 | 1.05 | 19.64
2018-01-27 09:00 | 13557.2628 | 639.803 | 20.38 | 23.32 | 48.38 | 26.6 | 6.59 | 1.61 | 1.07 | 4.11
2018-01-27 10:00 | 13457.5518 | 972.844 | 72.95 | 22.47 | 49.02 | 25.39 | 4 | 0.82 | 1.98 | 3
2018-01-27 11:00 | 14398.2707 | 1158.65 | 182.09 | 19.55 | 50.05 | 24.5 | 3 | 0.61 | 3.46 | 1.61
2018-01-27 12:00 | 13000.2655 | 1095.49 | 195.44 | 19.28 | 47.71 | 24.69 | 3 | 0.61 | 3.01 | 1
2018-01-27 13:00 | 13019.864 | 1153.12 | 199.14 | 20.74 | 46.29 | 23.48 | 3.25 | 0.61 | 2.63 | 1
2018-01-27 14:00 | 13306.2613 | 949.57 | 144.17 | 20.74 | 43.11 | 22.44 | 3.25 | 0.61 | 2 | 1
2018-01-27 15:00 | 12879.7343 | 847.279 | 17.18 | 19.91 | 40.4 | 21.48 | 2.61 | 0.5 | 2 | 1
2018-01-27 16:00 | 11216.8077 | 515.166 | 17.37 | 20.48 | 48.82 | 21.52 | 2.61 | 0.5 | 1.12 | 0.68
2018-01-27 17:00 | 10634.889 | 124.62 | 17.97 | 21.16 | 54.19 | 26.39 | 3 | 0.5 | 1 | 1
2018-01-27 18:00 | 10396.7542 | -0.048233 | 196.66 | 35.27 | 49.11 | 29.05 | 6 | 0.5 | 2 | 6
2018-01-27 19:00 | 11440.3691 | -0.048233 | 192.65 | 29.47 | 47.93 | 27.36 | 8 | 0.5 | 3.5 | 6
2018-01-27 20:00 | 11155.5191 | -0.048233 | 299.3557 | 27.61 | 44.53 | 25.13 | 6.54 | 0.5 | 1.17 | 3
2018-01-27 21:00 | 10734.5741 | -0.048233 | 186.18 | 23.43 | 40.01 | 23.58 | 4 | 0.5 | 1.4 | 2.51
2018-01-27 22:00 | 10336.8391 | -0.048233 | 18.01 | 22.15 | 35.9 | 22.89 | 3.6 | 0.5 | 3.5 | 2.51
2018-01-27 23:00 | 10036.1641 | -0.048233 | 16.92 | 21.91 | 34.51 | 22.02 | 3.25 | 0.01 | 10 | 1.87
2018-01-28 | 9920.1141 | -0.048233 | 16.48 | 20.79 | 34.68 | 22.3 | 2.61 | 0.01 | 3.98 | 1.01
2018-01-28 01:00 | 8820.7042 | -0.048233 | 16.21 | 20.22 | 34.6 | 20.94 | 2 | 0.01 | 3.5 | 0.01
2018-01-28 02:00 | 8811.2042 | -0.048233 | 15.63 | 19.21 | 32 | 20.01 | 2 | 0.01 | 1 | 0.01
2018-01-28 03:00 | 9786.1291 | -0.048233 | 16.41 | 20.64 | 32.79 | 19.7 | 2 | 0.25 | 1 | 0.01
2018-01-28 04:00 | 9134.2042 | -0.048233 | 16.84 | 18.41 | 32.9 | 19.73 | 2 | 0.25 | 1.69 | 0.01
2018-01-28 05:00 | 10734.5741 | -0.048233 | 17.01 | 18.81 | 38.17 | 22.5 | 2.01 | 0.25 | 3.46 | 1.5
2018-01-28 06:00 | 11380.2341 | -0.048233 | 43.95 | 19.71 | 45.99 | 26.8 | 4 | 0.25 | 4 | 4
2018-01-28 07:00 | 10461.3907 | 13.9902 | 178.28 | 22.12 | 42.91 | 31.17 | 34.87 | 1.61 | 8.94 | 34.87
2018-01-28 08:00 | 10859.0035 | 323.53 | 42.78 | 22.07 | 45.54 | 30.38 | 17.38 | 1.61 | 2 | 17.12
2018-01-28 09:00 | 12403.7099 | 450.071 | 19.85 | 23.62 | 42.98 | 30.64 | 7.43 | 1.61 | 1 | 5.32
2018-01-28 10:00 | 12002.2075 | 361.5 | 20.46 | 23.71 | 45 | 29.2 | 5.71 | 1.06 | 1.81 | 4.94
2018-01-28 11:00 | 10303.6886 | 146.988 | 20.2 | 22.76 | 44.64 | 24.99 | 5.46 | 0.66 | 3.46 | 4.67
2018-01-28 12:00 | 11719.0877 | 364.14 | 18.55 | 21.65 | 38.49 | 21.6 | 4 | 0.6 | 2.34 | 1.69
2018-01-28 13:00 | 10296.1323 | 266.034 | 17.43 | 20.05 | 36.69 | 20.75 | 2.51 | 0.61 | 2 | 1.01
2018-01-28 14:00 | 10922.6935 | 269.264 | 17.03 | 19.24 | 36.37 | 20.04 | 1.88 | 0.6 | 2.92 | 1.01
2018-01-28 15:00 | 10644.0501 | 225.147 | 16.86 | 18.43 | 36.72 | 19.81 | 1.51 | 0.5 | 2 | 1
2018-01-28 16:00 | 9430.3431 | 135.677 | 16.77 | 17.31 | 43.87 | 20.23 | 1.29 | 0.5 | 1 | 1
2018-01-28 17:00 | 9408.5317 | 55.7176 | 17.07 | 18.54 | 56.9 | 30.94 | 2.11 | 0.5 | 0.61 | 1.01
2018-01-28 18:00 | 9499.9542 | -0.048233 | 18.07 | 22.54 | 54.02 | 34.93 | 6.78 | 0.5 | 2 | 15.24
2018-01-28 19:00 | 9547.4542 | -0.048233 | 18.21 | 22.51 | 47.99 | 28.09 | 16.95 | 0.5 | 2 | 14.95
2018-01-28 20:00 | 9443.9042 | -0.048233 | 18 | 23.16 | 46.86 | 24.76 | 5 | 0.5 | 0.61 | 3
2018-01-28 21:00 | 10311.5191 | -0.048233 | 17.09 | 24.04 | 41.2 | 24.04 | 4.09 | 0.5 | 2 | 2.24
2018-01-28 22:00 | 9147.5042 | -0.048233 | 15.86 | 22.41 | 39.07 | 22.85 | 3.25 | 0.5 | 2.61 | 2.15
2018-01-28 23:00 | 9058.2042 | -0.048233 | 14.26 | 20.98 | 38.41 | 22.92 | 3.25 | 0.01 | 1.88 | 2
2018-01-29 | 10098.4091 | -0.048233 | 12.98 | 20.12 | 39.48 | 20.06 | 3 | 0.01 | 3.15 | 1
2018-01-29 01:00 | 9181.7042 | -0.048233 | 12.71 | 19.81 | 38.01 | 19.19 | 3 | 0.01 | 2.53 | 2.01
2018-01-29 02:00 | 10231.3391 | -0.048233 | 12.67 | 19.57 | 35.77 | 19.28 | 3 | 0.01 | 1 | 1.61
2018-01-29 03:00 | 10216.5691 | -0.048233 | 11.5 | 19.06 | 37.76 | 19.48 | 3 | 0.25 | 1 | 1.61
2018-01-29 04:00 | 9279.5542 | -0.048233 | 13.87 | 19.29 | 37.98 | 19.46 | 3.05 | 0.25 | 1 | 1.89
2018-01-29 05:00 | 9864.7542 | -0.048233 | 16.03 | 19.74 | 40.91 | 20.34 | 3.11 | 0.25 | 3.03 | 2.61
2018-01-29 06:00 | 11166.0691 | -0.048233 | 17.93 | 20.04 | 56.15 | 26.03 | 4.07 | 0.25 | 8 | 4.07
2018-01-29 07:00 | 9843.3081 | 1.377 | 19.62 | 21.11 | 55.73 | 31.02 | 32.72 | 2.2 | 3.98 | 32.52
2018-01-29 08:00 | 10628.6974 | 40.5947 | 16.94 | 21.83 | 47.33 | 31.58 | 6.82 | 2.2 | 2 | 5
2018-01-29 09:00 | 10660.7302 | 75.9575 | 16.49 | 23.1 | 47.18 | 28.26 | 6.35 | 2.12 | 2 | 3.61
2018-01-29 10:00 | 10426.4764 | 127.916 | 17.12 | 23.41 | 41.16 | 26.6 | 6.08 | 1.3 | 2 | 3.51
2018-01-29 11:00 | 10111.7108 | 204.56 | 15.29 | 20.29 | 37.06 | 22.19 | 4 | 0.76 | 3.5 | 3
2018-01-29 12:00 | 9661.5142 | 844.015 | 12.98 | 19.38 | 37.47 | 20.63 | 3.57 | 0.61 | 3.01 | 1.01
2018-01-29 13:00 | 9798.3051 | 176.493 | 12.19 | 19.22 | 33.29 | 20.05 | 2.24 | 0.6 | 2.77 | 1.01
2018-01-29 14:00 | 8888.4119 | 442.223 | 11.94 | 18.5 | 31.71 | 19.41 | 2.01 | 24.27 | 2.74 | 1.01
2018-01-29 15:00 | 9651.8236 | 219.648 | 11.19 | 18.15 | 33.02 | 19.42 | 3.85 | 0.5 | 15 | 1.2
2018-01-29 16:00 | 8733.1752 | 157.816 | 6.51 | 18.48 | 36.85 | 19.92 | 2.01 | 0.5 | 1.21 | 1.01
2018-01-29 17:00 | 8991.3728 | 111.603 | 11.21 | 19.46 | 48.25 | 30.22 | 3.11 | 0.5 | 1 | 1.01
2018-01-29 18:00 | 10008.7341 | -0.048233 | 14.24 | 22.03 | 41.73 | 37.43 | 38.28 | 0.5 | 2 | 14.36
2018-01-29 19:00 | 8949.9042 | -0.048233 | 12.97 | 21.91 | 38.2 | 28.06 | 17.16 | 0.5 | 3.11 | 14.09
2018-01-29 20:00 | 9823.0541 | -0.048233 | 11.59 | 21.41 | 37.53 | 25.46 | 7.18 | 0.5 | 1 | 2.61
2018-01-29 21:00 | 9739.7091 | -0.048233 | 11.67 | 20.53 | 36.7 | 24.88 | 26.45 | 0.5 | 1.45 | 2.01
2018-01-29 22:00 | 9661.6391 | -0.048233 | 12.53 | 19.91 | 30.32 | 22.07 | 25.15 | 0.5 | 3.01 | 2.75
2018-01-29 23:00 | 9560.3591 | -0.048233 | 12.01 | 19.12 | 17.58 | 22.11 | 3.85 | 0.01 | 8.61 | 2.75
2018-01-30 | 8551.8542 | -0.048233 | 12.98 | 18.42 | 31.75 | 19.19 | 3.85 | 0.01 | 2.86 | 2.11
2018-01-30 01:00 | 8642.1042 | -0.048233 | 12.85 | 18.12 | 24.48 | 18.89 | 3 | 0.17 | 2.99 | 2.01
2018-01-30 02:00 | 9625.7691 | -0.048233 | 12.62 | 17.97 | 18.95 | 19.11 | 50 | 0.17 | 1 | 1.2
2018-01-30 03:00 | 8652.5542 | -0.048233 | 13.2 | 18.07 | 19.11 | 19.63 | 50 | 0.5 | 1 | 1.2
2018-01-30 04:00 | 8954.6542 | -0.048233 | 13.67 | 18.83 | 24.46 | 20.28 | 2.49 | 0.5 | 1 | 1.61
2018-01-30 05:00 | 11169.2341 | -0.048233 | 13.25 | 19.78 | 34.83 | 23.01 | 3 | 0.5 | 2.99 | 2.95
2018-01-30 06:00 | 11883.5042 | -0.048233 | 12.1 | 24.28 | 44 | 39.73 | 4 | 0.5 | 8.61 | 17.3
2018-01-30 07:00 | 14240.9677 | 12.5476 | 93.04 | 93.04 | 46.64 | 37.61 | 25 | 2.12 | 4.21 | 24.8
2018-01-30 08:00 | 14727.8844 | 284.08 | 16.04 | 24.73 | 43.45 | 30.91 | 22.75 | 1 | 2 | 4.31
2018-01-30 09:00 | 14688.5698 | 104.815 | 20.02 | 22.48 | 47.37 | 28.05 | 4.17 | 1 | 1 | 4.17
2018-01-30 10:00 | 12836.0114 | 112.591 | 21.54 | 27.72 | 52.71 | 25.22 | 5.29 | 0.99 | 1 | 3.1
2018-01-30 11:00 | 13658.9025 | 132.827 | 16.17 | 22.23 | 51.4 | 23.73 | 5 | 1 | 15 | 1.52
2018-01-30 12:00 | 12398.1194 | 143.652 | 15.26 | 21.9 | 44.12 | 23.6 | 4.1 | 1 | 2.34 | 1.2
2018-01-30 13:00 | 11974.2104 | 140.432 | 14.22 | 21.12 | 42.35 | 22.8 | 3.75 | 1 | 2 | 1.2
2018-01-30 14:00 | 10962.3397 | 129.305 | 12.97 | 21.17 | 40.69 | 22.62 | 3.68 | 1 | 3.01 | 1.2
2018-01-30 15:00 | 11295.2198 | 200.705 | 0 | 21.75 | 41.66 | 22.17 | 3 | 0.51 | 2.34 | 1.2
2018-01-30 16:00 | 11932.2504 | 102.19 | 5.35 | 23.68 | 45 | 22.09 | 3.02 | 0.51 | 1.21 | 1.01
2018-01-30 17:00 | 10487.3406 | 40.3059 | 8.78 | 25.11 | 58.68 | 28.03 | 4 | 0.51 | 1 | 1.2
2018-01-30 18:00 | 10335.0042 | -0.048233 | 12.98 | 25.72 | 53.95 | 30 | 39.99 | 0.6 | 1.69 | 36.99
2018-01-30 19:00 | 10429.0542 | -0.048233 | 12.25 | 22.78 | 48.68 | 24.31 | 26.13 | 0.8 | 2 | 12.42
2018-01-30 20:00 | 11383.3991 | -0.048233 | 5.07 | 22.51 | 45.7 | 23.42 | 24.27 | 0.51 | 2 | 2.61
2018-01-30 21:00 | 10117.4542 | -0.048233 | 11.69 | 20.76 | 41.91 | 23.33 | 22.44 | 0.51 | 3.11 | 2.24
2018-01-30 22:00 | 9839.1042 | -0.048233 | 6.65 | 20.11 | 41.76 | 18.83 | 22 | 0.6 | 8.61 | 2.61
2018-01-30 23:00 | 9596.8542 | -0.048233 | -0.57 | 16.41 | 39.42 | 17.14 | 100.8141 | 0.17 | 20.77 | 3
2018-01-31 | 9477.1542 | -0.048233 | -1.05 | 6.72 | 45.2 | 14.94 | 25 | 0.17 | 9.23 | 2.11
2018-01-31 01:00 | 10438.1191 | -0.048233 | -20 | 6.18 | 44.26 | 14.69 | 27 | 0.01 | 9.67 | 2.61
2018-01-31 02:00 | 10300.9691 | -0.048233 | -11.49 | 2.11 | 42.69 | 15.29 | 100.8141 | 0.01 | 2.23 | 1.65
2018-01-31 03:00 | 9247.2542 | -0.048233 | -9.8 | 16.79 | 42.56 | 17.38 | 100.8141 | 0.25 | 1 | 2.61
2018-01-31 04:00 | 9582.6042 | -0.048233 | -1.35 | 15.43 | 40.11 | 18.54 | 25 | 0.25 | 2.47 | 2.02
2018-01-31 05:00 | 10710.2542 | -0.048233 | -1 | 20.26 | 39.94 | 21.86 | 25 | 0.25 | 10.48 | 3
2018-01-31 06:00 | 13769.8091 | -0.048233 | -0.16 | 20.36 | 39.75 | 34.04 | 39.64 | 0.25 | 32.25 | 39.44
2018-01-31 07:00 | 14513.267 | 19.6512 | 10.03 | 25.09 | 40.69 | 26.66 | 100.9641 | 1.61 | 30 | 100.2662
2018-01-31 08:00 | 13317.6947 | 409.626 | 11.93 | 22 | 44.8 | 31.38 | 40 | 0.99 | 2 | 4
2018-01-31 09:00 | 13826.8168 | 770.544 | 37.93 | 37.93 | 46.96 | 24.78 | 28.7 | 1.2 | 0.71 | 3
2018-01-31 10:00 | 13565.4794 | 991.452 | 16.78 | 23.6 | 52 | 25.73 | 28.23 | 0.97 | 1 | 3.75
2018-01-31 11:00 | 13375.0908 | 929.043 | 17 | 23.01 | 50.59 | 23.54 | 20 | 0.6 | 16.79 | 3.1
2018-01-31 12:00 | 15221.1707 | 1158.65 | 17.32 | 22.94 | 45.92 | 23.36 | 6.55 | 0.6 | 1.49 | 3.1
2018-01-31 13:00 | 14839.2607 | 1158.65 | 17.67 | 23.92 | 43.96 | 23.86 | 16.62 | 0.6 | 57.6962 | 3.1
2018-01-31 14:00 | 13703.0152 | 1003.64 | 17.75 | 23.38 | 42.34 | 23.77 | 20.97 | 0.6 | 29.23 | 3
2018-01-31 15:00 | 13885.2981 | 851.42 | 18.33 | 22.99 | 41.6 | 22.03 | 22.24 | 0.5 | 22 | 2.11
2018-01-31 16:00 | 13003.93 | 534 | 19.22 | 22.38 | 58.16 | 22.96 | 22 | 0.5 | 2.56 | 2.41
2018-01-31 17:00 | 11303.3441 | 135.257 | 20.28 | 21.86 | 61.85 | 33.54 | 4 | 0.5 | 0.51 | 2.96
2018-01-31 18:00 | 12268.5441 | -0.048233 | 23 | 23 | 58.47 | 31.82 | 22.95 | 0.5 | 1 | 22.95
2018-01-31 19:00 | 12130.3391 | -0.048233 | 18.35 | 21.45 | 50 | 22.74 | 24.94 | 0.5 | 2.11 | 24.74
2018-01-31 20:00 | 10810.0042 | -0.048233 | 16.98 | 20.96 | 47.4 | 23.68 | 20.33 | 0.5 | 0.61 | 4
2018-01-31 21:00 | 11785.3541 | -0.048233 | 16.43 | 22.07 | 44.98 | 22.27 | 19.66 | 0.5 | 0.71 | 3.31
2018-01-31 22:00 | 11435.0941 | -0.048233 | 18.66 | 18.77 | 44.56 | 18.93 | 19.88 | 0.5 | 3.5 | 3
2018-01-31 23:00 | 9832.4542 | -0.048233 | 0.43 | 0.43 | 40.1 | 17.58 | 25 | 0.01 | 11.84 | 4
2018-02-01 | 10768.3341 | -0.048233 | 0.02 | 0.02 | 45.98 | 11.92 | 35.31 | 0.01 | 8.61 | 3
2018-02-01 01:00 | 9632.9542 | -0.048233 | -2.32 | -2.32 | 44.79 | 10.8 | 100.8141 | 0.01 | 8.69 | 2.87
2018-02-01 02:00 | 9483.8042 | -0.048233 | -2.33 | -2.33 | 3 | 11.7 | 100.8141 | 0.01 | 1 | 2
2018-02-01 03:00 | 10518.2991 | -0.048233 | -0.86 | -0.86 | 3.07 | 14.84 | 100.8141 | 0.45 | 0.5 | 2
2018-02-01 04:00 | 9772.6042 | -0.048233 | 4.84 | 4.84 | 3.95 | 16.98 | 100.8141 | 0.45 | 3.66 | 2.02
2018-02-01 05:00 | 10649.4542 | -0.048233 | 13.3 | 13.3 | 5.11 | 19.1 | 20 | 0.45 | 4.58 | 2.89
2018-02-01 06:00 | 13848.9341 | -0.048233 | 11.87 | 11.87 | 32.96 | 27.05 | 20 | 0.45 | 17.22 | 19.8
2018-02-01 07:00 | 13100.561 | 15.0642 | 18.05 | 18.83 | 35.52 | 23.81 | 100.1641 | 423.1716 | 11 | 99.4662
2018-02-01 08:00 | 13451.1383 | 275.093 | 16.78 | 17.89 | 33.43 | 23.44 | 29.21 | 29 | 3.46 | 4
2018-02-01 09:00 | 13568.2401 | 112.358 | 15.93 | 18.98 | 42.9 | 25.29 | 23.51 | 23.3 | 1.58 | 4.82
2018-02-01 10:00 | 15158.4436 | 154.193 | 14.86 | 18.98 | 43.31 | 25.28 | 20.21 | 20 | 2.73 | 3.5
2018-02-01 11:00 | 14651.1616 | 138.357 | 14.24 | 19.35 | 43.2 | 27.21 | 4.1 | 1 | 1.16 | 3.08
2018-02-01 12:00 | 15003.0917 | 141.94 | 14.18 | 20.02 | 43.01 | 28.83 | 3.75 | 1 | 2.47 | 3
2018-02-01 13:00 | 13117.6694 | 138.073 | 14.22 | 21.32 | 41.96 | 31.84 | 3 | 1 | 2.68 | 2
2018-02-01 14:00 | 12398.3293 | 134.873 | 12.77 | 21.82 | 40.73 | 34.02 | 2.75 | 1 | 2 | 2.5
2018-02-01 15:00 | 12132.2001 | 108.737 | 11.8 | 22.11 | 41.37 | 33.21 | 2.75 | 1 | 2 | 2.02
2018-02-01 16:00 | 12043.3362 | 114.196 | 10.96 | 21.98 | 44.89 | 32.92 | 2 | 1 | 2 | 1.84
2018-02-01 17:00 | 13055.6461 | 46.02 | 12.77 | 21.66 | 58.64 | 34.12 | 2.59 | 1 | 1 | 1.57
2018-02-01 18:00 | 11537.7042 | -0.048233 | 14.53 | 20.47 | 54.83 | 38.17 | 33.87 | 1 | 0.71 | 14.61
2018-02-01 19:00 | 12805.5391 | -0.048233 | 14.55 | 19.11 | 47.83 | 26.39 | 36.46 | 1 | 1 | 24.03
2018-02-01 20:00 | 11342.0042 | -0.048233 | 15.35 | 18.35 | 47.23 | 23.75 | 24.99 | 1 | 0.5 | 3
2018-02-01 21:00 | 11171.0042 | -0.048233 | 14.09 | 17.45 | 46.89 | 23.1 | 23.06 | 1 | 2.11 | 3.01
2018-02-01 22:00 | 10828.0542 | -0.048233 | 11.96 | 14.48 | 45.33 | 20.77 | 22 | 1 | 8.11 | 3
2018-02-01 23:00 | 11550.0891 | -0.048233 | 7.79 | 7.79 | 45.01 | 20.08 | 25 | 0.01 | 15.71 | 2.62
2018-02-02 | 10323.6042 | -0.048233 | 1.14 | 1.14 | 39.06 | 17.75 | 100.8141 | 0.01 | 14.3 | 2
2018-02-02 01:00 | 11365.4641 | -0.048233 | 0 | 0 | 6.08 | 17.38 | 83.3141 | 0.17 | 10 | 1.29
2018-02-02 02:00 | 10095.6042 | -0.048233 | -0.02 | 1.71 | 4.68 | 17.38 | 83.3141 | 0.17 | 9.5 | 1.27
2018-02-02 03:00 | 10048.1042 | -0.048233 | -0.6 | 3.7 | 4.73 | 17.66 | 35 | 0.61 | 2.91 | 1.28
2018-02-02 04:00 | 11468.8541 | -0.048233 | -0.39 | -0.13 | 7.52 | 18.6 | 83.3141 | 0.71 | 2.93 | 1.28
2018-02-02 05:00 | 12083.9191 | -0.048233 | 7.48 | 7.48 | 45.43 | 20.18 | 83.3141 | 0.61 | 2.95 | 1.85
2018-02-02 06:00 | 14296.2541 | -0.048233 | 7.55 | 18.23 | 51.15 | 25.69 | 31.22 | 0.61 | 15.13 | 28.22
2018-02-02 07:00 | 13141.7743 | 2.4466 | 82.78 | 18.9 | 55.56 | 25.05 | 47.81 | 25 | 11 | 47.81
2018-02-02 08:00 | 15319.1261 | 51.4987 | 12.01 | 18.87 | 53.22 | 25.33 | 26.47 | 20 | 1 | 25.27
2018-02-02 09:00 | 14236.4862 | 150.775 | 0 | 19.65 | 52.11 | 26.51 | 22.75 | 20 | 1 | 5.67
2018-02-02 10:00 | 13701.3009 | 111.422 | 10.09 | 20.9 | 57.28 | 26.61 | 7.9 | 11.25 | 10 | 5.33
2018-02-02 11:00 | 13624.824 | 155.92 | 10.74 | 22.04 | 59.18 | 27.3 | 5 | 1 | 1 | 3
2018-02-02 12:00 | 15315.2915 | 150.864 | 12.16 | 26.41 | 54.38 | 28.81 | 4 | 1 | 1.27 | 3.45
2018-02-02 13:00 | 13891.7189 | 146.862 | 14.23 | 27.48 | 51.74 | 28.86 | 3.21 | 1 | 11.78 | 3.11
2018-02-02 14:00 | 13014.1079 | 120.061 | 14.73 | 23.14 | 49.92 | 28.87 | 2.5 | 1 | 2.14 | 2.5
2018-02-02 15:00 | 14026.8042 | 115.549 | 14.97 | 22.43 | 51.51 | 29.87 | 2 | 1 | 12.1 | 2
2018-02-02 16:00 | 13671.9855 | 130.228 | 15.8 | 23.04 | 61.02 | 30.18 | 2 | 0.99 | 2 | 2
2018-02-02 17:00 | 13021.8895 | 25.0232 | 16.27 | 23.57 | 78.21 | 35.56 | 2 | 1 | 1 | 2
2018-02-02 18:00 | 12865.6741 | -0.048233 | 34.3 | 34.3 | 119.227 | 45.35 | 5 | 1 | 1.3 | 5
2018-02-02 19:00 | 11235.6042 | -0.048233 | 18.54 | 25.16 | 70.34 | 31.38 | 29.28 | 1.55 | 15 | 21.99
2018-02-02 20:00 | 10850.8542 | -0.048233 | 17.76 | 26.9 | 61.61 | 27.94 | 6.38 | 1 | 1 | 3.08
2018-02-02 21:00 | 10603.8542 | -0.048233 | 15.89 | 23.44 | 50.9 | 26.59 | 4.91 | 1 | 1 | 2.7
2018-02-02 22:00 | 11446.6991 | -0.048233 | 13.59 | 21.41 | 45.58 | 23.96 | 4.23 | 1 | 2.11 | 3
2018-02-02 23:00 | 9874.2542 | -0.048233 | 3.61 | 19.89 | 47.09 | 22.66 | 2.61 | 0.25 | 2 | 2.61
2018-02-03 | 9787.8042 | -0.048233 | 8.77 | 19.49 | 43.52 | 21.07 | 26.17 | 0.25 | 2 | 2.16
2018-02-03 01:00 | 9659.5542 | -0.048233 | 9.01 | 18.96 | 38.78 | 20.53 | 2 | 0.25 | 3.49 | 0.01
2018-02-03 02:00 | 9585.4542 | -0.048233 | 11.31 | 18.73 | 38.06 | 18.69 | 2 | 0.25 | 1 | 0.01
2018-02-03 03:00 | 10634.3491 | -0.048233 | 11.15 | 18.79 | 38.7 | 18.74 | 2.11 | 0.62 | 1 | 0.01
2018-02-03 04:00 | 9680.4542 | -0.048233 | 9.95 | 19.5 | 46.16 | 19.06 | 2 | 0.62 | 2.53 | 0.01
2018-02-03 05:00 | 10561.1042 | -0.048233 | 8.09 | 20.38 | 49.25 | 23.93 | 2.05 | 0.62 | 2 | 1
2018-02-03 06:00 | 12242.6042 | -0.048233 | 11.54 | 21.33 | 61.76 | 45.53 | 5.22 | 0.62 | 4.46 | 5
2018-02-03 07:00 | 14547.7054 | 9.2942 | 13.94 | 22.58 | 59.14 | 36.24 | 38.18 | 16.2 | 3.5 | 38.18
2018-02-03 08:00 | 14974.728 | 186.055 | 15.32 | 21.93 | 53.71 | 35.22 | 23.63 | 10 | 1.45 | 22.63
2018-02-03 09:00 | 13454.1755 | 545.29 | 15.44 | 22.49 | 52.08 | 28.76 | 15.85 | 12.02 | 1 | 12.82
2018-02-03 10:00 | 15452.8604 | 603.261 | 15.25 | 22.56 | 52.43 | 25.47 | 4.46 | 6.53 | 2.11 | 3.25
2018-02-03 11:00 | 13301.2264 | 809.291 | 16.43 | 21.67 | 48.1 | 24.31 | 3.25 | 0.99 | 2.11 | 1.8
2018-02-03 12:00 | 15143.532 | 1064.56 | 16.13 | 21.51 | 44.81 | 24.3 | 3.25 | 1.3 | 1.66 | 1.48
2018-02-03 13:00 | 15139.2922 | 1157.04 | 15.42 | 21.2 | 42.72 | 24.56 | 2.89 | 1.34 | 2 | 0.97
2018-02-03 14:00 | 12561.641 | 1041.78 | 14.69 | 20.56 | 40.65 | 24.36 | 2.1 | 1.19 | 2 | 0.83
2018-02-03 15:00 | 12128.3108 | 846.643 | 13.49 | 20.35 | 41.43 | 22.7 | 2 | 0.99 | 2 | 0.54
2018-02-03 16:00 | 12734.9282 | 540.022 | 13.49 | 20.3 | 45.43 | 22.53 | 2.07 | 0.99 | 1.76 | 0.01
2018-02-03 17:00 | 12085.2022 | 141.168 | 14.09 | 20.92 | 55.24 | 34.43 | 2.11 | 1 | 1 | 0.61
2018-02-03 18:00 | 11796.9591 | -0.048233 | 36.14 | 23.32 | 55.05 | 39.43 | 4.31 | 1.42 | 1.13 | 4.31
2018-02-03 19:00 | 11714.6691 | -0.048233 | 17.61 | 23.27 | 49.57 | 24.68 | 20.63 | 1.61 | 10 | 18.63
2018-02-03 20:00 | 11469.9091 | -0.048233 | 17.66 | 23.11 | 47.52 | 24.08 | 5.26 | 1.5 | 1 | 3
2018-02-03 21:00 | 10118.4042 | -0.048233 | 16.46 | 22.57 | 46.8 | 24.33 | 5 | 1.15 | 2.61 | 3
2018-02-03 22:00 | 9799.2042 | -0.048233 | 13.83 | 22.9 | 42.07 | 22.02 | 3.73 | 0.99 | 3.5 | 3
2018-02-03 23:00 | 10660.7241 | -0.048233 | 11.81 | 22 | 37.17 | 22.35 | 3 | 0.25 | 12.9 | 2.28
2018-02-04 | 9321.3542 | -0.048233 | 11.6 | 20.27 | 2.21 | 21.62 | 2.75 | 0.25 | 3.95 | 1.61
2018-02-04 01:00 | 9243.4542 | -0.048233 | 12.65 | 19.74 | 2.18 | 20.5 | 2.25 | 0.25 | 3.31 | 0.01
2018-02-04 02:00 | 9286.2042 | -0.048233 | 11.52 | 19.7 | 2 | 20.5 | 2.27 | 0.25 | 0.5 | 0.01
2018-02-04 03:00 | 9281.4542 | -0.048233 | 12.1 | 19.43 | 1.91 | 20.07 | 2.49 | 0.76 | 0.5 | 0.19
2018-02-04 04:00 | 10495.0891 | -0.048233 | 12.67 | 19.81 | 2.13 | 20.08 | 2.59 | 0.76 | 1 | 1
2018-02-04 05:00 | 10740.9041 | -0.048233 | 13.79 | 19.89 | 40.53 | 20.98 | 3 | 0.76 | 2.4 | 2.5
2018-02-04 06:00 | 10315.0542 | -0.048233 | 36.8 | 20.39 | 44.3 | 23.04 | 3.55 | 0.76 | 4.44 | 3.55
2018-02-04 07:00 | 10314.5365 | 25.4068 | 21.07 | 21.11 | 42.12 | 24.81 | 38.81 | 59.1473 | 2.61 | 38.61
2018-02-04 08:00 | 10669.8775 | 403.45 | 19.49 | 22.26 | 40.33 | 27.55 | 22.56 | 21.76 | 1 | 19.75
2018-02-04 09:00 | 11226.8055 | 738.69 | 21.15 | 22.46 | 39.79 | 34.16 | 7.01 | 9 | 1 | 4.84
2018-02-04 10:00 | 11536.8542 | 797.057 | 16.56 | 21.88 | 37.06 | 27 | 4.78 | 9.71 | 1 | 3.14
2018-02-04 11:00 | 11915.5935 | 1133.73 | 16.17 | 22.51 | 35.92 | 24.66 | 3.6 | 1.45 | 1 | 3.08
2018-02-04 12:00 | 12987.7357 | 1158.65 | 15.56 | 22.52 | 34.19 | 24.07 | 3.01 | 1.91 | 2.23 | 1.61
2018-02-04 13:00 | 13122.2588 | 1139.16 | 15.52 | 21.75 | 31.79 | 23.38 | 2.5 | 2 | 3.38 | 1.29
2018-02-04 14:00 | 11391.811 | 1036.38 | 14.67 | 20.5 | 31.15 | 21.68 | 2.75 | 2 | 3.3 | 1
2018-02-04 15:00 | 10731.0385 | 799.83 | 14.57 | 19.39 | 30.99 | 21.18 | 3.01 | 1 | 3.01 | 1
2018-02-04 16:00 | 11663.543 | 524.491 | 14.29 | 19.25 | 35.04 | 21.1 | 2.75 | 1 | 2.73 | 0.35
2018-02-04 17:00 | 10164.7938 | 143.783 | 15.36 | 20.57 | 47.82 | 28.12 | 2.75 | 1 | 1 | 1
2018-02-04 18:00 | 10141.2042 | -0.048233 | 18.34 | 25.91 | 41.47 | 31.48 | 3.55 | 1.19 | 1 | 3
2018-02-04 19:00 | 11274.7341 | -0.048233 | 19.17 | 21.28 | 35.8 | 23.2 | 15.07 | 1.59 | 10 | 14.87
2018-02-04 20:00 | 11037.3591 | -0.048233 | 19.43 | 20.8 | 37.43 | 22.55 | 5.24 | 1.56 | 1 | 2.61
2018-02-04 21:00 | 10821.0841 | -0.048233 | 17.45 | 21.21 | 34.14 | 21.33 | 3.55 | 1.07 | 3.46 | 2.11
2018-02-04 22:00 | 10643.8441 | -0.048233 | 15.27 | 20.58 | 15.47 | 18.76 | 3.8 | 1.03 | 15 | 2
2018-02-04 23:00 | 9529.4042 | -0.048233 | 13.97 | 21.49 | 14.19 | 17.44 | 3 | 0.17 | 15 | 1.5
2018-02-05 | 10472.9341 | -0.048233 | 10.72 | 18.9 | 33.26 | 15.47 | 3.01 | 0.17 | 8.84 | 1
2018-02-05 01:00 | 10449.7241 | -0.048233 | 10.92 | 18.45 | 32.1 | 13.43 | 3.62 | 0.25 | 10 | 1.68
2018-02-05 02:00 | 9353.6542 | -0.048233 | 11.61 | 18.65 | 15.99 | 12.46 | 3 | 0.25 | 2.47 | 1.43
2018-02-05 03:00 | 10322.0691 | -0.048233 | 12.4 | 18.66 | 16.72 | 13.01 | 3 | 0.8 | 1.63 | 1.68
2018-02-05 04:00 | 9297.6042 | -0.048233 | 13.5 | 18.7 | 31.2 | 16.22 | 3 | 0.8 | 2.6 | 1.89
2018-02-05 05:00 | 9355.5542 | -0.048233 | 14.35 | 19.88 | 36.74 | 16.61 | 3 | 0.8 | 3.96 | 2.5
2018-02-05 06:00 | 9171.2542 | -0.048233 | 59.49 | 18.64 | 39.5 | 20 | 5 | 0.8 | 32 | 25
2018-02-05 07:00 | 9021.1542 | -0.048233 | 17.44 | 19.64 | 51.69 | 20.04 | 46.06 | 23.85 | 15 | 47
2018-02-05 08:00 | 9567.8138 | 410.383 | 16.34 | 21.49 | 48.99 | 21.55 | 26.53 | 8.7 | 1 | 25.53
2018-02-05 09:00 | 10062.2366 | 738.828 | 15.42 | 22.49 | 44.37 | 22.99 | 3.25 | 7.88 | 1 | 2.7
2018-02-05 10:00 | 10344.6659 | 967.122 | 98.29 | 25.95 | 45.83 | 22.88 | 4.5 | 6.31 | 1.77 | 2.01
2018-02-05 11:00 | 11785.6476 | 1118.23 | 11.23 | 24.77 | 45.52 | 24.12 | 3.25 | 1 | 2 | 2.01
2018-02-05 12:00 | 11909.0826 | 1146.23 | 13.07 | 27.47 | 48.48 | 24.51 | 3.01 | 1 | 1.56 | 1.82
2018-02-05 13:00 | 10850.311 | 1144.38 | 13.83 | 23.65 | 43.5 | 22.8 | 3.05 | 1 | 3.1 | 1
2018-02-05 14:00 | 12190.0608 | 1052.56 | 13.88 | 22.15 | 42.37 | 22.27 | 3.05 | 1 | 2 | 1
2018-02-05 15:00 | 10792.6792 | 860.715 | 13.53 | 21.78 | 42.82 | 22.34 | 3.01 | 1 | 2 | 1
2018-02-05 16:00 | 10618.2887 | 549.146 | 13.33 | 21.15 | 48.42 | 20.8 | 3.01 | 1 | 2 | 1
2018-02-05 17:00 | 10108.5861 | 143.617 | 13.26 | 20.54 | 55.82 | 26.83 | 3.01 | 1 | 1 | 1
2018-02-05 18:00 | 9947.4042 | -0.048233 | 15.68 | 21.03 | 55.75 | 40.42 | 5.2 | 1 | 1 | 3
2018-02-05 19:00 | 11115.4291 | -0.048233 | 15.63 | 19.47 | 54.32 | 24.03 | 27.02 | 2 | 10.49 | 30.35
2018-02-05 20:00 | 9891.3542 | -0.048233 | 15.22 | 18.15 | 54.41 | 21.16 | 5.27 | 1.45 | 1 | 2.83
2018-02-05 21:00 | 9813.4542 | -0.048233 | 15.68 | 16.23 | 50.04 | 21.74 | 4.17 | 0.99 | 1 | 2.4
2018-02-05 22:00 | 10938.1891 | -0.048233 | 15.33 | 18.78 | 47.02 | 17.34 | 3.13 | 0.99 | 15 | 2.01
2018-02-05 23:00 | 10763.0591 | -0.048233 | 11.67 | 11.67 | 47.53 | 8.36 | 3.66 | 0.25 | 32 | 22
2018-02-06 | 9570.2542 | -0.048233 | 7.88 | 7.88 | 47.03 | 5.08 | 4.27 | 0.25 | 15 | 1.22
2018-02-06 01:00 | 9651.9542 | -0.048233 | 2.71 | 2.71 | 43.65 | 4.44 | 3.5 | 0.25 | 1.11 | 1
2018-02-06 02:00 | 10640.6791 | -0.048233 | 6.13 | 6.13 | 43.56 | 4.28 | 2 | 0.25 | 1.53 | 0.5
2018-02-06 03:00 | 10611.1391 | -0.048233 | -0.56 | -0.56 | 43.95 | 4.57 | 2 | 0.97 | 2.11 | 0.5
2018-02-06 04:00 | 10895.9891 | -0.048233 | 5.66 | 5.66 | 46.2 | 4.89 | 2 | 0.97 | 2.78 | 0.5
2018-02-06 05:00 | 10877.4542 | -0.048233 | 13.14 | 13.14 | 49.16 | 10.63 | 3.01 | 0.97 | 3 | 1.5
2018-02-06 06:00 | 12671.0542 | -0.048233 | 15.13 | 16.7 | 56.2 | 22.43 | 4.2 | 0.97 | 19.84 | 22
2018-02-06 07:00 | 14907.0991 | -0.048233 | 16.01 | 18.35 | 60.04 | 23.27 | 46.05 | 20.95 | 3.64 | 50
2018-02-06 08:00 | 13925.0753 | 401.974 | 16.17 | 18.49 | 56.84 | 23.06 | 15.01 | 14.41 | 3.11 | 14.9
2018-02-06 09:00 | 16426.7066 | 739.338 | 18.43 | 19.13 | 55.39 | 24.25 | 15.01 | 13.7 | 2.65 | 14.3
2018-02-06 10:00 | 14832.141 | 1005.78 | 16.88 | 20.07 | 54.9 | 23.72 | 5 | 10.45 | 3.11 | 4
2018-02-06 11:00 | 14385.033 | 1148.14 | 14.78 | 19.44 | 52.48 | 24.46 | 3.93 | 1 | 1.97 | 3
2018-02-06 12:00 | 14371.2675 | 1158.65 | 14.36 | 19.07 | 48.61 | 25.22 | 3.29 | 1 | 2.79 | 2.9
2018-02-06 13:00 | 14502.3675 | 1158.65 | 13.53 | 18.93 | 45.66 | 25.07 | 2.75 | 1 | 3.19 | 2.5
2018-02-06 14:00 | 13653.0865 | 1067.67 | 11.97 | 16.79 | 42.28 | 27.62 | 3.25 | 1 | 2.85 | 1
2018-02-06 15:00 | 13169.0596 | 861.168 | 12.67 | 16.22 | 41.81 | 28.9 | 3 | 1 | 2 | 1
2018-02-06 16:00 | 12516.2291 | 530.978 | 12.53 | 18.37 | 45 | 27.26 | 3 | 1 | 2 | 1
2018-02-06 17:00 | 12101.1807 | 156.085 | 15.11 | 19.37 | 56.43 | 34.07 | 3.03 | 0.99 | 2 | 1
2018-02-06 18:00 | 12026.9542 | -0.048233 | 19.2 | 19.8 | 55.24 | 46.33 | 3.62 | 1 | 1.21 | 3.62
2018-02-06 19:00 | 13231.7591 | -0.048233 | 17.86 | 17.86 | 51.74 | 24.98 | 29.19 | 1 | 5 | 31.19
2018-02-06 20:00 | 12827.6941 | -0.048233 | 16.87 | 18.25 | 49.36 | 23.1 | 3.62 | 1 | 2.19 | 3
2018-02-06 21:00 | 11197.6042 | -0.048233 | 16.24 | 16.24 | 47.98 | 21.96 | 3.5 | 0.99 | 3.98 | 2.11
2018-02-06 22:00 | 10898.3542 | -0.048233 | 16.4 | 16.49 | 44.01 | 16.3 | 3.62 | 1 | 8.61 | 2.5
2018-02-06 23:00 | 10589.6042 | -0.048233 | 14.76 | 15.32 | 45.53 | 8.23 | 22.2 | 0.25 | 23.72 | 22
2018-02-07 | 10205.8042 | -0.048233 | 12.53 | 12.53 | 44.67 | 6.96 | 35 | 0.25 | 11.02 | 2.61
2018-02-07 01:00 | 11274.7341 | -0.048233 | 11.09 | 11.09 | 43.33 | 5.31 | 3.51 | 0.25 | 13.19 | 1.7
2018-02-07 02:00 | 10205.8042 | -0.048233 | 10.11 | 10.11 | 39.63 | 4.7 | 2.89 | 0.25 | 2.06 | 1.7
2018-02-07 03:00 | 11304.2741 | -0.048233 | 8.92 | 8.92 | 36.53 | 5.77 | 2.89 | 0.8 | 2.02 | 1.7
2018-02-07 04:00 | 10481.3042 | -0.048233 | 9.77 | 9.77 | 40.82 | 7.01 | 2.89 | 0.8 | 13.37 | 1.7
2018-02-07 05:00 | 12686.3241 | -0.048233 | 13.73 | 13.73 | 36.41 | 14.86 | 2.81 | 0.8 | 10 | 2.5
2018-02-07 06:00 | 13066.2542 | -0.048233 | 13.59 | 13.59 | 39.39 | 22.83 | 3.52 | 0.8 | 36.97 | 22
2018-02-07 07:00 | 15671.9741 | -0.048233 | 15.82 | 15.82 | 43.01 | 22.52 | 18.21 | 18 | 13.11 | 35
2018-02-07 08:00 | 14220.9537 | 139.425 | 14.38 | 14.38 | 44.99 | 23.82 | 7.76 | 11.94 | 3.5 | 5.34
2018-02-07 09:00 | 15142.1393 | 607.094 | 18 | 18 | 48.56 | 25.61 | 17.46 | 13.75 | 1.75 | 14.35
2018-02-07 10:00 | 16665.3792 | 366.568 | 17.22 | 19.47 | 46.59 | 25.19 | 12.04 | 10.75 | 3.01 | 10.8
2018-02-07 11:00 | 14694.258 | 547.64 | 16.57 | 20.49 | 35.43 | 28.13 | 6 | 2.12 | 1.75 | 3
2018-02-07 12:00 | 15151.0845 | 1125.51 | 15.58 | 21.29 | 33.67 | 27.34 | 3.51 | 2.12 | 1.75 | 2.54
2018-02-07 13:00 | 16846.5987 | 1068.34 | 401.3657 | 357.04 | 31.61 | 31.97 | 3.3 | 2 | 3.11 | 2.5
2018-02-07 14:00 | 15234.9554 | 342.716 | 14.9 | 25.76 | 19.03 | 35.67 | 3.33 | 2 | 3.5 | 1
2018-02-07 15:00 | 14486.6513 | 250.423 | 14.33 | 26.86 | 19.02 | 39.02 | 3.01 | 1.33 | 3.45 | 1
2018-02-07 16:00 | 14224.4838 | 199.923 | 13.11 | 26.47 | 31.6 | 35.27 | 3 | 1.5 | 2 | 1
2018-02-07 17:00 | 14222.244 | 156.8 | 12.5 | 22.78 | 44.36 | 37.38 | 3.29 | 1.5 | 2 | 1
2018-02-07 18:00 | 13681.1891 | -0.048233 | 15.22 | 21.32 | 40.77 | 37.68 | 3.51 | 1.4 | 2 | 2.85
2018-02-07 19:00 | 13659.0341 | -0.048233 | 14.45 | 21.03 | 36.12 | 27.54 | 5.12 | 2 | 10.26 | 17.15
2018-02-07 20:00 | 13298.2241 | -0.048233 | 14.68 | 19.91 | 35 | 24.44 | 4.04 | 1.56 | 2.33 | 3
2018-02-07 21:00 | 11706.8042 | -0.048233 | 14.49 | 20.38 | 34.38 | 24.32 | 3.52 | 1.25 | 3.5 | 3
2018-02-07 22:00 | 12573.4391 | -0.048233 | 14.41 | 15.76 | 18.05 | 18.95 | 3.51 | 0.99 | 5.05 | 2.5
2018-02-07 23:00 | 10838.5042 | -0.048233 | 10.32 | 13.36 | 33.34 | 16.64 | 3.52 | 0.25 | 9 | 2.5
2018-02-08 | 11755.8141 | -0.048233 | -0.14 | 12.85 | 16.03 | 13.11 | 3.52 | 0.25 | 9.11 | 1
2018-02-08 01:00 | 11782.1891 | -0.048233 | 4.84 | 9.05 | 13.05 | 10.46 | 3.25 | 0.25 | 10.54 | 1
2018-02-08 02:00 | 10555.4042 | -0.048233 | 2.61 | 2.61 | 11.29 | 8.29 | 3 | 0.25 | 1 | 0.5
2018-02-08 03:00 | 11755.8141 | -0.048233 | 1.62 | 1.98 | 12.25 | 8.5 | 3 | 0.51 | 0.81 | 0.5
2018-02-08 04:00 | 11950.9891 | -0.048233 | 6.35 | 6.35 | 14.48 | 11.48 | 3.25 | 0.51 | 10.68 | 0.5
2018-02-08 05:00 | 11418.0042 | -0.048233 | 8.66 | 8.66 | 33.53 | 16.19 | 3.51 | 0.51 | 8.35 | 1.61
2018-02-08 06:00 | 14415.4691 | -0.048233 | 14.2 | 14.2 | 35.95 | 22.1 | 3.29 | 0.51 | 13 | 3.29
2018-02-08 07:00 | 15600.2341 | -0.048233 | 16.63 | 16.98 | 33.72 | 22.2 | 30.37 | 25.57 | 3.5 | 30.17
2018-02-08 08:00 | 14175.362 | 68.4337 | 15.73 | 16.41 | 35.79 | 22.07 | 5.01 | 10.45 | 3.5 | 4
2018-02-08 09:00 | 16124.4385 | 237.828 | 16.06 | 17.67 | 39.9 | 23.5 | 5.35 | 7.5 | 1.73 | 4
2018-02-08 10:00 | 14759.827 | 395.66 | 16.25 | 17.83 | 39.88 | 25.27 | 5.29 | 7 | 3.46 | 3
2018-02-08 11:00 | 16986.9348 | 1024.36 | 14.97 | 18.61 | 39.88 | 28.37 | 3.86 | 2 | 2.92 | 2.5
2018-02-08 12:00 | 17150.5632 | 674.458 | 14.29 | 19.56 | 38.64 | 30.44 | 3.25 | 1 | 2.84 | 1.61
2018-02-08 13:00 | 18151.8711 | 786.565 | 13.96 | 23.26 | 35.19 | 37.08 | 3.25 | 1.07 | 3 | 1.61
2018-02-08 14:00 | 14361.9793 | 329.873 | 13.79 | 24.85 | 33.43 | 44.98 | 3.25 | 1 | 2 | 1
2018-02-08 15:00 | 13281.455 | 235.479 | 13.91 | 29.73 | 30.85 | 51.39 | 3.01 | 1 | 2 | 1
2018-02-08 16:00 | 14323.0501 | 72.3508 | 14.08 | 29.77 | 35.18 | 42.43 | 3.01 | 1.6 | 2 | 1
2018-02-08 17:00 | 13379.8132 | 43.0139 | 15.08 | 20.25 | 51.07 | 37.16 | 3.01 | 1.5 | 1.38 | 1
2018-02-08 18:00 | 12995.0042 | -0.048233 | 60.02 | 20.7 | 48.63 | 40.76 | 15.01 | 1.45 | 1.75 | 14.86
2018-02-08 19:00 | 14087.3641 | -0.048233 | 21.17 | 21.17 | 37.5 | 28.4 | 20.01 | 2 | 1.75 | 18.03
2018-02-08 20:00 | 13546.1491 | -0.048233 | 21.5 | 21.5 | 35.07 | 27.16 | 6.41 | 2 | 1.75 | 3.11
2018-02-08 21:00 | 11934.8042 | -0.048233 | 60.34 | 20.89 | 36.82 | 23.72 | 5.16 | 1.59 | 1.75 | 3.11
2018-02-08 22:00 | 11442.7042 | -0.048233 | 20.35 | 20.35 | 33.48 | 20.18 | 4.06 | 0.99 | 2.69 | 3.01
2018-02-08 23:00 | 11776.9141 | -0.048233 | 17.14 | 18.76 | 33.99 | 20.39 | 3.92 | 0.25 | 1.75 | 2.5
2018-02-09 | 10112.7042 | -0.048233 | 16.69 | 18.56 | 32.39 | 17.56 | 3.52 | 0.25 | 4.09 | 1
2018-02-09 01:00 | 10963.5091 | -0.048233 | 16.73 | 18.82 | 31.54 | 16.96 | 3.01 | 0.25 | 2.11 | 1.14
2018-02-09 02:00 | 10879.1091 | -0.048233 | 16.56 | 18.16 | 30.87 | 16.66 | 3 | 0.25 | 1.29 | 1
2018-02-09 03:00 | 10756.7291 | -0.048233 | 16.53 | 17.49 | 30.98 | 16.53 | 3 | 0.76 | 2.29 | 1.38
2018-02-09 04:00 | 9811.5542 | -0.048233 | 16.89 | 18.94 | 32.5 | 17.46 | 3 | 0.76 | 2.11 | 1.87
2018-02-09 05:00 | 11762.1441 | -0.048233 | 17.75 | 19.47 | 35.32 | 19.86 | 2.89 | 0.76 | 3.46 | 2.59
2018-02-09 06:00 | 12288.2042 | -0.048233 | 18.66 | 19.84 | 50.19 | 33.06 | 5.22 | 0.76 | 7.95 | 5.22
2018-02-09 07:00 | 14265.6591 | -0.048233 | 21.31 | 24.45 | 44.79 | 28.48 | 34.15 | 29.15 | 1.75 | 34.15
2018-02-09 08:00 | 13406.5757 | 182.185 | 17.5 | 26.57 | 41.02 | 26.5 | 16.52 | 12.98 | 2.55 | 14.98
2018-02-09 09:00 | 14977.5173 | 80.6989 | 18.8 | 31.52 | 40.52 | 24.45 | 5.24 | 9.56 | 2.03 | 4
2018-02-09 10:00 | 12616.1748 | 116.184 | 17.12 | 22.13 | 45.04 | 23.15 | 5.28 | 7.57 | 3.25 | 3
2018-02-09 11:00 | 13609.8228 | 136.306 | 16.55 | 20.98 | 46.48 | 22.86 | 4.01 | 1.15 | 3.02 | 2.88
2018-02-09 12:00 | 12664.9525 | 154.529 | 16.45 | 19.65 | 45.7 | 23.55 | 4.27 | 1.22 | 2.86 | 2.5
2018-02-09 13:00 | 12381.4934 | 143.151 | 16.19 | 18.86 | 43.53 | 23.03 | 3.52 | 1.16 | 2.86 | 1.17
2018-02-09 14:00 | 13186.9345 | 236.464 | 16 | 18.15 | 40.64 | 23.13 | 4.18 | 1.53 | 2.76 | 1
2018-02-09 15:00 | 12901.1762 | 207.603 | 16.05 | 17.86 | 39.75 | 22.32 | 3.52 | 1 | 3.01 | 1
2018-02-09 16:00 | 11301.8279 | 179.661 | 16.44 | 17.99 | 44.76 | 21.82 | 3.52 | 0.99 | 3.01 | 0.91
2018-02-09 17:00 | 11184.5751 | 121.237 | 16.93 | 18.14 | 51.99 | 22.96 | 3.52 | 1 | 2 | 1
2018-02-09 18:00 | 11119.7042 | -0.048233 | 19.01 | 19.01 | 49.92 | 27.46 | 30 | 1.45 | 1.75 | 2.91
2018-02-09 19:00 | 11066.5042 | -0.048233 | 18.41 | 18.41 | 44.19 | 21.98 | 35.01 | 1.45 | 10.38 | 27.55
2018-02-09 20:00 | 10873.6542 | -0.048233 | 15.96 | 15.96 | 41.34 | 20.34 | 20 | 1.61 | 1.75 | 3.01
2018-02-09 21:00 | 10673.2042 | -0.048233 | 16.52 | 17.62 | 38.32 | 20 | 3.67 | 0.99 | 3.39 | 3
2018-02-09 22:00 | 10413.8542 | -0.048233 | 15.77 | 15.77 | 39.05 | 12.49 | 5 | 0.99 | 5 | 2.61
2018-02-09 23:00 | 10126.0042 | -0.048233 | 14.66 | 15.34 | 38.58 | 10.28 | 3.52 | 0.25 | 11 | 2.5
2018-02-10 | 11220.9291 | -0.048233 | 6.6 | 14.42 | 37.1 | 8.03 | 3.52 | 0.25 | 11.52 | 1
2018-02-10 01:00 | 10070.9042 | -0.048233 | 5.38 | 14.1 | 36.59 | 7.65 | 3 | 0.17 | 12 | 1
2018-02-10 02:00 | 10020.5542 | -0.048233 | 2.79 | 13.16 | 35.84 | 6.49 | 3 | 0.17 | 1.58 | 1
2018-02-10 03:00 | 11172.3991 | -0.048233 | 8.6 | 11.01 | 35.91 | 7.37 | 3 | 0.5 | 0.5 | 1
2018-02-10 04:00 | 10418.6042 | -0.048233 | 12.59 | 12.59 | 35.89 | 8.39 | 3 | 0.5 | 2.29 | 1
2018-02-10 05:00 | 11400.9042 | -0.048233 | 11.55 | 11.55 | 50.28 | 12.52 | 3 | 0.5 | 11.03 | 2.36
2018-02-10 06:00 | 13082.4042 | -0.048233 | 16.33 | 16.33 | 59.74 | 21.74 | 4.48 | 0.5 | 23 | 25
2018-02-10 07:00 | 13696.1042 | -0.048233 | 18.98 | 18.98 | 58.82 | 21.95 | 47 | 25.42 | 11.8 | 85.1162
2018-02-10 08:00 | 15709.0386 | 119.084 | 16.87 | 17.37 | 57.69 | 21.2 | 25 | 12.12 | 3.5 | 6.35
2018-02-10 09:00 | 14596.066 | 161.28 | 17 | 31.8 | 56.16 | 22.15 | 25 | 7.5 | 1 | 3.56
2018-02-10 10:00 | 14736.6822 | 254.297 | 43.8 | 43.8 | 57.55 | 22.92 | 7.21 | 7 | 3.5 | 3.08
2018-02-10 11:00 | 16351.7182 | 658.259 | 15.3 | 18.01 | 57.63 | 22.41 | 30 | 0.97 | 3.46 | 2.75
2018-02-10 12:00 | 15220.7879 | 250.882 | 15.29 | 18.17 | 50.22 | 25.29 | 6 | 0.97 | 2.05 | 2.61
2018-02-10 13:00 | 17008.4009 | 458.707 | 14.59 | 17.33 | 41.64 | 25 | 4.81 | 0.99 | 2.43 | 2.5
2018-02-10 14:00 | 15200.7122 | 159.258 | 13.83 | 18.05 | 41.29 | 28.82 | 5.43 | 0.97 | 3.01 | 2.46
2018-02-10 15:00 | 15168.061 | 685.309 | 13.25 | 17.99 | 41.26 | 27.49 | 23 | 0.76 | 3.37 | 1.9
2018-02-10 16:00 | 12985.1738 | 280.604 | 13.31 | 18.15 | 46.15 | 25.32 | 5 | 0.76 | 3.18 | 1.22
2018-02-10 17:00 | 12621.3228 | 56.6029 | 14.19 | 17.77 | 58.08 | 26.6 | 4.15 | 0.97 | 1.24 | 1.7
2018-02-10 18:00 | 13714.9491 | -0.048233 | 15.5 | 18.45 | 58.39 | 28.22 | 20 | 0.97 | 3.05 | 2.85
2018-02-10 19:00 | 13350.9741 | -0.048233 | 14.47 | 16.87 | 58.03 | 21.32 | 45 | 1 | 10.83 | 44.33
2018-02-10 20:00 | 13104.1041 | -0.048233 | 11.37 | 11.37 | 57.62 | 19.72 | 30 | 0.99 | 0.94 | 1.96
2018-02-10 21:00 | 11676.4042 | -0.048233 | 11.9 | 12.47 | 48.83 | 17.6 | 23 | 0.82 | 3.98 | 2
2018-02-10 22:00 | 11383.8042 | -0.048233 | 9.05 | 11.91 | 38.53 | 12.47 | 36 | 0.75 | 10 | 1.87
2018-02-10 23:00 | 12135.6141 | -0.048233 | -0.17 | 15.61 | 37.16 | 10.56 | 35 | 0.25 | 52.6962 | 22
2018-02-11 | 10491.7542 | -0.048233 | 1.28 | 11.86 | 50.82 | 11.36 | 45.01 | 0.25 | 18.45 | 2.75
2018-02-11 01:00 | 10546.8542 | -0.048233 | 7.97 | 8.11 | 51.84 | 7.53 | 3 | 0.25 | 14.24 | 2.5
2018-02-11 02:00 | 11683.0191 | -0.048233 | 1.96 | 5.65 | 51.39 | 5.74 | 3 | 0.25 | 1 | 2.18
2018-02-11 03:00 | 10366.3542 | -0.048233 | 2.94 | 2.94 | 51.73 | 6.99 | 35 | 0.5 | 12 | 2.5
2018-02-11 04:00 | 11787.4641 | -0.048233 | 4.04 | 4.04 | 52.47 | 7.25 | 23.5 | 0.5 | 12.1 | 2.15
2018-02-11 05:00 | 12294.9191 | -0.048233 | 7.48 | 7.48 | 55 | 11.74 | 3 | 0.5 | 11.97 | 2.5
2018-02-11 06:00 | 11732.4542 | -0.048233 | 9.23 | 9.23 | 60.13 | 17.94 | 18 | 0.5 | 28.23 | 22.34
2018-02-11 07:00 | 11689.7042 | -0.048233 | 13.27 | 13.27 | 60.65 | 20.82 | 28.58 | 20 | 11 | 28.58
2018-02-11 08:00 | 13132.4174 | 114.789 | 16.23 | 17.13 | 57.73 | 22.66 | 9.55 | 9.25 | 1.75 | 4.99
2018-02-11 09:00 | 12051.3628 | 196.645 | 16.77 | 18.13 | 56.67 | 22.41 | 4.95 | 7.5 | 0.84 | 4
2018-02-11 10:00 | 13406.5285 | 118.61 | 16.94 | 18.67 | 61.88 | 23.45 | 3.5 | 7.5 | 3.5 | 3
2018-02-11 11:00 | 11944.9152 | 138.595 | 16.41 | 19.39 | 57.47 | 23.66 | 4.4 | 1 | 3.46 | 3.11
2018-02-11 12:00 | 11967.0664 | 149.912 | 15.51 | 19.69 | 56.82 | 26.66 | 3.93 | 1 | 3.11 | 3.03
2018-02-11 13:00 | 11919.8638 | 146.225 | 15.54 | 20.47 | 56.1 | 33.92 | 3.5 | 1 | 3.45 | 3
2018-02-11 14:00 | 11664.764 | 126.699 | 11.33 | 20.78 | 52.66 | 36.39 | 3.61 | 1 | 2.11 | 3.61
2018-02-11 15:00 | 11628.9082 | 101.956 | 11.09 | 21.07 | 53.43 | 37.29 | 3.5 | 1 | 2.71 | 3
2018-02-11 16:00 | 11669.6335 | 74.8247 | 15.5 | 20.82 | 57.68 | 35.92 | 3.5 | 1 | 2.11 | 3
2018-02-11 17:00 | 11699.6483 | 26.4193 | 10.04 | 20.41 | 89.79 | 37.91 | 3.5 | 1 | 2.68 | 2.75
2018-02-11 18:00 | 11490.2042 | -0.048233 | 13.14 | 20.42 | 84.65 | 40.33 | 20 | 1.45 | 2 | 16.95
2018-02-11 19:00 | 11519.6542 | -0.048233 | 15.76 | 19.71 | 77.64 | 25.72 | 23.32 | 1.61 | 8.11 | 22.78
2018-02-11 20:00 | 12567.1091 | -0.048233 | 11.92 | 20.23 | 71 | 23.25 | 4.69 | 1.59 | 2.11 | 3.55
2018-02-11 21:00 | 12290.6991 | -0.048233 | 12.98 | 18.37 | 62.41 | 21.6 | 3.77 | 1 | 3.5 | 3
2018-02-11 22:00 | 12079.6991 | -0.048233 | 15.31 | 17.85 | 57.19 | 18.13 | 5 | 0.99 | 11 | 3
2018-02-11 23:00 | 10652.3042 | -0.048233 | 10.43 | 17.78 | 53.1 | 14.64 | 18 | 0.25 | 22 | 3
2018-02-12 | 11746.3191 | -0.048233 | 9.47 | 17.39 | 60 | 14.32 | 20.25 | 0.25 | 11 | 2.5
2018-02-12 01:00 | 11684.0741 | -0.048233 | 10.42 | 13.76 | 56.84 | 11.84 | 3 | 0.97 | 11.71 | 1.8
2018-02-12 02:00 | 10435.7042 | -0.048233 | 10.92 | 16.91 | 55.63 | 6.79 | 23 | 0.25 | 0.61 | 1.8
2018-02-12 03:00 | 10361.6042 | -0.048233 | 12.4 | 17.75 | 55.08 | 6.67 | 23 | 0.5 | 0.61 | 1.8
2018-02-12 04:00 | 11480.4591 | -0.048233 | 15.15 | 16.72 | 57.16 | 5.13 | 23 | 0.5 | 1 | 1.8
2018-02-12 05:00 | 10373.0042 | -0.048233 | 7.8 | 7.8 | 59.29 | 5.73 | 23 | 0.5 | 11.9 | 2.5
2018-02-12 06:00 | 11440.3691 | -0.048233 | 6.1 | 6.1 | 64.03 | 11.91 | 23 | 0.5 | 52.6962 | 30.69
2018-02-12 07:00 | 10234.3042 | -0.048233 | 8.67 | 8.67 | 78.27 | 12.9 | 40 | 20.86 | 52.6962 | 50
2018-02-12 08:00 | 11556.3652 | 47.9007 | 11.29 | 11.29 | 64.04 | 15.33 | 35 | 8.6 | 2.11 | 4
2018-02-12 09:00 | 11963.1176 | 315.448 | 12.71 | 12.71 | 74.47 | 17.31 | 27 | 7.5 | 2.58 | 16.69
2018-02-12 10:00 | 11980.0789 | 183.525 | 14.3 | 14.3 | 82.96 | 20 | 21 | 7.5 | 25.47 | 3
2018-02-12 11:00 | 12318.7961 | 366.584 | 14.95 | 14.95 | 75.77 | 19.29 | 3.62 | 0.97 | 11 | 3.03
2018-02-12 12:00 | 12120.2346 | 306.374 | 17.01 | 17.07 | 70.89 | 22.16 | 3.02 | 0.9 | 2.61 | 3
2018-02-12 13:00 | 12353.5647 | 477.54 | 17.33 | 20.1 | 63.27 | 24.35 | 3 | 0.9 | 2.61 | 2.5
2018-02-12 14:00 | 11281.0438 | 445.783 | 16.79 | 21.25 | 61.56 | 27.29 | 3.42 | 0.99 | 2.11 | 3
2018-02-12 15:00 | 11210.8075 | 228.85 | 17.07 | 28.95 | 61.64 | 25.28 | 3.33 | 0.99 | 2.96 | 2.85
2018-02-12 16:00 | 12648.7526 | 340.339 | 16.87 | 27.8 | 61.84 | 24.16 | 3 | 0.99 | 2.96 | 2.8
2018-02-12 17:00 | 11138.2525 | 55.4763 | 15.89 | 15.89 | 86.41 | 26.09 | 3.12 | 0.99 | 2.78 | 2.75
2018-02-12 18:00 | 12242.1691 | -0.048233 | 16.38 | 20.34 | 130.667 | 29.11 | 5.57 | 0.99 | 3.11 | 3.52
2018-02-12 19:00 | 10984.8042 | -0.048233 | 15.35 | 21.64 | 75.55 | 24.48 | 20 | 1.09 | 10.03 | 22.61
2018-02-12 20:00 | 12129.2841 | -0.048233 | 13.72 | 20.76 | 70.13 | 21.8 | 5.54 | 1.09 | 1.97 | 3
2018-02-12 21:00 | 10904.0542 | -0.048233 | 14.58 | 19.41 | 61.79 | 21.08 | 5.2 | 0.97 | 2.31 | 2.5
2018-02-12 22:00 | 10705.5042 | -0.048233 | 15.19 | 18.3 | 61.03 | 18.67 | 5.18 | 0.97 | 11 | 2.75
2018-02-12 23:00 | 10538.3042 | -0.048233 | 12.69 | 16.32 | 58.65 | 17.21 | 3 | 0.25 | 39.89 | 2.75
2018-02-13 | 10485.1042 | -0.048233 | 12.22 | 19.23 | 52.08 | 16.78 | 25 | 0.25 | 10.56 | 2.5
2018-02-13 01:00 | 10401.5042 | -0.048233 | 11.45 | 16.74 | 50.66 | 16.12 | 3 | 0.25 | 2.69 | 1
2018-02-13 02:00 | 10232.4042 | -0.048233 | 11.19 | 16.94 | 49.95 | 15.85 | 3 | 0.25 | 1.64 | 1
2018-02-13 03:00 | 11408.7191 | -0.048233 | 12.09 | 16.68 | 50.88 | 16.57 | 3 | 0.97 | 1 | 1
2018-02-13 04:00 | 11659.8091 | -0.048233 | 13.08 | 17.04 | 51.11 | 17.65 | 3 | 0.97 | 2.99 | 1
2018-02-13 05:00 | 12955.3491 | -0.048233 | 15.31 | 18.93 | 59.37 | 19.96 | 3 | 0.97 | 4.35 | 1.79
2018-02-13 06:00 | 14785.7741 | -0.048233 | 16.23 | 19.54 | 62.23 | 23.06 | 16 | 0.97 | 13.3 | 22
2018-02-13 07:00 | 14616.6542 | -0.048233 | 16.22 | 21.94 | 71.78 | 21.99 | 30 | 8.55 | 10.8 | 30
2018-02-13 08:00 | 15030.8137 | 46.9092 | 16.94 | 21.96 | 70.67 | 22.35 | 17.27 | 6.46 | 1.75 | 4.34
2018-02-13 09:00 | 15834.7919 | 342.202 | 20.49 | 20.49 | 76.15 | 23.48 | 6.24 | 7 | 1.75 | 6.04
2018-02-13 10:00 | 19055.3235 | 693.918 | 17.94 | 21.32 | 79.96 | 23.29 | 5.78 | 7.37 | 3.5 | 3.1
2018-02-13 11:00 | 15991.9485 | 1060.63 | 17.01 | 20.91 | 71.2 | 22.59 | 3.8 | 2 | 3 | 3
2018-02-13 12:00 | 18264.8458 | 1158.65 | 16.21 | 20.63 | 67.82 | 22.25 | 3.8 | 1.26 | 2.11 | 3
2018-02-13 13:00 | 16122.8015 | 1132.37 | 14.6 | 20.87 | 63.72 | 22.5 | 3.8 | 1 | 2.61 | 2.61
2018-02-13 14:00 | 15021.3924 | 988.992 | 14.71 | 22.18 | 61.27 | 22.44 | 3.8 | 1.03 | 2.08 | 2.03
2018-02-13 15:00 | 15732.3657 | 800.195 | 14.64 | 21.2 | 61.08 | 21.97 | 3.8 | 1 | 3.33 | 1.76
2018-02-13 16:00 | 12949.2856 | 130.827 | 13.55 | 20.58 | 63.32 | 22.38 | 3.8 | 1.01 | 3.46 | 1
2018-02-13 17:00 | 12850.0353 | 137.353 | 12.1 | 20.6 | 121.667 | 24.81 | 3.8 | 1 | 2.44 | 1
2018-02-13 18:00 | 13938.6091 | -0.048233 | 15.7 | 21.06 | 133.057 | 41.29 | 20 | 1.09 | 2 | 3
2018-02-13 19:00 | 13784.5791 | -0.048233 | 14.03 | 20.83 | 129.117 | 26.87 | 30.71 | 1.51 | 10 | 25.91
2018-02-13 20:00 | 13573.5791 | -0.048233 | 11.31 | 20.31 | 83.13 | 23.88 | 6.53 | 1.45 | 2 | 1.09
2018-02-13 21:00 | 11835.0542 | -0.048233 | 13.93 | 19.24 | 66.04 | 22.93 | 18.25 | 1.37 | 3.5 | 2.75
2018-02-13 22:00 | 11305.9042 | -0.048233 | 8 | 22.65 | 62.9 | 20.23 | 6.15 | 1.21 | 15.86 | 3
2018-02-13 23:00 | 11015.2042 | -0.048233 | 0.23 | 18.56 | 60.4 | 19.89 | 35.01 | 0.25 | 144.8134 | 3
2018-02-14 | 12071.2591 | -0.048233 | -0.31 | 20.04 | 75.81 | 17.63 | 38.25 | 0.25 | 19.23 | 2.24
2018-02-14 01:00 | 10918.3042 | -0.048233 | -0.25 | 20.18 | 73.69 | 16.68 | 3 | 0.25 | 10 | 2.5
2018-02-14 02:00 | 10833.7542 | -0.048233 | -0.72 | 18.26 | 80.59 | 15.73 | 3 | 0.25 | 1.91 | 1.43
2018-02-14 03:00 | 10765.3542 | -0.048233 | -0.99 | 19.04 | 76.35 | 16.42 | 3 | 0.8 | 2.99 | 1.5
2018-02-14 04:00 | 12173.5941 | -0.048233 | -1.03 | 19.63 | 75.55 | 17.1 | 3 | 0.8 | 10.94 | 1.44
2018-02-14 05:00 | 12175.1542 | -0.048233 | -0.44 | 19.99 | 74.38 | 19.28 | 3 | 0.8 | 10.03 | 2
2018-02-14 06:00 | 15285.8441 | -0.048233 | 666.3811 | 398.77 | 74.99 | 23.85 | 30.46 | 0.8 | 107.6734 | 28.46
2018-02-14 07:00 | 14517.8542 | -0.048233 | 11.41 | 21.07 | 65.21 | 24.09 | 17.75 | 11.9 | 26.76 | 85.1162
2018-02-14 08:00 | 15580.2147 | 75.976 | 16.61 | 21.1 | 77.5 | 22.3 | 8.5 | 10.3 | 11.03 | 3.11
2018-02-14 09:00 | 15607.8454 | 88.1663 | 16.47 | 19.7 | 89.95 | 22 | 9.21 | 8.96 | 1 | 3.01
2018-02-14 10:00 | 13942.3121 | 271.118 | 14.38 | 18.51 | 91.34 | 21.75 | 7.41 | 6.32 | 11 | 3.76
2018-02-14 11:00 | 13507.7754 | 317.711 | 12.74 | 18.22 | 91.39 | 20.54 | 5.72 | 1.7 | 2 | 3.16
2018-02-14 12:00 | 15663.6588 | 1112.07 | 14.45 | 18.2 | 118.507 | 19.66 | 5.25 | 1.05 | 2 | 2.95
2018-02-14 13:00 | 14198.1727 | 983.445 | 15.03 | 18.22 | 80.74 | 19.7 | 5 | 1.44 | 3.01 | 3
2018-02-14 14:00 | 13180.3047 | 987.005 | 17.43 | 17.84 | 77.25 | 18.47 | 4.37 | 1.7 | 3.37 | 2.75
2018-02-14 15:00 | 12080.5515 | 745.37 | 16.13 | 16.13 | 70.88 | 18.5 | 4.68 | 0.99 | 3.26 | 2.75
2018-02-14 16:00 | 12834.8283 | 541.714 | 15.68 | 16.12 | 84.54 | 18.94 | 4.01 | 0.99 | 3.37 | 2.75
2018-02-14 17:00 | 12048.0325 | 125.936 | 16.99 | 17.07 | 469.2092 | 22.65 | 3.28 | 0.99 | 1.71 | 2.15
2018-02-14 18:00 | 11810.6741 | -0.048233 | 18.85 | 19.55 | 136.357 | 34.16 | 7.14 | 0.99 | 2 | 12
2018-02-14 19:00 | 11660.8641 | -0.048233 | 18.91 | 21.42 | 118.657 | 25 | 27.1 | 1.45 | 11 | 27.8
2018-02-14 20:00 | 11495.2291 | -0.048233 | 17.87 | 27.7 | 118.207 | 24.76 | 6.4 | 1.45 | 2 | 3.23
2018-02-14 21:00 | 9962.6042 | -0.048233 | 16.12 | 21.69 | 82.18 | 22.19 | 5.19 | 0.99 | 3.98 | 3
2018-02-14 22:00 | 10726.1341 | -0.048233 | 16.12 | 20.6 | 68.13 | 19.21 | 4.38 | 0.99 | 6.48 | 2.66
2018-02-14 23:00 | 9166.5042 | -0.048233 | 8.15 | 20.63 | 61.98 | 19.87 | 3.01 | 0.25 | 12.32 | 3.01
2018-02-15 | 10028.7791 | -0.048233 | 1.67 | 20.18 | 56.02 | 18.05 | 3.01 | 0.25 | 14.6 | 2.75
2018-02-15 01:00 | 9974.9741 | -0.048233 | -0.76 | 18.5 | 54.98 | 17.56 | 2.5 | 0.25 | 4.97 | 2.5
2018-02-15 02:00 | 8875.8042 | -0.048233 | -0.46 | 17.65 | 54.2 | 17.51 | 2.5 | 0.25 | 3.98 | 2.11
2018-02-15 03:00 | 9824.1091 | -0.048233 | 1.17 | 17.06 | 53.88 | 17.5 | 2.5 | 0.62 | 3.5 | 2.5
2018-02-15 04:00 | 9125.6542 | -0.048233 | 2.85 | 17.06 | 54.11 | 18.05 | 2.5 | 0.62 | 3.5 | 2.2
2018-02-15 05:00 | 10330.2542 | -0.048233 | 9.4 | 16.96 | 55.33 | 19.88 | 2.5 | 0.62 | 7.99 | 2.5
2018-02-15 06:00 | 12136.2042 | -0.048233 | 11.96 | 17.57 | 60 | 28.71 | 22.36 | 0.8 | 22.36 | 22.16
2018-02-15 07:00 | 14715.0891 | -0.048233 | 15.34 | 19.61 | 60.04 | 27.76 | 28.64 | 14.81 | 11 | 102.2262
2018-02-15 08:00 | 14776.1129 | 86.7942 | 14.52 | 18.65 | 66.43 | 24.75 | 5.01 | 8.86 | 3.5 | 3.16
2018-02-15 09:00 | 15211.8783 | 122.842 | 17.87 | 18.03 | 78.26 | 23.95 | 5.01 | 1.17 | 1 | 1.99
2018-02-15 10:00 | 14244.6059 | 122.322 | 17.36 | 17.92 | 128.397 | 23.3 | 4.36 | 1.36 | 3.46 | 2.71
2018-02-15 11:00 | 12956.2568 | 228.165 | 17.09 | 20.12 | 85.7 | 22.99 | 3.18 | 1 | 2.53 | 2.32
2018-02-15 12:00 | 15578.7419 | 1048.58 | 17.21 | 19.21 | 119.107 | 22 | 3 | 1 | 3.43 | 1.8
2018-02-15 13:00 | 13927.1995 | 805.137 | 137.55 | 18.36 | 80.85 | 20.96 | 3 | 1 | 3.46 | 1.75
2018-02-15 14:00 | 13314.0367 | 1035.94 | 15.77 | 18.45 | 74.7 | 20.28 | 2.95 | 1 | 3.46 | 1.75
2018-02-15 15:00 | 11444.7668 | 769.123 | 15.52 | 18.25 | 69.71 | 20.68 | 3 | 0.99 | 3.44 | 1.75
2018-02-15 16:00 | 10879.1121 | 543.697 | 131.32 | 18.96 | 73.9 | 21.88 | 3 | 0.99 | 3.18 | 1.75
2018-02-15 17:00 | 10423.4978 | 172.103 | 16.28 | 20.06 | 477.0392 | 23.66 | 3 | 0.99 | 2.31 | 1.75
2018-02-15 18:00 | 10323.6042 | -0.048233 | 18.53 | 20.82 | 527.3992 | 41.02 | 6.36 | 0.99 | 2 | 4.01
2018-02-15 19:00 | 11480.4591 | -0.048233 | 17.52 | 23.29 | 480.6992 | 32.06 | 27.5 | 1.45 | 10 | 27.5
2018-02-15 20:00 | 10098.4542 | -0.048233 | 16.35 | 27.36 | 149.737 | 30.85 | 8 | 1.22 | 2 | 3.43
2018-02-15 21:00 | 11003.5991 | -0.048233 | 14.93 | 22 | 75.52 | 25.42 | 4.42 | 0.99 | 3.5 | 3
2018-02-15 22:00 | 9661.4542 | -0.048233 | 12.84 | 21.2 | 70.63 | 22.06 | 4 | 0.99 | 4.4 | 2.75
2018-02-15 23:00 | 10337.8941 | -0.048233 | 1.68 | 19.04 | 67.85 | 20.31 | 3 | 0.25 | 9.33 | 2.75
2018-02-16 | 9021.1542 | -0.048233 | -0.14 | 17.82 | 60.89 | 18.94 | 3 | 0.25 | 12.29 | 1.7
2018-02-16 01:00 | 8899.5542 | -0.048233 | 0 | 17.07 | 59.6 | 17.78 | 2.35 | 0.25 | 12.93 | 1.11
2018-02-16 02:00 | 8907.1542 | -0.048233 | 3.55 | 16.94 | 58.95 | 17.53 | 2.01 | 0.25 | 2.11 | 1
2018-02-16 03:00 | 9082.9042 | -0.048233 | 7.31 | 16.84 | 59.02 | 17.41 | 2 | 0.62 | 2 | 1
2018-02-16 04:00 | 9460.0542 | -0.048233 | 11.67 | 17.14 | 60.88 | 17.96 | 2 | 0.62 | 3.49 | 1
2018-02-16 05:00 | 11637.6541 | -0.048233 | 13.28 | 18.59 | 64.36 | 21.12 | 2.11 | 0.62 | 9.5 | 1.5
2018-02-16 06:00 | 13700.1791 | -0.048233 | 14.53 | 20.84 | 76.42 | 40.63 | 3 | 0.8 | 57.6962 | 3
2018-02-16 07:00 | 14667.6141 | -0.048233 | 15.94 | 25.5 | 88 | 35.83 | 20.77 | 14.77 | 9.89 | 20.62
2018-02-16 08:00 | 14757.1121 | 144.784 | 14.58 | 20.52 | 88.61 | 27.69 | 6.55 | 11.68 | 3.11 | 4.9
2018-02-16 09:00 | 13967.2239 | 303.341 | 15.24 | 21.03 | 138.437 | 25.34 | 5.4 | 7.5 | 2.2 | 2.91
2018-02-16 10:00 | 15262.4898 | 605.815 | 13.39 | 28.13 | 484.0792 | 24.02 | 4.23 | 7.5 | 3.5 | 3.23
2018-02-16 11:00 | 13536.93 | 1057.4 | 13.48 | 20.5 | 122.287 | 24.02 | 5.18 | 1.81 | 3.01 | 2.8
2018-02-16 12:00 | 16754.0857 | 1158.65 | 14.42 | 20.65 | 77.54 | 23.64 | 4.01 | 1.64 | 1 | 2.45
2018-02-16 13:00 | 14964.7846 | 1121.63 | 16.26 | 20.57 | 75 | 22.49 | 4.41 | 1.02 | 1.61 | 3
2018-02-16 14:00 | 13761.5361 | 1006.11 | 19.09 | 20.48 | 70.51 | 21.73 | 4.86 | 1.2 | 1.05 | 2.79
2018-02-16 15:00 | 11590.0579 | 820.061 | 16.35 | 19.74 | 70.48 | 21.41 | 4 | 0.99 | 1.66 | 2.11
2018-02-16 16:00 | 11040.3861 | 564.459 | 16.61 | 19.76 | 74.83 | 20.89 | 3.9 | 0.99 | 2.32 | 2.01
2018-02-16 17:00 | 10678.1273 | 187.134 | 17.82 | 19.07 | 484.7492 | 21.58 | 3.31 | 0.99 | 1 | 1.5
2018-02-16 18:00 | 10459.4542 | -0.048233 | 19.43 | 19.9 | 524.3292 | 25.92 | 5 | 0.99 | 2.21 | 4.37
2018-02-16 19:00 | 10378.7042 | -0.048233 | 47.83 | 20.4 | 485.3492 | 22.25 | 30.13 | 0.99 | 7.37 | 30.13
2018-02-16 20:00 | 11369.6841 | -0.048233 | 17.47 | 18.33 | 120.427 | 22.22 | 5.31 | 0.99 | 2 | 3.42
2018-02-16 21:00 | 10095.6042 | -0.048233 | 46.91 | 14.86 | 82.78 | 22.23 | 5 | 0.99 | 3.5 | 2.97
2018-02-16 22:00 | 9902.7542 | -0.048233 | 15.92 | 15.92 | 69.75 | 16.59 | 5.79 | 0.99 | 4.07 | 2.5
2018-02-16 23:00 | 10669.1641 | -0.048233 | 12.41 | 12.41 | 62.63 | 12.36 | 3.01 | 0.25 | 15.12 | 2.75
2018-02-17 | 10591.0941 | -0.048233 | 11.29 | 11.29 | 67.02 | 10.45 | 2.99 | 0.25 | 9.97 | 1.7
2018-02-17 01:00 | 9577.8542 | -0.048233 | 10.63 | 10.63 | 67.49 | 9.93 | 3 | 0.25 | 0.61 | 1
2018-02-17 02:00 | 9556.0042 | -0.048233 | 10.52 | 10.52 | 66.74 | 9.32 | 3.49 | 0.25 | 3.11 | 1
2018-02-17 03:00 | 9382.1542 | -0.048233 | 10.65 | 10.65 | 67.84 | 9.27 | 3 | 0.61 | 2.11 | 1
2018-02-17 04:00 | 10882.2741 | -0.048233 | 10.28 | 11.8 | 70.21 | 10.9 | 3 | 0.61 | 9.44 | 1
2018-02-17 05:00 | 10779.6042 | -0.048233 | 12.2 | 14.16 | 82.53 | 12.95 | 3.01 | 0.61 | 1 | 1.79
2018-02-17 06:00 | 12305.3042 | -0.048233 | 40.13 | 22.08 | 467.3092 | 22.69 | 5 | 0.61 | 12.46 | 5
2018-02-17 07:00 | 12908.5542 | -0.048233 | 15.96 | 20.44 | 122.287 | 23.2 | 86.0041 | 23 | 2.81 | 85.3062
2018-02-17 08:00 | 12948.8971 | 102.418 | 13.91 | 19.84 | 121.397 | 23.14 | 45 | 23 | 1.75 | 43
2018-02-17 09:00 | 14912.7404 | 121.299 | 269.4057 | 225.08 | 120.447 | 23.12 | 22.75 | 10.26 | 1.75 | 16.22
2018-02-17 10:00 | 13011.8925 | 145.729 | 29.89 | 23.66 | 133.547 | 23.25 | 5.62 | 7.5 | 2.83 | 2.71
2018-02-17 11:00 | 13000.1448 | 231.363 | 20.96 | 21.37 | 135.967 | 22.51 | 7.56 | 1.69 | 2.56 | 3
2018-02-17 12:00 | 13172.1671 | 249.439 | 69.39 | 20.37 | 122.247 | 22.1 | 4.73 | 1.35 | 2.11 | 3
2018-02-17 13:00 | 13094.876 | 504.08 | 14.31 | 20.72 | 86.77 | 23.2 | 4 | 1.43 | 2.11 | 3
2018-02-17 14:00 | 14320.416 | 995.854 | 15.52 | 21.62 | 77.49 | 23.21 | 3.76 | 1.35 | 2.11 | 3.1
2018-02-17 15:00 | 12239.2813 | 867.454 | 15.48 | 25.22 | 76.55 | 24.1 | 3.25 | 0.99 | 2.61 | 3
2018-02-17 16:00 | 11852.5467 | 592.365 | 65.5 | 25.69 | 126.847 | 24.94 | 3 | 0.99 | 2.11 | 3
2018-02-17 17:00 | 11265.3251 | 212.237 | 251.0757 | 36.1 | 518.4392 | 25 | 2.77 | 1.15 | 2 | 2.48
2018-02-17 18:00 | 12352.9441 | -0.048233 | 118.69 | 118.69 | 514.7592 | 29.6 | 5.54 | 1.45 | 10 | 3.2
2018-02-17 19:00 | 10901.2042 | -0.048233 | 59.51 | 59.51 | 493.2992 | 22.94 | 25 | 1.61 | 7.83 | 26.15
2018-02-17 20:00 | 10707.4042 | -0.048233 | 57.33 | 57.33 | 130.677 | 23.52 | 15 | 1.45 | 2.11 | 2.37
2018-02-17 21:00 | 10553.5042 | -0.048233 | 15.43 | 17.81 | 118.957 | 20.08 | 20 | 0.99 | 8.4 | 2.5
2018-02-17 22:00 | 11296.8891 | -0.048233 | 14.25 | 16.7 | 74.67 | 15.55 | 23.25 | 0.99 | 10.2 | 3.06
2018-02-17 23:00 | 10044.3042 | -0.048233 | 4.25 | 15.14 | 67.42 | 13.13 | 43.25 | 0.25 | 27.93 | 3.7
2018-02-18 | 10747.2341 | -0.048233 | 0.8 | 16.34 | 68.62 | 14.96 | 35.25 | 0.25 | 19.9 | 2.3
2018-02-18 01:00 | 9566.4542 | -0.048233 | -0.41 | 16.98 | 63.67 | 14.55 | 470.3578 | 0.25 | 26.78 | 1.17
2018-02-18 02:00 | 9467.6542 | -0.048233 | -0.69 | 17.3 | 63.4 | 14.94 | 50.3 | 0.25 | 16.48 | 1.08
2018-02-18 03:00 | 10412.7991 | -0.048233 | -0.59 | 17.74 | 64.77 | 14.91 | 50.3 | 0.82 | 15 | 1.08
2018-02-18 04:00 | 10362.1591 | -0.048233 | 4.77 | 18.39 | 68.98 | 17.07 | 45 | 0.8 | 15 | 1.12
2018-02-18 05:00 | 9426.8042 | -0.048233 | 9.3 | 18.22 | 75.1 | 18.71 | 45 | 0.8 | 25.26 | 2.34
2018-02-18 06:00 | 9708.0042 | -0.048233 | 16.56 | 16.56 | 126.737 | 18.93 | 36.02 | 0.8 | 21.67 | 36.02
2018-02-18 07:00 | 10834.7991 | -0.048233 | 14.93 | 17.76 | 127.457 | 20.6 | 41.59 | 11.63 | 11.59 | 41.59
2018-02-18 08:00 | 11421.6526 | 455.211 | 13.07 | 18.62 | 120.137 | 21.87 | 31.04 | 10.53 | 1.75 | 25.86
2018-02-18 09:00 | 10666.6522 | 795.055 | 14.1 | 20.82 | 124.597 | 24.5 | 32.75 | 7.5 | 1 | 5.8
2018-02-18 10:00 | 12243.8974 | 1029.59 | 12.33 | 21.82 | 123.467 | 26.38 | 5.8 | 7 | 2.01 | 4.86
2018-02-18 11:00 | 11279.0175 | 1158.65 | 13.37 | 24.62 | 126.287 | 25.96 | 33.37 | 1 | 2.61 | 4.59
2018-02-18 12:00 | 12656.4657 | 1158.65 | 12.05 | 30.39 | 125.487 | 28.06 | 33.64 | 1 | 2 | 3.11
2018-02-18 13:00 | 12828.4307 | 1158.65 | 11.74 | 26.31 | 83.83 | 36.83 | 3.7 | 1 | 2 | 3
2018-02-18 14:00 | 11683.062 | 1111.96 | 13.05 | 35.86 | 77.21 | 34.76 | 3.86 | 1 | 2 | 3
2018-02-18 15:00 | 11606.4939 | 858.362 | 13.28 | 25.89 | 74.55 | 32.79 | 3.7 | 1 | 1.17 | 1.63
2018-02-18 16:00 | 11169.7722 | 590.655 | 12.55 | 25.77 | 79.22 | 31.34 | 3.7 | 1 | 1 | 2.11
2018-02-18 17:00 | 11885.2987 | 206.686 | 12.09 | 32.16 | 152.597 | 25.13 | 3.7 | 1 | 1 | 1.55
2018-02-18 18:00 | 10423.3542 | -0.048233 | 14.92 | 21.8 | 572.8792 | 28.79 | 35.31 | 1 | 1 | 30.31
2018-02-18 19:00 | 11501.5591 | -0.048233 | 13.37 | 27.27 | 136.187 | 23.23 | 40.81 | 2.01 | 5 | 37.81
2018-02-18 20:00 | 10297.0042 | -0.048233 | 13.78 | 20.89 | 126.547 | 21.78 | 4.02 | 0.99 | 2.11 | 2.76
2018-02-18 21:00 | 10142.1542 | -0.048233 | 12.61 | 20.52 | 82.15 | 20.09 | 25.04 | 0.99 | 11.31 | 3
2018-02-18 22:00 | 9992.0542 | -0.048233 | 12.94 | 19.77 | 75.96 | 16.85 | 22.01 | 1 | 14.29 | 20.01
2018-02-18 23:00 | 11141.8041 | -0.048233 | 6.71 | 20.59 | 71.9 | 14.12 | 47 | 0.25 | 25.53 | 25.53
2018-02-19 | 11096.4391 | -0.048233 | 0.75 | 17.95 | 64.68 | 14.05 | 50 | 0.25 | 23.31 | 2.5
2018-02-19 01:00 | 9936.0042 | -0.048233 | 0.85 | 17.31 | 63.91 | 11.5 | 35.75 | 0.25 | 22.09 | 2.18
2018-02-19 02:00 | 9896.1042 | -0.048233 | -0.31 | 9.17 | 63.99 | 9.79 | 30.75 | 0.25 | 15 | 1.11
2018-02-19 03:00 | 9852.4042 | -0.048233 | -0.76 | 8.9 | 63.74 | 10.35 | 30.75 | 0.8 | 15 | 2.05
2018-02-19 04:00 | 9787.8042 | -0.048233 | -0.69 | 5.83 | 63.22 | 12.4 | 27.75 | 0.8 | 15 | 1.11
2018-02-19 05:00 | 9936.0042 | -0.048233 | -0.45 | 5.67 | 60.78 | 12.57 | 27.75 | 0.8 | 15.59 | 1.49
2018-02-19 06:00 | 11237.8091 | -0.048233 | 8.54 | 8.54 | 71.35 | 17.54 | 33 | 0.8 | 52.6962 | 33
2018-02-19 07:00 | 11228.3141 | -0.048233 | -0.13 | -0.13 | 79.52 | 18.35 | 28.01 | 10 | 15 | 40
2018-02-19 08:00 | 10633.3025 | 449.95 | 12.44 | 14.69 | 84.09 | 19.95 | 4.96 | 2.61 | 1.75 | 4.75
2018-02-19 09:00 | 10958.478 | 763.24 | 14.34 | 14.34 | 85 | 20 | 5.99 | 6.5 | 0.61 | 4.84
2018-02-19 10:00 | 12523.6624 | 1004.77 | 15.03 | 15.03 | 125.757 | 21.37 | 4.8 | 1 | 11 | 3.01
2018-02-19 11:00 | 11324.6175 | 1158.65 | 14.65 | 18.97 | 125.587 | 22.27 | 3.89 | 1 | 2.89 | 2.96
2018-02-19 12:00 | 11467.1175 | 1158.65 | 13.03 | 19.84 | 90.41 | 22.73 | 3.85 | 1 | 3.03 | 3
2018-02-19 13:00 | 11550.7175 | 1158.65 | 16.44 | 20.84 | 79.36 | 24.61 | 4 | 1 | 3.37 | 3
2018-02-19 14:00 | 12904.8655 | 1095.1 | 15.9 | 20.39 | 75.36 | 28.86 | 3.85 | 1 | 2 | 3
2018-02-19 15:00 | 12657.1905 | 854.337 | 16.75 | 18.72 | 71.38 | 31.22 | 3.27 | 1.45 | 3.01 | 3
2018-02-19 16:00 | 12191.3215 | 563.755 | 15.91 | 18.44 | 74.78 | 30.67 | 3.27 | 1.45 | 1 | 3.01
2018-02-19 17:00 | 11878.2334 | 202.989 | 12.95 | 17.68 | 130.757 | 30.1 | 3.85 | 1.5 | 1 | 3
2018-02-19 18:00 | 10404.3542 | -0.048233 | 12.46 | 17.43 | 486.7392 | 51.91 | 6.01 | 2 | 1 | 16
2018-02-19 19:00 | 10347.3542 | -0.048233 | 12.43 | 18.98 | 144.067 | 26.66 | 30.09 | 1.92 | 10.83 | 29.57
2018-02-19 20:00 | 10185.8542 | -0.048233 | 11.53 | 19.66 | 91 | 25.24 | 5.73 | 1 | 0.61 | 3
2018-02-19 21:00 | 11349.6391 | -0.048233 | 10.52 | 17.77 | 79.25 | 21.98 | 4.46 | 0.99 | 11 | 3.01
2018-02-19 22:00 | 10153.5542 | -0.048233 | 687.4911 | 419.88 | 76.51 | 18.94 | 23.25 | 0.99 | 11.76 | 3
2018-02-19 23:00 | 11373.9041 | -0.048233 | 9.45 | 39.41 | 65.11 | 17.7 | 25 | 0.25 | 16.13 | 3
2018-02-20 | 11314.8241 | -0.048233 | -0.25 | 19.48 | 60.4 | 17.48 | 47 | 0.25 | 22.14 | 3
2018-02-20 01:00 | 11097.4941 | -0.048233 | -0.34 | 37.01 | 58.38 | 16.15 | 3.01 | 0.25 | 14.87 | 2.43
2018-02-20 02:00 | 11005.7091 | -0.048233 | -0.17 | 17.9 | 57.06 | 16.07 | 3 | 0.25 | 9.22 | 1.98
2018-02-20 03:00 | 10911.8141 | -0.048233 | -0.32 | 17.83 | 56.87 | 16.16 | 3 | 0.97 | 8.24 | 2.11
2018-02-20 04:00 | 9801.1042 | -0.048233 | 6.12 | 6.12 | 59.26 | 17.55 | 3 | 0.97 | 10.64 | 1.96
2018-02-20 05:00 | 9338.4542 | -0.048233 | 6.11 | 6.11 | 68.1 | 18.57 | 3 | 0.97 | 13.77 | 2.5
2018-02-20 06:00 | 9497.1042 | -0.048233 | -0.52 | 14.87 | 125.757 | 21.99 | 27.04 | 0.97 | 15.15 | 26.84
2018-02-20 07:00 | 10530.9591 | -0.048233 | 9.94 | 16.49 | 138.857 | 20.85 | 30 | 20 | 15.93 | 30
2018-02-20 08:00 | 9920.9127 | 426.066 | 11.81 | 16.64 | 149.967 | 21.28 | 4.82 | 6 | 9.84 | 4.22
2018-02-20 09:00 | 10060.291 | 676.78 | 14.69 | 16.53 | 146.737 | 22.35 | 4.67 | 1 | 1 | 3.68
2018-02-20 10:00 | 10236.7554 | 977.532 | 14.43 | 18.61 | 128.327 | 22.41 | 4 | 10.27 | 10 | 3.95
2018-02-20 11:00 | 10433.5175 | 1158.65 | 15.69 | 17.72 | 144.487 | 22.59 | 4 | 1 | 1.61 | 3
2018-02-20 12:00 | 11269.4499 | 808.943 | 17.49 | 17.64 | 76.56 | 23.03 | 3.75 | 1 | 3.01 | 3
2018-02-20 13:00 | 11197.6234 | 847.861 | 16.3 | 17.18 | 74.34 | 24.05 | 3.75 | 1 | 2.61 | 2.38
2018-02-20 14:00 | 11320.7092 | 1031.53 | 14.09 | 14.09 | 66.15 | 25.55 | 3.75 | 1 | 2.03 | 2.42
2018-02-20 15:00 | 10687.3378 | 509.178 | 15.2 | 16.47 | 66.56 | 26.08 | 3.75 | 1 | 2.03 | 2.61
2018-02-20 16:00 | 9641.4579 | 523.903 | 15 | 16.95 | 71 | 25.26 | 3.75 | 1 | 1.1 | 2.48
2018-02-20 17:00 | 10768.2141 | 200.838 | 13.37 | 17.7 | 120.597 | 28.35 | 3.75 | 1 | 1 | 2.3
2018-02-20 18:00 | 10478.2091 | -0.048233 | 13.42 | 18.09 | 148.067 | 54.63 | 7.01 | 1 | 1 | 6
2018-02-20 19:00 | 10663.8891 | -0.048233 | 14.51 | 19.64 | 124.037 | 36.05 | 34.17 | 1 | 10 | 33.17
2018-02-20 20:00 | 9481.9042 | -0.048233 | 12.07 | 18.89 | 81.6 | 26.47 | 6 | 1 | 1.27 | 4.43
2018-02-20 21:00 | 10478.2091 | -0.048233 | 10.87 | 18.42 | 85.94 | 25.05 | 3.75 | 1 | 3.5 | 2.9
2018-02-20 22:00 | 9227.3042 | -0.048233 | 9.32 | 19.46 | 78.89 | 20.74 | 4 | 1 | 11.93 | 2.9
2018-02-20 23:00 | 9278.6042 | -0.048233 | 12.16 | 18.21 | 75 | 19.06 | 3.75 | 0.25 | 11.09 | 3
2018-02-21 | 9297.6042 | -0.048233 | 11.29 | 17.35 | 67.02 | 16.57 | 25 | 0.25 | 13.02 | 2.9
2018-02-21 01:00 | 10038.2741 | -0.048233 | 8.12 | 18.14 | 64.48 | 14.65 | 3.8 | 0.25 | 11.53 | 1.61
2018-02-21 02:00 | 9040.1542 | -0.048233 | 5.59 | 16.98 | 65.47 | 13.54 | 3 | 0.25 | 1.05 | 1.5
2018-02-21 03:00 | 8930.9042 | -0.048233 | 1.73 | 15.41 | 61.65 | 11.69 | 3 | 0.8 | 1.93 | 1.5
2018-02-21 04:00 | 10429.6791 | -0.048233 | -0.56 | 16.96 | 61.52 | 15.34 | 3 | 0.8 | 8.29 | 1.51
2018-02-21 05:00 | 11469.9091 | -0.048233 | 0 | 18.28 | 62.68 | 17.39 | 3 | 0.8 | 14.1 | 2.75
2018-02-21 06:00 | 11728.6542 | -0.048233 | 9.91 | 17.04 | 64.85 | 22.35 | 25.75 | 0.8 | 162.7434 | 25.75
2018-02-21 07:00 | 12610.2542 | -0.048233 | 10.43 | 19.94 | 65.08 | 20.02 | 28.57 | 25.57 | 18.7 | 99.3062
2018-02-21 08:00 | 14126.69 | 55.2275 | 10.35 | 18.21 | 73.47 | 19.94 | 4.21 | 7.82 | 8.81 | 2.4
2018-02-21 09:00 | 14960.8105 | 138.863 | 11.2 | 20.67 | 73.36 | 20.56 | 4.63 | 8.25 | 2.1 | 3.17
2018-02-21 10:00 | 13733.7415 | 201.57 | 11.34 | 20.8 | 72.67 | 21.28 | 4.1 | 13.02 | 10 | 3.35
2018-02-21 11:00 | 12948.8714 | 255.391 | 12.35 | 20.53 | 64.03 | 20.24 | 4 | 1 | 3.01 | 2.81
2018-02-21 12:00 | 15750.3672 | 448.258 | 11.88 | 17.24 | 62.28 | 20.99 | 4.01 | 1.01 | 2.99 | 1.96
2018-02-21 13:00 | 13839.353 | 1083.74 | 12.7 | 17.6 | 55.71 | 21.87 | 4.01 | 1 | 2.99 | 1.96
2018-02-21 14:00 | 14056.5035 | 1090.7 | 11.57 | 17.55 | 51.19 | 21.83 | 4 | 1 | 2.11 | 2.3
2018-02-21 15:00 | 13494.5134 | 849.008 | 11.17 | 19.46 | 49.44 | 22.58 | 4 | 1 | 2.26 | 2.66
2018-02-21 16:00 | 11777.036 | 569.88 | 11.02 | 21.25 | 54.09 | 23.29 | 4.49 | 1 | 2 | 3
2018-02-21 17:00 | 12565.4804 | 206.408 | 12.38 | 22.99 | 69.17 | 26.17 | 4.34 | 1 | 0.7 | 2.9
2018-02-21 18:00 | 11021.8542 | -0.048233 | 18.21 | 28.02 | 72.55 | 47.09 | 16.15 | 1.45 | 1.2 | 16.15
2018-02-21 19:00 | 10853.7042 | -0.048233 | 18.69 | 28.07 | 67.1 | 24.86 | 28.32 | 3 | 1.75 | 27.31
2018-02-21 20:00 | 11841.2691 | -0.048233 | 1013.1411 | 745.53 | 60.34 | 24.12 | 6.41 | 1.87 | 0.71 | 2.99
2018-02-21 21:00 | 11583.8491 | -0.048233 | 18.17 | 27.69 | 50.5 | 22.98 | 5.86 | 1.23 | 3.31 | 3.21
2018-02-21 22:00 | 10177.3042 | -0.048233 | 15.41 | 21.66 | 52.87 | 19.3 | 4 | 1 | 11 | 3
2018-02-21 23:00 | 10776.7741 | -0.048233 | 14.62 | 20.53 | 46.61 | 18.4 | 25.62 | 0.25 | 12.83 | 4.87
2018-02-22 | 10302.0241 | -0.048233 | 14.75 | 16.56 | 62.61 | 17.87 | 20 | 0.25 | 11.6 | 3
2018-02-22 01:00 | 10065.7041 | -0.048233 | 11.77 | 15.1 | 55.85 | 17.12 | 3.81 | 0.25 | 3.04 | 2
2018-02-22 02:00 | 10060.4291 | -0.048233 | 11.18 | 14.05 | 53.26 | 16.29 | 3.01 | 0.25 | 2.8 | 1.5
2018-02-22 03:00 | 10048.8241 | -0.048233 | 11.02 | 12.62 | 49.97 | 16.37 | 3 | 0.51 | 3.5 | 1.5
2018-02-22 04:00 | 10412.7991 | -0.048233 | 11.56 | 12.95 | 46.03 | 16.31 | 3 | 0.51 | 3.66 | 1.5
2018-02-22 05:00 | 11606.0041 | -0.048233 | 12.63 | 15.8 | 49.71 | 18.3 | 3 | 0.51 | 4.91 | 2.11
2018-02-22 06:00 | 13809.8991 | -0.048233 | 13.49 | 16.85 | 45.9 | 24.02 | 5.11 | 0.51 | 15.69 | 19.8
2018-02-22 07:00 | 12890.5042 | -0.048233 | 15.63 | 18.22 | 45.94 | 21.03 | 28 | 27.79 | 19.09 | 99.2462
2018-02-22 08:00 | 14919.3637 | 226.577 | 15.59 | 16.37 | 55.7 | 20.39 | 4.21 | 9.09 | 3.5 | 3.21
2018-02-22 09:00 | 13687.4043 | 147.794 | 16.43 | 17.23 | 57.3 | 20.93 | 4.02 | 8.25 | 2.44 | 3.82
2018-02-22 10:00 | 15037.9774 | 222.007 | 16.69 | 18.59 | 57.29 | 22.23 | 4 | 10.07 | 3.98 | 3.21
2018-02-22 11:00 | 14918.5609 | 197.816 | 17.95 | 19.33 | 56.71 | 24.08 | 4.16 | 2 | 3.01 | 2.61
2018-02-22 12:00 | 15088.3916 | 176.793 | 18.85 | 19.63 | 57.36 | 25.58 | 4.48 | 2 | 3.04 | 3
2018-02-22 13:00 | 15174.6273 | 187.533 | 18.42 | 22.17 | 51.01 | 29.44 | 4.89 | 1.52 | 3.35 | 3
2018-02-22 14:00 | 12771.5292 | 154.715 | 18.78 | 31.75 | 48.71 | 30.88 | 5 | 1 | 2.38 | 3.1
2018-02-22 15:00 | 12438.0336 | 157.667 | 16.5 | 26.61 | 48.46 | 40.48 | 5 | 1 | 3.01 | 3
2018-02-22 16:00 | 13337.5697 | 68.2462 | 1182.8311 | 915.22 | 52.43 | 32.94 | 4.8 | 1 | 1.86 | 3
2018-02-22 17:00 | 13147.5956 | 38.1759 | 15.51 | 26.49 | 88.02 | 29.59 | 4.42 | 1 | 1 | 2.75
2018-02-22 18:00 | 11308.7542 | -0.048233 | 15.54 | 24.24 | 126.737 | 35.36 | 7.44 | 2 | 1.3 | 5.43
2018-02-22 19:00 | 11353.4042 | -0.048233 | 16.64 | 23.74 | 84.21 | 25.84 | 27.72 | 8.75 | 1.75 | 27.72
2018-02-22 20:00 | 12349.7791 | -0.048233 | 15.62 | 25.01 | 61 | 22.65 | 35 | 2 | 1 | 2
2018-02-22 21:00 | 12023.7841 | -0.048233 | 13.92 | 21.19 | 48.87 | 20 | 5.16 | 1.82 | 1.75 | 4
2018-02-22 22:00 | 11844.4341 | -0.048233 | 12.1 | 21.27 | 51 | 16.24 | 4.46 | 1.4 | 7.13 | 4.46
2018-02-22 23:00 | 10228.6042 | -0.048233 | 9.7 | 15.97 | 46.05 | 12.12 | 6 | 0.25 | 19.63 | 4.13
2018-02-23 | 11189.2791 | -0.048233 | -0.34 | 15.18 | 56.19 | 7.77 | 20 | 0.25 | 11.85 | 3
2018-02-23 01:00 | 9856.2042 | -0.048233 | 3.13 | 3.13 | 59.5 | 4.4 | 15.01 | 0.25 | 13.33 | 2.5
2018-02-23 02:00 | 9839.1042 | -0.048233 | 0 | 0 | 55.28 | 3.22 | 3.8 | 0.25 | 12 | 1.54
2018-02-23 03:00 | 10843.2391 | -0.048233 | -0.22 | 0 | 53.41 | 3.26 | 3.8 | 0.49 | 12 | 2.01
2018-02-23 04:00 | 10311.2542 | -0.048233 | 7.95 | 12.22 | 61.06 | 4.16 | 3.8 | 0.49 | 17.37 | 1.75
2018-02-23 05:00 | 12602.9791 | -0.048233 | 10.97 | 14.57 | 60.68 | 8.59 | 15.01 | 0.49 | 14.93 | 3
2018-02-23 06:00 | 13098.5542 | -0.048233 | 12.21 | 16.85 | 74.79 | 19.33 | 26.07 | 0.61 | 28.12 | 26.07
2018-02-23 07:00 | 13536.5042 | -0.048233 | 14.66 | 18.63 | 471.1092 | 19.38 | 44.52 | 26.25 | 11 | 45
2018-02-23 08:00 | 14096.0848 | 113.984 | 12.8 | 17.07 | 127.397 | 19.57 | 22.35 | 10.46 | 11 | 20.67
2018-02-23 09:00 | 14900.8497 | 335.105 | 14.48 | 19.76 | 76.38 | 19.84 | 15.64 | 10.17 | 3.01 | 11.95
2018-02-23 10:00 | 16403.275 | 272.128 | 123.44 | 19.96 | 69.18 | 22.5 | 17.04 | 10.13 | 11 | 15.04
2018-02-23 11:00 | 16791.7408 | 724.342 | 11.73 | 18.15 | 65.14 | 22.22 | 17.9 | 8.6 | 2 | 16.9
2018-02-23 12:00 | 15328.3649 | 725.121 | 12.96 | 16.8 | 66.24 | 22.83 | 16.24 | 8.6 | 2.11 | 3.1
2018-02-23 13:00 | 16707.824 | 598.8 | 12.31 | 16.84 | 65.96 | 27.9 | 6.62 | 7.98 | 2.11 | 3.23
2018-02-23 14:00 | 14515.1754 | 890.132 | 250.1957 | 16.07 | 64.56 | 30.31 | 8.44 | 6.9 | 2 | 5.76
2018-02-23 15:00 | 13975.3237 | 765.867 | 16.26 | 16.26 | 66.96 | 32.48 | 7.92 | 0.95 | 2.71 | 3.76
2018-02-23 16:00 | 14856.2389 | 507.743 | 10.1 | 16.52 | 126.507 | 32.31 | 6.87 | 0.99 | 2.97 | 3.75
2018-02-23 17:00 | 12749.0931 | 190.098 | 11.51 | 15.55 | 483.4792 | 25.63 | 3.26 | 0.99 | 2.11 | 2.96
2018-02-23 18:00 | 12394.6042 | -0.048233 | 56.99 | 16.6 | 546.0292 | 28.7 | 38.75 | 25 | 2 | 37.75
2018-02-23 19:00 | 13694.9041 | -0.048233 | 94.14 | 17.88 | 522.1792 | 20.79 | 476.1978 | 467.5816 | 5 | 478.3906
2018-02-23 20:00 | 13220.1541 | -0.048233 | 50.21 | 17.76 | 468.0792 | 20.69 | 461.0978 | 455.7316 | 2.11 | 462.3406
2018-02-23 21:00 | 12968.0091 | -0.048233 | 15 | 17.39 | 130.217 | 18.67 | 85.8541 | 23 | 2.54 | 81.7862
2018-02-23 22:00 | 11388.5542 | -0.048233 | 16.5 | 18.26 | 73.86 | 14.9 | 25.41 | 10.05 | 10.78 | 23
2018-02-23 23:00 | 12158.8241 | -0.048233 | 9.18 | 12.58 | 64.21 | 8.5 | 21.51 | 0.25 | 16.06 | 12.44
2018-02-24 | 10656.1042 | -0.048233 | 6.29 | 6.29 | 86.69 | 11.44 | 37 | 0.25 | 25 | 2.52
2018-02-24 01:00 | 10427.1542 | -0.048233 | 7.91 | 9.36 | 78.96 | 7.25 | 20 | 0.25 | 16.22 | 1.55
2018-02-24 02:00 | 11551.1441 | -0.048233 | 4.87 | 7.03 | 78.64 | 5.79 | 20 | 0.25 | 15 | 1.25
2018-02-24 03:00 | 11614.4441 | -0.048233 | 5.2 | 5.2 | 77.84 | 9.74 | 20 | 0.61 | 13.39 | 1.53
2018-02-24 04:00 | 12096.5791 | -0.048233 | 3.29 | 3.29 | 80.53 | 14.3 | 20 | 0.61 | 12.59 | 1.45
2018-02-24 05:00 | 11923.4042 | -0.048233 | 0.23 | 0.23 | 155.627 | 16.44 | 20.87 | 0.61 | 10 | 2.5
2018-02-24 06:00 | 14845.9091 | -0.048233 | 4.76 | 4.76 | 1048.3792 | 22.18 | 16.73 | 0.61 | 13 | 16.53
2018-02-24 07:00 | 13941.7423 | 71.5182 | 15.64 | 15.64 | 2030.1392 | 21.64 | 454.7278 | 450.9016 | 7.66 | 458.1706
2018-02-24 08:00 | 14249.2144 | 82.1731 | 102.24 | 15.01 | 860.0692 | 22.19 | 118.9041 | 53.5873 | 3.5 | 101.8862
2018-02-24 09:00 | 16547.8079 | 165.126 | 16.04 | 16.04 | 812.7792 | 22.54 | 27.54 | 18.66 | 2.11 | 21.07
2018-02-24 10:00 | 14887.9715 | 385.549 | 12.81 | 18.7 | 994.8892 | 24.05 | 27.5 | 20 | 2.21 | 22.87
2018-02-24 11:00 | 14559.6629 | 530.961 | 14.02 | 18.95 | 609.8692 | 24.39 | 21.55 | 8.45 | 2.11 | 2.74
2018-02-24 12:00 | 14862.617 | 668.86 | 15.77 | 19.39 | 548.6392 | 25.36 | 17.73 | 8.45 | 1.75 | 1.51
2018-02-24 13:00 | 16922.5682 | 825.349 | 14.29 | 20.03 | 474.4592 | 30.63 | 5.01 | 1.41 | 2.11 | 1.51
2018-02-24 14:00 | 14527.9415 | 1058.57 | 13.78 | 20.22 | 145.307 | 35.86 | 5.3 | 1.25 | 3.44 | 3
2018-02-24 15:00 | 15371.3078 | 874.96 | 13.42 | 20.61 | 145.207 | 34.02 | 4.39 | 1 | 3.46 | 2.61
2018-02-24 16:00 | 13217.4478 | 560.103 | 13.36 | 20.67 | 522.0992 | 33.41 | 4.39 | 1.25 | 3.21 | 2.62
2018-02-24 17:00 | 12678.0692 | 197.336 | 14.71 | 20.11 | 924.1692 | 29.95 | 5.01 | 1.25 | 2 | 2.2
2018-02-24 18:00 | 13556.6991 | -0.048233 | 40.56 | 19.46 | 2586.0792 | 34.33 | 5.56 | 1.25 | 2 | 3.21
2018-02-24 19:00 | 12036.4542 | -0.048233 | 159.81 | 19.03 | 873.3292 | 25.06 | 38.11 | 21.48 | 3.5 | 25.98
2018-02-24 20:00 | 12977.5041 | -0.048233 | 169.64 | 16.8 | 626.0592 | 23.62 | 26.82 | 15.82 | 3.46 | 18.82
2018-02-24 21:00 | 11265.0542 | -0.048233 | 149.79 | 8.12 | 124.807 | 23.11 | 6.69 | 1.15 | 3.46 | 3.5
2018-02-24 22:00 | 10451.8542 | -0.048233 | 150.79 | 11.66 | 83.49 | 19.95 | 6.08 | 0.99 | 3.98 | 3.91
2018-02-24 23:00 | 11001.4891 | -0.048233 | 12.34 | 12.34 | 66.16 | 18.75 | 4.48 | 0.25 | 3.01 | 4.48
2018-02-25 | 10572.1041 | -0.048233 | 11.42 | 13.09 | 74.54 | 15.68 | 3 | 0.25 | 2.99 | 2.5
2018-02-25 01:00 | 10342.1141 | -0.048233 | 9.83 | 9.83 | 73.04 | 15.21 | 2.25 | 0.25 | 2.61 | 1.5
2018-02-25 02:00 | 10194.4141 | -0.048233 | 0 | 0 | 70.33 | 15.14 | 2.25 | 0.25 | 2.11 | 1.5
2018-02-25 03:00 | 9151.3042 | -0.048233 | 7.44 | 7.44 | 71.63 | 15.32 | 2.21 | 0.76 | 1.1 | 1.5
2018-02-25 04:00 | 9474.3042 | -0.048233 | 11.41 | 14.17 | 73.33 | 15.75 | 2.21 | 0.76 | 2.07 | 1.5
2018-02-25 05:00 | 10952.9591 | -0.048233 | 11.32 | 15.74 | 82.08 | 17.09 | 2.21 | 0.76 | 2.05 | 2.11
2018-02-25 06:00 | 11684.0741 | -0.048233 | 16.55 | 16.55 | 482.7392 | 19.84 | 6 | 0.76 | 3.82 | 5.8
2018-02-25 07:00 | 11391.7791 | 19.8949 | 149.7 | 19.13 | 154.187 | 21.69 | 83.0941 | 68.3173 | 4.11 | 93.3162
2018-02-25 08:00 | 10509.1622 | 384.276 | 15.3 | 22.56 | 569.5992 | 24.67 | 29.09 | 23.09 | 3.5 | 29.09
2018-02-25 09:00 | 11556.4225 | 334.955 | 15.44 | 20.82 | 564.1492 | 28.49 | 8.37 | 7.57 | 0.51 | 6.85
2018-02-25 10:00 | 11652.0762 | 616.622 | 13.94 | 20.74 | 470.7892 | 25.02 | 5.64 | 9.7 | 2.14 | 4.74
2018-02-25 11:00 | 11874.8795 | 1028.81 | 14.25 | 20.68 | 147.307 | 22.07 | 5 | 2 | 1.46 | 3.25
2018-02-25 12:00 | 10331.7212 | 714.496 | 14.18 | 20.71 | 120.607 | 20.19 | 4.2 | 0.99 | 0.66 | 3
2018-02-25 13:00 | 11447.2553 | 529.479 | 14.73 | 20.35 | 75.13 | 19.64 | 3.6 | 1 | 1.32 | 2.81
2018-02-25 14:00 | 11221.5993 | 647.587 | 14.55 | 19.24 | 73.08 | 18.88 | 4 | 1 | 3.01 | 3
2018-02-25 15:00 | 9680.3195 | 446.81 | 14.47 | 19.24 | 73.04 | 19.1 | 3.89 | 0.99 | 2.99 | 2.5
2018-02-25 16:00 | 9529.982 | 291.56 | 14.31 | 18.29 | 72.87 | 18.36 | 4 | 0.99 | 1.78 | 2.5
2018-02-25 17:00 | 10607.8604 | 182.844 | 14.78 | 18.19 | 155.857 | 18.16 | 3.5 | 1 | 2 | 2
2018-02-25 18:00 | 9400.2042 | -0.048233 | 15.68 | 18.83 | 625.3192 | 21.18 | 5.75 | 0.99 | 0.51 | 3.25
2018-02-25 19:00 | 9472.4042 | -0.048233 | 16.84 | 20.37 | 477.8292 | 18.68 | 17 | 1.61 | 2.7 | 16.4
2018-02-25 20:00 | 9371.7042 | -0.048233 | 15.15 | 17.09 | 125.757 | 19.77 | 7 | 1.08 | 0.51 | 3.39
2018-02-25 21:00 | 9390.7042 | -0.048233 | 15.3 | 16.61 | 81.27 | 17.37 | 7.13 | 1.14 | 2.11 | 3.32
2018-02-25 22:00 | 9350.8042 | -0.048233 | 14.08 | 15.99 | 75.04 | 13.96 | 5.83 | 0.99 | 10.11 | 4.55
2018-02-25 23:00 | 9223.5042 | -0.048233 | 13.4 | 14 | 74.21 | 10.53 | 3.01 | 0.25 | 25.93 | 22
2018-02-26 | 10168.0391 | -0.048233 | 10.44 | 10.44 | 70.65 | 8.09 | 3 | 0.25 | 9.92 | 2.5
2018-02-26 01:00 | 10168.0391 | -0.048233 | 9.01 | 9.01 | 64.89 | 7.4 | 1.56 | 0.25 | 15 | 1.56
2018-02-26 02:00 | 10082.5841 | -0.048233 | 8.57 | 8.57 | 63.74 | 7.7 | 1.25 | 0.25 | 11.41 | 1.25
2018-02-26 03:00 | 9123.7542 | -0.048233 | 8.62 | 8.62 | 63.99 | 7.8 | 1.59 | 0.76 | 1.28 | 1.59
2018-02-26 04:00 | 10361.1041 | -0.048233 | 10.56 | 10.56 | 67.34 | 8.47 | 1.61 | 0.76 | 15 | 1.61
2018-02-26 05:00 | 10714.5291 | -0.048233 | 13.07 | 16.28 | 74.08 | 11.56 | 1.61 | 0.76 | 10.72 | 1.61
2018-02-26 06:00 | 11048.9641 | -0.048233 | 54.8 | 14.08 | 129.167 | 16.91 | 4 | 0.76 | 27.13 | 20.56
2018-02-26 07:00 | 10717.8004 | 19.0525 | 15.49 | 15.49 | 1342.3892 | 16.95 | 31.01 | 28.01 | 14.54 | 38
2018-02-26 08:00 | 9818.338 | 54.0926 | 16.79 | 16.79 | 155.817 | 18.61 | 15 | 13.17 | 2.35 | 13.17
2018-02-26 09:00 | 10177.8981 | 397.577 | 16.51 | 18.24 | 472.0792 | 18.72 | 6 | 8.67 | 0.5 | 5
2018-02-26 10:00 | 11781.0647 | 507.886 | 13.41 | 18.84 | 611.6492 | 19.26 | 4.2 | 9.2 | 2.11 | 3
2018-02-26 11:00 | 10638.5598 | 489.484 | 13.92 | 21.17 | 637.2592 | 18.76 | 3.89 | 1.2 | 0.61 | 3.11
2018-02-26 12:00 | 12283.2194 | 661.862 | 13.16 | 23.46 | 542.1392 | 18.86 | 3.89 | 0.99 | 1.03 | 3
2018-02-26 13:00 | 10884.6535 | 601.53 | 13.89 | 21.33 | 149.537 | 18.66 | 3.89 | 1 | 3.5 | 3
2018-02-26 14:00 | 11207.6487 | 908.525 | 15.75 | 20.84 | 88.17 | 18.55 | 3.5 | 1 | 3.46 | 2.5
2018-02-26 15:00 | 11033.1394 | 728.831 | 15.7 | 20.68 | 88.63 | 19.47 | 3.5 | 0.99 | 3.01 | 2.42
2018-02-26 16:00 | 10835.6364 | 500.933 | 15.6 | 20.65 | 140.497 | 19.43 | 3.89 | 1 | 2.11 | 2.25
2018-02-26 17:00 | 11850.5217 | 193.722 | 15.51 | 20.71 | 1298.7692 | 19.65 | 3 | 1 | 2 | 1.5
2018-02-26 18:00 | 11664.0291 | -0.048233 | 290.4957 | 246.17 | 676.4992 | 31.45 | 6 | 0.99 | 0.51 | 3.25
2018-02-26 19:00 | 11881.3591 | -0.048233 | 29.45 | 29.45 | 1122.8892 | 21.52 | 30.18 | 1.61 | 12.01 | 29.51
2018-02-26 20:00 | 10622.8542 | -0.048233 | 16.95 | 24.53 | 541.3292 | 20.65 | 15.4 | 1.58 | 0.51 | 3.89
2018-02-26 21:00 | 10487.9542 | -0.048233 | 16.64 | 24.39 | 126.607 | 18.61 | 13.8 | 0.99 | 2.11 | 3
2018-02-26 22:00 | 10337.8542 | -0.048233 | 14.27 | 20.65 | 89.22 | 17.06 | 6 | 0.99 | 2.25 | 2.74
2018-02-26 23:00 | 10238.1042 | -0.048233 | 15.22 | 20.46 | 72.38 | 16.1 | 3.38 | 0.25 | 15 | 3.15
2018-02-27 | 10034.8042 | -0.048233 | 14.09 | 18.68 | 75 | 16.31 | 2.62 | 0.25 | 8.11 | 2.11
2018-02-27 01:00 | 11090.1091 | -0.048233 | 12.66 | 18.18 | 65.57 | 13.29 | 2.11 | 0.25 | 10 | 1.74
2018-02-27 02:00 | 9962.6042 | -0.048233 | 12.82 | 17.74 | 61.94 | 12.92 | 2 | 0.25 | 2.61 | 1.67
2018-02-27 03:00 | 11035.2491 | -0.048233 | 13.85 | 18.32 | 64.01 | 12.63 | 2.11 | 0.97 | 2.11 | 1.97
2018-02-27 04:00 | 10334.0542 | -0.048233 | 14.26 | 19.16 | 65.38 | 15.03 | 2.15 | 0.97 | 2.99 | 1.75
2018-02-27 05:00 | 11489.2542 | -0.048233 | 13.36 | 20.16 | 90.62 | 16.74 | 4.01 | 0.97 | 1.61 | 3.34
2018-02-27 06:00 | 12959.8542 | -0.048233 | 13.55 | 17.62 | 468.3292 | 21.16 | 21 | 0.97 | 25.28 | 21
2018-02-27 07:00 | 13824.6722 | 59.2865 | 14.69 | 19.33 | 155.457 | 20.24 | 96.0241 | 25.3 | 11 | 95.3262
2018-02-27 08:00 | 14387.1601 | 183.379 | 15.76 | 19.91 | 152.717 | 21.87 | 37.53 | 12.43 | 2.4 | 35.45
2018-02-27 09:00 | 15684.4097 | 387.905 | 17.41 | 17.41 | 466.5892 | 22.23 | 21.45 | 9.09 | 1.21 | 15.88
2018-02-27 10:00 | 16102.0801 | 473.558 | 16.05 | 16.05 | 151.287 | 21.62 | 20.11 | 11.98 | 2.21 | 16.85
2018-02-27 11:00 | 15571.3778 | 405.924 | 15.8 | 25.59 | 137.837 | 22.91 | 5.5 | 2.22 | 2.11 | 2.22
2018-02-27 12:00 | 17742.8175 | 1158.65 | 15.67 | 20.98 | 133.907 | 23.94 | 4.24 | 2.22 | 2.11 | 2.22
2018-02-27 13:00 | 17871.0164 | 857.352 | 14.01 | 20.83 | 88.35 | 27.45 | 4.91 | 2.22 | 2.51 | 2.11
2018-02-27 14:00 | 14989.7555 | 1068.69 | 11.51 | 18.64 | 79.55 | 30.48 | 4.02 | 1.68 | 2.67 | 3
2018-02-27 15:00 | 15823.6085 | 816.681 | 9.62 | 16.95 | 77.04 | 35.19 | 3.61 | 1.19 | 2.65 | 2.51
2018-02-27 16:00 | 15276.5783 | 523.169 | 9.5 | 17.98 | 72.76 | 36.15 | 3.22 | 1.09 | 2 | 2.25
2018-02-27 17:00 | 14699.6157 | 189.285 | 5.46 | 18.6 | 134.057 | 28.64 | 3.36 | 1.82 | 2 | 2.25
2018-02-27 18:00 | 12761.3042 | -0.048233 | 9.65 | 18.63 | 465.7492 | 33.84 | 8.46 | 2 | 2.11 | 3.43
2018-02-27 19:00 | 14087.3641 | -0.048233 | 56.14 | 44.32 | 131.677 | 24.1 | 40 | 20 | 2.25 | 31.58
2018-02-27 20:00 | 13890.0791 | -0.048233 | 9.68 | 16.99 | 144.697 | 22.23 | 35 | 8.55 | 1.82 | 2.25
2018-02-27 21:00 | 13628.4391 | -0.048233 | 115.18 | 115.18 | 485.7592 | 19.57 | 22.01 | 1.62 | 10.36 | 2.51
2018-02-27 22:00 | 13094.6091 | -0.048233 | 4.74 | 19.71 | 125.537 | 16.92 | 23 | 1.3 | 10.2 | 5
2018-02-27 23:00 | 12489.0391 | -0.048233 | 0.99 | 17.25 | 76.22 | 13.6 | 47.01 | 0.3 | 57.6962 | 26.69
2018-02-28 | 11114.0042 | -0.048233 | 1.46 | 15.41 | 84.44 | 11.96 | 35 | 0.3 | 18.91 | 4
2018-02-28 01:00 | 10912.6042 | -0.048233 | -0.13 | 15.06 | 74.57 | 8.17 | 26 | 0.3 | 11.6 | 2.03
2018-02-28 02:00 | 12036.4441 | -0.048233 | -0.45 | 11.63 | 65.78 | 5.78 | 45.59 | 0.3 | 10.72 | 1.25
2018-02-28 03:00 | 12054.3791 | -0.048233 | -0.48 | 6.69 | 69.97 | 5.22 | 47.01 | 0.82 | 10.11 | 1.21
2018-02-28 04:00 | 12556.5591 | -0.048233 | -0.31 | 11.63 | 72.21 | 8.93 | 26 | 0.82 | 13.72 | 1.2
2018-02-28 05:00 | 13610.5041 | -0.048233 | -0.5 | 13.76 | 118.637 | 13.04 | 26 | 0.82 | 11.91 | 1.98
2018-02-28 06:00 | 13993.4542 | -0.048233 | -0.21 | 17.39 | 88.28 | 17.75 | 26.51 | 0.82 | 35.12 | 26.51
2018-02-28 07:00 | 16611.0326 | 35.0546 | 1.05 | 17.08 | 131.027 | 18.14 | 30.14 | 27.14 | 18.75 | 45
2018-02-28 08:00 | 15370.3165 | 53.2805 | 360.8757 | 17.06 | 133.177 | 18.01 | 7.22 | 11.7 | 14.2 | 11.7
2018-02-28 09:00 | 16586.1505 | 95.1058 | 1109.8911 | 19.4 | 125.177 | 20.44 | 20.88 | 11.7 | 1.36 | 20.88
2018-02-28 10:00 | 16712.551 | 131.159 | 1140.1011 | 101.7 | 118.367 | 21.12 | 29.85 | 9.79 | 2.25 | 29.84
2018-02-28 11:00 | 15880.9343 | 150.773 | 273.3057 | 228.98 | 75.46 | 24.81 | 6 | 8 | 1.91 | 3.08
2018-02-28 12:00 | 17487.4889 | 161.883 | 186.54 | 186.54 | 70 | 28.31 | 6.62 | 2.25 | 1.17 | 4
2018-02-28 13:00 | 15510.6006 | 157.948 | 298.6957 | 254.37 | 66.77 | 32.72 | 5.06 | 1 | 1.93 | 3.75
2018-02-28 14:00 | 14586.0074 | 198.692 | 304.8457 | 260.52 | 64.48 | 38.91 | 3.33 | 1 | 1.77 | 3.33
2018-02-28 15:00 | 15590.9366 | 121.139 | 104.09 | 104.09 | 64.98 | 40.87 | 3.17 | 1 | 2.21 | 3
2018-02-28 16:00 | 15075.5428 | 269.614 | 130.95 | 130.95 | 65 | 40.77 | 3 | 1.21 | 2.41 | 2.83
2018-02-28 17:00 | 14397.0723 | 72.514 | 103.76 | 22.2 | 126.667 | 33.94 | 2.79 | 1.5 | 1.72 | 2.79
2018-02-28 18:00 | 12596.0042 | -0.048233 | 50.78 | 25.24 | 146.617 | 33.4 | 6 | 2 | 2.11 | 14.49
2018-02-28 19:00 | 14193.9191 | -0.048233 | 63.07 | 63.07 | 81.83 | 27.37 | 23 | 2.85 | 2.84 | 20
2018-02-28 20:00 | 12469.6542 | -0.048233 | 72.22 | 19.29 | 81.08 | 23.1 | 7.23 | 2 | 2.11 | 2.51
2018-02-28 21:00 | 13469.1341 | -0.048233 | 176.19 | 17.21 | 82.7 | 21.91 | 5.58 | 1.9 | 3.01 | 2.72
2018-02-28 22:00 | 11753.3542 | -0.048233 | 85.51 | 85.51 | 74.92 | 16.96 | 4.23 | 1.4 | 8.05 | 3.01
2018-02-28 23:00 | 12665.2241 | -0.048233 | 34.21 | 15.94 | 64.29 | 14.36 | 3 | 0.3 | 11 | 3
2018-03-01 | 12551.2841 | -0.048233 | 4.05 | 13.91 | 68.83 | 12.07 | 25.13 | 0.3 | 54.6362 | 2.25
2018-03-01 01:00 | 11036.1042 | -0.048233 | 249.6457 | 12.96 | 68.68 | 11.59 | 20 | 0.25 | 52.6962 | 6
2018-03-01 02:00 | 12404.6391 | -0.048233 | 382.6257 | 0 | 69.06 | 10.43 | 3.79 | 0.25 | 12 | 3.79
2018-03-01 03:00 | 10984.8042 | -0.048233 | 82.3 | 0 | 68.47 | 11.78 | 3 | 0.99 | 12 | 3
2018-03-01 04:00 | 12406.7491 | -0.048233 | 149.6 | 4.75 | 69.44 | 13.85 | 2.61 | 0.99 | 10.11 | 2.61
2018-03-01 05:00 | 13320.3791 | -0.048233 | 92.42 | 9.25 | 77.81 | 16.2 | 2.75 | 0.99 | 11.07 | 2.74
2018-03-01 06:00 | 15071.6791 | -0.048233 | 6.74 | 14.32 | 69.37 | 25.24 | 3.44 | 0.99 | 26.53 | 15.14
2018-03-01 07:00 | 14652.7031 | 18.898 | 11.9 | 15.86 | 68.56 | 24.67 | 25 | 24.79 | 14.11 | 24.88
2018-03-01 08:00 | 14601.0575 | 73.5342 | 11.18 | 16.13 | 82.1 | 25.17 | 6.72 | 11.01 | 2.11 | 5.72
2018-03-01 09:00 | 15531.0522 | 127.476 | 88.14 | 15.9 | 128.407 | 29.21 | 17.34 | 13.59 | 0.72 | 6.35
2018-03-01 10:00 | 17550.0337 | 697.103 | 90.62 | 71.41 | 61.66 | 30.64 | 17.84 | 15.09 | 1 | 4
2018-03-01 11:00 | 17781.1029 | 971.126 | 70.14 | 41.71 | 61.95 | 32.66 | 7.79 | 7.51 | 2 | 4.83
2018-03-01 12:00 | 18390.549 | 1021.8 | 82.12 | 19.32 | 56.87 | 34.39 | 5.62 | 1.91 | 2.25 | 3
2018-03-01 13:00 | 15603.789 | 861.041 | 69.59 | 20.68 | 53.83 | 41.55 | 5.28 | 1.41 | 2.25 | 1.95
2018-03-01 14:00 | 15806.2621 | 261.239 | 333.8557 | 127.51 | 52.67 | 48.68 | 4.34 | 7.62 | 1.9 | 4
2018-03-01 15:00 | 14342.7884 | 699.672 | 52.3 | 18.65 | 54.36 | 36.02 | 3.62 | 1.15 | 0.58 | 3.45
2018-03-01 16:00 | 14800.2535 | 94.6763 | 16.87 | 18.28 | 55.85 | 30.33 | 3.19 | 1.28 | 0.58 | 3
2018-03-01 17:00 | 12227.5172 | 38.0707 | 16.5 | 18.04 | 85.5 | 27.09 | 4 | 1.26 | 0.61 | 1.5
2018-03-01 18:00 | 13014.9671 | 7.4617 | 86.91 | 18.15 | 142.817 | 36.81 | 6.8 | 1.87 | 2 | 4.24
2018-03-01 19:00 | 11534.8542 | -0.048233 | 776.9011 | 20.57 | 68.47 | 26.89 | 33.54 | 1.25 | 3.42 | 30.05
2018-03-01 20:00 | 12396.1991 | -0.048233 | 61.42 | 19.09 | 57.55 | 25.43 | 16.86 | 1.9 | 2.11 | 16.17
2018-03-01 21:00 | 10701.7042 | -0.048233 | 49.62 | 18.54 | 56.77 | 22.4 | 5.28 | 1.25 | 2.11 | 4.27
2018-03-01 22:00 | 11285.2841 | -0.048233 | 12.73 | 17.94 | 52.12 | 18.72 | 4 | 1.38 | 10 | 3
2018-03-01 23:00 | 10998.3241 | -0.048233 | 10.89 | 15.25 | 12.61 | 17.77 | 3 | 0.25 | 12.03 | 3
2018-03-02 | 10583.7091 | -0.048233 | 10.75 | 13.93 | 6.01 | 15.94 | 3 | 0.25 | 22 | 3
2018-03-02 01:00 | 9321.3542 | -0.048233 | 9.9 | 13.57 | 4.2 | 15.04 | 4 | 0.25 | 13.73 | 2.01
2018-03-02 02:00 | 10303.0791 | -0.048233 | 8.56 | 13.86 | 3.94 | 14.65 | 4 | 0.25 | 10.35 | 1.5
2018-03-02 03:00 | 10257.7141 | -0.048233 | 2.93 | 14.09 | 3.93 | 15.37 | 4 | 0.97 | 11.37 | 1.51
2018-03-02 04:00 | 10527.7941 | -0.048233 | 1.26 | 14.73 | 3.95 | 16.55 | 3.51 | 0.97 | 0.5 | 1.5
2018-03-02 05:00 | 11429.8191 | -0.048233 | 7.07 | 17.11 | 57.27 | 18.42 | 4 | 0.97 | 10.71 | 2.71
2018-03-02 06:00 | 13224.3741 | -0.048233 | 63.73 | 17.77 | 483.6692 | 36 | 4.92 | 0.97 | 16.03 | 4.72
2018-03-02 07:00 | 14039.9286 | 63.9892 | 82.11 | 20.4 | 61.94 | 27.03 | 37.84 | 21.46 | 8 | 37.84
2018-03-02 08:00 | 14288.3165 | 365.428 | 10.11 | 18.28 | 60.02 | 25.37 | 26.31 | 12.25 | 2.11 | 26.31
2018-03-02 09:00 | 13479.0598 | 766.484 | 124.74 | 18.5 | 61.54 | 26.56 | 15.55 | 13.92 | 2.11 | 15.04
2018-03-02 10:00 | 14724.6055 | 972.972 | 91.51 | 16.86 | 67.25 | 27.45 | 18 | 17.79 | 2.11 | 3.77
2018-03-02 11:00 | 14474.2307 | 1158.65 | 71.73 | 17.32 | 62.92 | 27.34 | 6.39 | 8.01 | 2.11 | 3.43
2018-03-02 12:00 | 14760.1357 | 1158.65 | 12.46 | 18.19 | 59.83 | 25.29 | 6 | 6.64 | 2.11 | 3.08
2018-03-02 13:00 | 14805.5007 | 1158.65 | 14.01 | 18.71 | 56.52 | 26.27 | 5.2 | 7.79 | 2 | 2.02
2018-03-02 14:00 | 12877.174 | 1093.92 | 13.71 | 19.6 | 54.45 | 25.01 | 5.6 | 7.79 | 2.11 | 2.06
2018-03-02 15:00 | 11936.0508 | 865.264 | 12.55 | 19.89 | 55.47 | 24.87 | 5 | 0.99 | 1.88 | 1.5
2018-03-02 16:00 | 11188.9983 | 534.893 | 12.26 | 19.73 | 60.63 | 24.17 | 5.48 | 0.99 | 2.16 | 1.5
2018-03-02 17:00 | 10720.484 | 184.72 | 12.09 | 19.42 | 129.027 | 24.36 | 5.33 | 0.99 | 2.11 | 1.5
2018-03-02 18:00 | 10444.0117 | 4.6966 | 14.86 | 20.02 | 146.127 | 32.19 | 6.75 | 1.15 | 2.35 | 2.11
2018-03-02 19:00 | 11491.0091 | -0.048233 | 135.87 | 21.01 | 124.897 | 26.49 | 19.55 | 1.43 | 3.02 | 15.55
2018-03-02 20:00 | 10088.0042 | -0.048233 | 116.99 | 20.79 | 68.65 | 25.19 | 6.97 | 0.99 | 2.25 | 16.21
2018-03-02 21:00 | 10044.3042 | -0.048233 | 176.32 | 18.56 | 61.53 | 22.36 | 6.41 | 1.3 | 15.78 | 2.62
2018-03-02 22:00 | 10884.3841 | -0.048233 | 134.1 | 20.45 | 58.02 | 21.11 | 5 | 0.99 | 18.01 | 2
2018-03-02 23:00 | 10499.3091 | -0.048233 | 8.16 | 16.42 | 55.9 | 18.15 | 3.92 | 0.25 | 112.3134 | 3.92
2018-03-03 | 10156.4341 | -0.048233 | 7.26 | 14.65 | 56.46 | 16.49 | 3.19 | 0.25 | 28.79 | 3.18
2018-03-03 01:00 | 9131.3542 | -0.048233 | 8.91 | 14.11 | 56.02 | 15.83 | 3 | 0.25 | 22.95 | 2.98
2018-03-03 02:00 | 9050.6042 | -0.048233 | 7.68 | 14 | 55.88 | 15.49 | 2.6 | 0.25 | 13.69 | 2
2018-03-03 03:00 | 10070.9791 | -0.048233 | 7.88 | 14.35 | 55.66 | 15.6 | 2.71 | 0.97 | 13.43 | 2
2018-03-03 04:00 | 9416.3542 | -0.048233 | 7.04 | 14.63 | 59.84 | 16.11 | 2.5 | 0.97 | 8 | 1.51
2018-03-03 05:00 | 10355.9042 | -0.048233 | 4.83 | 15.51 | 62.91 | 18.79 | 3 | 0.97 | 9.09 | 3
2018-03-03 06:00 | 13385.7891 | -0.048233 | 58.77 | 17.74 | 72.6 | 35.17 | 4 | 0.97 | 52.6962 | 4
2018-03-03 07:00 | 12852.1652 | 117.595 | 61.93 | 18.82 | 81.25 | 33 | 32.95 | 23.55 | 11.25 | 36.63
2018-03-03 08:00 | 13173.3517 | 492.686 | 10.34 | 19.21 | 74.96 | 25.92 | 17.37 | 12.6 | 1 | 17.37
2018-03-03 09:00 | 15960.1065 | 840.063 | 10.69 | 26.31 | 73.67 | 26.08 | 15.48 | 15.27 | 0.51 | 5.03
2018-03-03 10:00 | 16701.1986 | 1076.52 | 10.85 | 30.92 | 63.32 | 23.99 | 20.21 | 20 | 0.9 | 4.81
2018-03-03 11:00 | 13618.8675 | 1158.65 | 14.54 | 25.39 | 60 | 25.31 | 5.63 | 7.5 | 1 | 3.12
2018-03-03 12:00 | 13464.046 | 1081.68 | 70.16 | 27.42 | 52.78 | 25 | 5.31 | 2.4 | 1 | 3
2018-03-03 13:00 | 14870.9107 | 1158.65 | 141.12 | 35.04 | 51.8 | 24.78 | 4.11 | 1.04 | 1.91 | 3
2018-03-03 14:00 | 13903.6867 | 1084.85 | 28.21 | 27.69 | 51.81 | 25.24 | 4.71 | 9.67 | 1 | 3.1
2018-03-03 15:00 | 13248.2902 | 871.621 | 21.85 | 26.66 | 51.91 | 24.61 | 4.87 | 0.99 | 2.98 | 3
2018-03-03 16:00 | 12530.3299 | 592.09 | 22.61 | 28.83 | 52.04 | 23.22 | 4.72 | 0.99 | 2.61 | 2.89
2018-03-03 17:00 | 12025.4861 | 234.565 | 51.62 | 51.62 | 90.06 | 19.4 | 5.04 | 0.99 | 2.11 | 3
2018-03-03 18:00 | 11650.9589 | 8.5629 | 70.25 | 70.25 | 126.027 | 22.66 | 4.68 | 1.25 | 2.39 | 4.11
2018-03-03 19:00 | 11515.2741 | -0.048233 | 74.23 | 74.23 | 88.11 | 19.66 | 36.3 | 8.65 | 17.88 | 35.18
2018-03-03 20:00 | 11120.7041 | -0.048233 | 38.05 | 30.21 | 79.03 | 18.73 | 17.25 | 8.55 | 19.84 | 16.53
2018-03-03 21:00 | 10968.7841 | -0.048233 | 17.83 | 26.05 | 54.02 | 17.62 | 6.74 | 1.21 | 49.9762 | 4.74
2018-03-03 22:00 | 10693.4291 | -0.048233 | 17.39 | 26.31 | 48.24 | 14.68 | 4.92 | 0.99 | 50.3562 | 3
2018-03-03 23:00 | 10395.9191 | -0.048233 | 19.13 | 19.48 | 46.18 | 14.25 | 3.65 | 0.47 | 109.7434 | 3.64
2018-03-04 | 10238.7241 | -0.048233 | 14.31 | 14.31 | 23.99 | 12.94 | 2.36 | 0.47 | 110.1434 | 2.36
2018-03-04 01:00 | 10272.4841 | -0.048233 | 11.83 | 13.77 | 21.36 | 12.06 | 2.67 | 0.45 | 56.6962 | 2.54
2018-03-04 02:00 | 10157.4891 | -0.048233 | 10.08 | 18.79 | 19.8 | 12.72 | 2.01 | 0.45 | 15.15 | 1.4
2018-03-04 03:00 | 9062.0042 | -0.048233 | 9.32 | 22.82 | 19.32 | 12.95 | 2.3 | 0.64 | 14 | 0.5
2018-03-04 04:00 | 10286.1991 | -0.048233 | 8.3 | 24.46 | 19.96 | 14.28 | 2.01 | 0.64 | 14 | 1.3
2018-03-04 05:00 | 10785.2141 | -0.048233 | 9.64 | 26.71 | 24.18 | 15.55 | 2.61 | 0.64 | 14 | 1.43
2018-03-04 06:00 | 11348.5841 | -0.048233 | 9.05 | 34.86 | 38.13 | 17.35 | 3.8 | 0.94 | 100.7434 | 25
2018-03-04 07:00 | 11401.52 | 27.128 | 50.97 | 50.97 | 39.55 | 17.62 | 21.06 | 18.86 | 40 | 30.57
2018-03-04 08:00 | 11822.1036 | 63.7854 | 54.22 | 54.22 | 35 | 20.11 | 5 | 10 | 17.91 | 4.92
2018-03-04 09:00 | 11943.6297 | 140.976 | 12.09 | 32.25 | 35.29 | 23.03 | 6.64 | 9.8 | 0.25 | 3.76
2018-03-04 10:00 | 12062.4396 | 194.592 | 11.89 | 29.64 | 35 | 23.51 | 6.23 | 9.79 | 0.25 | 2.63
2018-03-04 11:00 | 10784.3744 | 189.973 | 11.34 | 32.2 | 35.15 | 23.23 | 6.93 | 7.5 | 0.25 | 3.5
2018-03-04 12:00 | 10893.3888 | 243.725 | 11.77 | 28.87 | 33.53 | 22.48 | 4.16 | 2 | 1 | 3.1
2018-03-04 13:00 | 11066.189 | 528.62 | 14.89 | 28.12 | 31.92 | 21.32 | 4.89 | 2 | 2.56 | 3.1
2018-03-04 14:00 | 10723.0794 | 483.452 | 15.24 | 25.72 | 31.45 | 21.26 | 5.55 | 2 | 2.22 | 3.1
2018-03-04 15:00 | 10784.5681 | 673.177 | 16.88 | 24.85 | 30.47 | 20.06 | 5.01 | 0.95 | 1.57 | 3.01
2018-03-04 16:00 | 11459.3203 | 273.915 | 71.48 | 33.67 | 32.37 | 19.39 | 5 | 0.99 | 1.57 | 3
2018-03-04 17:00 | 10007.9386 | 41.6722 | 16.63 | 28.45 | 35 | 20.45 | 5 | 0.99 | 1.48 | 3
2018-03-04 18:00 | 11192.9534 | 2.4345 | 119.23 | 119.23 | 41.59 | 25.9 | 5.99 | 0.99 | 2.25 | 3.76
2018-03-04 19:00 | 11047.9091 | -0.048233 | 71.95 | 71.95 | 36.25 | 22.84 | 49.18 | 23 | 10 | 48.18
2018-03-04 20:00 | 9752.6542 | -0.048233 | 12.28 | 22.3 | 35.24 | 22.71 | 52.37 | 23 | 2.22 | 77.4862
2018-03-04 21:00 | 9619.6542 | -0.048233 | 14.37 | 26.43 | 34.58 | 19.72 | 24.21 | 19.38 | 16.59 | 23.99
2018-03-04 22:00 | 10448.6691 | -0.048233 | 11.33 | 15.93 | 31.78 | 16.38 | 6.3 | 13.34 | 52.6962 | 4.11
2018-03-04 23:00 | 9347.0042 | -0.048233 | 11.11 | 18.69 | 34.36 | 14.82 | 16.5 | 0.47 | 99.7034 | 15.5
2018-03-05 | 9306.1542 | -0.048233 | 9 | 14.4 | 22.51 | 14.44 | 16.5 | 0.47 | 36.16 | 16.49
2018-03-05 01:00 | 9303.3042 | -0.048233 | 9.26 | 11.69 | 22.12 | 12.88 | 16.5 | 0.45 | 52.6962 | 2.61
2018-03-05 02:00 | 9246.3042 | -0.048233 | 9.54 | 10.21 | 21.55 | 13.2 | 16.5 | 0.45 | 20 | 2.01
2018-03-05 03:00 | 9217.8042 | -0.048233 | 12.17 | 12.17 | 21.19 | 13.63 | 16.5 | 0.71 | 20 | 2.11
2018-03-05 04:00 | 9074.3542 | -0.048233 | 12.22 | 12.22 | 20.7 | 14.51 | 4 | 0.71 | 16.49 | 1.94
2018-03-05 05:00 | 10328.3991 | -0.048233 | 12.98 | 17.06 | 30.68 | 15.18 | 6.89 | 0.71 | 20 | 3.94
2018-03-05 06:00 | 10264.0441 | -0.048233 | 12.89 | 29.45 | 44.69 | 21.94 | 22.98 | 16.58 | 98.7434 | 25
2018-03-05 07:00 | 10119.3042 | 24.7575 | 13.11 | 21.62 | 57.53 | 23.31 | 123.4241 | 419.8316 | 30.31 | 457.7406
2018-03-05 08:00 | 10520.506 | 82.0436 | 19.71 | 20.45 | 49.11 | 22.46 | 96.4941 | 78.5673 | 16.93 | 78.3762
2018-03-05 09:00 | 9487.953 | 135.319 | 16.08 | 19.57 | 57.49 | 24.99 | 37.28 | 24.14 | 2.19 | 22.1
2018-03-05 10:00 | 10973.0582 | 468.003 | 16.37 | 19.99 | 65.56 | 26.73 | 27.24 | 23.83 | 2.11 | 25.43
2018-03-05 11:00 | 10052.481 | 493.559 | 33 | 26.48 | 62.79 | 29.22 | 20.3 | 17.5 | 2.11 | 18.8
2018-03-05 12:00 | 9960.731 | 309.98 | 30.95 | 30.95 | 62.28 | 27.31 | 18.04 | 15.84 | 2.25 | 16.54
2018-03-05 13:00 | 10395.6001 | 809.737 | 15.78 | 28.08 | 57.66 | 29.03 | 7.92 | 10.21 | 8.11 | 4.11
2018-03-05 14:00 | 11506.8924 | 559.007 | 45.59 | 45.59 | 57.34 | 28.07 | 6.89 | 7.58 | 10 | 4.11
2018-03-05 15:00 | 10444.7265 | 515.449 | 12.93 | 38.67 | 58.55 | 27.32 | 5.86 | 0.95 | 11 | 3.86
2018-03-05 16:00 | 10215.2578 | 151.903 | 38.02 | 38.02 | 59.68 | 26.64 | 5.16 | 0.99 | 10.03 | 3.1
2018-03-05 17:00 | 11259.1907 | 66.2187 | 40.9 | 40.9 | 57.78 | 24.76 | 6 | 0.99 | 11 | 3
2018-03-05 18:00 | 11270.7475 | 3.1729 | 105.32 | 105.32 | 127.007 | 30.85 | 36.21 | 58.1573 | 11 | 34.21
2018-03-05 19:00 | 11362.2991 | -0.048233 | 86.8 | 86.8 | 74.02 | 26.02 | 506.0178 | 504.6916 | 10 | 507.2706
2018-03-05 20:00 | 11261.0191 | -0.048233 | 43.46 | 43.46 | 58.04 | 26.14 | 649.3278 | 594.0316 | 10 | 648.3106
2018-03-05 21:00 | 11113.3191 | -0.048233 | 44.14 | 44.14 | 63.3 | 23.4 | 478.3578 | 449.6116 | 11 | 475.4106
2018-03-05 22:00 | 9865.7042 | -0.048233 | 6.48 | 25.88 | 60.81 | 18.42 | 46.05 | 65.9473 | 15 | 39.44
2018-03-05 23:00 | 9638.6542 | -0.048233 | 9.26 | 23.75 | 59.02 | 16.39 | 28.35 | 25.55 | 94.7434 | 25.92
2018-03-06 | 10611.1391 | -0.048233 | 0 | 21.56 | 56.49 | 10.82 | 19.92 | 0.47 | 27.69 | 19
2018-03-06 01:00 | 10503.5291 | -0.048233 | 0.51 | 41.4 | 47.86 | 10.49 | 17.25 | 0.45 | 27.67 | 1.16
2018-03-06 02:00 | 9328.9542 | -0.048233 | 0 | 27.22 | 46.25 | 7.19 | 22.25 | 0.45 | 52.6962 | 1.28
2018-03-06 03:00 | 9410.6542 | -0.048233 | 6.65 | 25.42 | 44.58 | 8.55 | 22.25 | 0.99 | 20.66 | 1.38
2018-03-06 04:00 | 11020.4791 | -0.048233 | 0.33 | 31.52 | 46.95 | 11.12 | 22.25 | 0.99 | 15.25 | 1.39
2018-03-06 05:00 | 12587.1541 | -0.048233 | -0.15 | 45.47 | 61.65 | 14.25 | 22.25 | 0.99 | 23.15 | 12
2018-03-06 06:00 | 12725.2042 | -0.048233 | 45.63 | 45.63 | 74.48 | 21.22 | 26.01 | 21.76 | 62.6962 | 45
2018-03-06 07:00 | 14550.9187 | 66.7565 | 4.5 | 23.48 | 136.127 | 20.07 | 517.0678 | 435.3316 | 52.6962 | 535.9806
2018-03-06 08:00 | 15548.8998 | 188.263 | 8.55 | 23.2 | 133.817 | 21.22 | 104.7541 | 88.8673 | 15.8 | 102.3062
2018-03-06 09:00 | 18900.842 | 390.49 | 40.46 | 40.46 | 72.78 | 24.52 | 27.29 | 21.93 | 11.87 | 24.04
2018-03-06 10:00 | 17536.3039 | 520.089 | 9.63 | 25.07 | 65.06 | 25.61 | 17.48 | 13.63 | 10.11 | 16.52
2018-03-06 11:00 | 17035.6347 | 366.521 | 46.85 | 46.85 | 58.96 | 29.83 | 7.92 | 10.37 | 11 | 11.87
2018-03-06 12:00 | 18154.4484 | 731.008 | 7.21 | 39.53 | 52.53 | 30.8 | 8 | 8.62 | 11 | 6.01
2018-03-06 13:00 | 16880.3809 | 509.361 | 8.26 | 34.67 | 50 | 33.06 | 7.96 | 7.95 | 11 | 5.96
2018-03-06 14:00 | 14478.6944 | 540.731 | 77.52 | 77.52 | 47.27 | 37.59 | 8 | 8.81 | 11.01 | 6.36
2018-03-06 15:00 | 13798.4631 | 263.698 | 80.26 | 80.26 | 46.44 | 39.05 | 6.62 | 0.99 | 11 | 4.42
2018-03-06 16:00 | 14445.6339 | 128.544 | 8.57 | 27.53 | 49.15 | 41.7 | 5.45 | 0.99 | 11 | 1.5
2018-03-06 17:00 | 12588.4424 | 58.992 | 8.31 | 33.17 | 57.52 | 34.98 | 5.45 | 1.48 | 11 | 1.76
2018-03-06 18:00 | 12228.6548 | 5.2682 | 7.88 | 41.11 | 70.95 | 52.71 | 8.88 | 1.56 | 11 | 6.13
2018-03-06 19:00 | 12260.6542 | -0.048233 | 61.39 | 61.39 | 61.27 | 33.48 | 29.81 | 20.74 | 8.73 | 25.09
2018-03-06 20:00 | 13448.0341 | -0.048233 | 53.68 | 53.68 | 59.8 | 28.96 | 46.28 | 57.5873 | 2.25 | 46.28
2018-03-06 21:00 | 12003.2042 | -0.048233 | 53.62 | 53.62 | 52.56 | 25.81 | 20.28 | 15 | 12 | 3
2018-03-06 22:00 | 11657.4042 | -0.048233 | 6.59 | 42.46 | 53.91 | 19.51 | 5.28 | 0.99 | 20.61 | 3.28
2018-03-06 23:00 | 11421.8042 | -0.048233 | 3.95 | 31.66 | 47.28 | 18.78 | 21.91 | 0.47 | 52.6962 | 21.71
2018-03-07 | 11286.9042 | -0.048233 | -0.72 | 46.65 | 62.21 | 21.56 | 28.31 | 0.47 | 55.0162 | 28.31
2018-03-07 01:00 | 12343.4491 | -0.048233 | -0.67 | 55.14 | 62.59 | 20.34 | 6 | 0.45 | 52.6962 | 6
2018-03-07 02:00 | 11079.8042 | -0.048233 | -1.03 | 58.07 | 59.34 | 18.68 | 18 | 0.45 | 35.06 | 4.09
2018-03-07 03:00 | 12141.9441 | -0.048233 | -1.06 | 51.95 | 55.61 | 18.96 | 4.89 | 0.99 | 26.65 | 4.89
2018-03-07 04:00 | 11392.3542 | -0.048233 | -0.92 | 47.6 | 47.78 | 20.39 | 5.07 | 0.99 | 18.56 | 4.09
2018-03-07 05:00 | 13567.2491 | -0.048233 | 0.47 | 28.04 | 55.61 | 21.64 | 6.16 | 0.99 | 52.6962 | 5.16
2018-03-07 06:00 | 13799.6542 | -0.048233 | 5.34 | 34.2 | 49.9 | 28.94 | 29.04 | 0.99 | 49.8362 | 29.04
2018-03-07 07:00 | 14746.0722 | 38.1813 | 8.28 | 30 | 54.61 | 28.44 | 26.66 | 22.05 | 8.61 | 26.83
2018-03-07 08:00 | 15469.5074 | 103.692 | 9.42 | 33.19 | 56.48 | 29.02 | 25.04 | 20 | 2.61 | 24.85
2018-03-07 09:00 | 17666.2736 | 183.283 | 48.44 | 48.44 | 66.89 | 34.94 | 35 | 23.12 | 1.76 | 35
2018-03-07 10:00 | 18168.9346 | 244.739 | 91.45 | 91.45 | 52.66 | 37.24 | 36.24 | 21.51 | 2 | 36.24
2018-03-07 11:00 | 17510.6262 | 744.75 | 110.74 | 110.74 | 51.74 | 40.69 | 4.14 | 10.03 | 1 | 2.53
2018-03-07 12:00 | 16294.704 | 1068.32 | 45.43 | 45.43 | 44.92 | 44.29 | 4.61 | 13.42 | 2 | 3.24
2018-03-07 13:00 | 17893.4857 | 1158.65 | 183.73 | 183.73 | 38.05 | 49.39 | 5 | 5.25 | 2 | 2
2018-03-07 14:00 | 14921.2329 | 980.561 | 13.29 | 24.14 | 15.17 | 52.88 | 4.2 | 6.03 | 1 | 4.2
2018-03-07 15:00 | 15599.3608 | 576.124 | 14.09 | 26.39 | 15.05 | 58.55 | 3.9 | 1 | 1 | 3.27
2018-03-07 16:00 | 13792.2653 | 460.174 | 13.95 | 36.03 | 15.66 | 52.14 | 3.01 | 1.22 | 1 | 3
2018-03-07 17:00 | 13227.8029 | 172.003 | 11.78 | 24.37 | 55.03 | 44.79 | 3.03 | 1.32 | 1 | 3.03
2018-03-07 18:00 | 14388.3112 | 7.2097 | 155.73 | 28.42 | 70.27 | 56.16 | 4.82 | 1.6 | 2.61 | 4.82
2018-03-07 19:00 | 12825.9042 | -0.048233 | 14.67 | 29.81 | 60.66 | 40.45 | 26.61 | 1.99 | 2.78 | 20.29
2018-03-07 20:00 | 13947.0491 | -0.048233 | 12.91 | 24.01 | 53.27 | 33.96 | 8.62 | 1.76 | 2 | 5
2018-03-07 21:00 | 12175.1542 | -0.048233 | 12.79 | 22.83 | 46.93 | 29.02 | 5.73 | 0.99 | 2 | 3.1
2018-03-07 22:00 | 12740.1291 | -0.048233 | 114.25 | 21.52 | 42.5 | 25.16 | 5.47 | 0.99 | 20.94 | 4
2018-03-07 23:00 | 10774.8542 | -0.048233 | 7.38 | 17.37 | 13 | 22.15 | 4 | 0.47 | 12 | 4
2018-03-08 | 11741.0441 | -0.048233 | 1.6 | 16.73 | 11.35 | 24.25 | 3 | 0.47 | 13.98 | 2.69
2018-03-08 01:00 | 10349.2542 | -0.048233 | 3.25 | 19.07 | 5.55 | 22.26 | 3 | 0.45 | 52.6962 | 2.7
2018-03-08 02:00 | 10185.8542 | -0.048233 | 4.6 | 22.53 | 3.89 | 22.16 | 2.01 | 0.45 | 22.18 | 1.64
2018-03-08 03:00 | 11249.4141 | -0.048233 | 5.09 | 26.26 | 5.38 | 22.05 | 2.01 | 0.99 | 20 | 1.45
2018-03-08 04:00 | 11734.7141 | -0.048233 | 7.81 | 28.35 | 5.37 | 22.47 | 3 | 0.99 | 14.87 | 1.04
2018-03-08 05:00 | 11494.0042 | -0.048233 | 9.28 | 28.32 | 6.96 | 23.04 | 4.2 | 0.99 | 21.59 | 4.2
2018-03-08 06:00 | 13068.1542 | -0.048233 | 11.03 | 20.52 | 14.32 | 25.41 | 19.1 | 0.99 | 32.89 | 19.1
2018-03-08 07:00 | 13822.11 | 76.5895 | 14.15 | 20.18 | 37.8 | 32.14 | 25 | 24.79 | 2 | 24.8
2018-03-08 08:00 | 14061.5583 | 99.6403 | 44.56 | 17.66 | 46.29 | 29.71 | 6.31 | 9.9 | 2 | 6.31
2018-03-08 09:00 | 14467.8787 | 179.346 | 15.7 | 18.47 | 52.81 | 29.82 | 5.27 | 8 | 2 | 5.07
2018-03-08 10:00 | 14405.4855 | 242.669 | 20.89 | 21.24 | 50.24 | 32.7 | 5.25 | 7.5 | 2 | 4.13
2018-03-08 11:00 | 14946.1647 | 846.805 | 740.3111 | 72.78 | 50.64 | 33.54 | 4.72 | 6.53 | 2 | 2.6
2018-03-08 12:00 | 15099.6952 | 648.416 | 19.89 | 19.89 | 48.73 | 36.22 | 4.25 | 9.29 | 2 | 2.65
2018-03-08 13:00 | 17019.5522 | 964.277 | 15.31 | 21.29 | 44.84 | 35.63 | 4.2 | 5.8 | 1 | 1.99
2018-03-08 14:00 | 16130.9426 | 840.993 | 192.18 | 22.31 | 41.97 | 36.23 | 3.93 | 7.79 | 1 | 2.81
2018-03-08 15:00 | 15510.8664 | 526.243 | 191.75 | 24.56 | 41.47 | 37.06 | 3.44 | 1.11 | 1 | 2.99
2018-03-08 16:00 | 14323.8046 | 232.066 | 135.02 | 24.08 | 46.86 | 37.98 | 3.65 | 1.1 | 0.84 | 2.41
2018-03-08 17:00 | 12132.1669 | 112.702 | 12.83 | 31.26 | 53.35 | 39.45 | 5.54 | 1.31 | 1.75 | 2.76
2018-03-08 18:00 | 11885.15 | 6.6842 | 50.15 | 50.15 | 62.13 | 41.5 | 13.86 | 1.12 | 1 | 13.86
2018-03-08 19:00 | 11864.5042 | -0.048233 | 71.65 | 45.11 | 55.99 | 51.43 | 25.74 | 2 | 2 | 25.3
2018-03-08 20:00 | 11668.8042 | -0.048233 | 43.77 | 43.77 | 51.19 | 43.69 | 17.25 | 2 | 2 | 17.25
2018-03-08 21:00 | 11425.6042 | -0.048233 | 13.86 | 37.44 | 47.48 | 38.33 | 7.55 | 1.31 | 5 | 3.1
2018-03-08 22:00 | 12249.5541 | -0.048233 | 13.25 | 31.23 | 46.7 | 40.53 | 5.83 | 1.21 | 2 | 4
2018-03-08 23:00 | 10514.5542 | -0.048233 | 11.97 | 22.37 | 12.07 | 29.47 | 5.32 | 0.47 | 30 | 5
2018-03-09 | 10426.2042 | -0.048233 | 11.5 | 22.55 | 12.86 | 26.56 | 3 | 0.5 | 13.26 | 3
2018-03-09 01:00 | 10354.9542 | -0.048233 | 12.43 | 20.67 | 8.34 | 19.91 | 3 | 0.45 | 11 | 2.11
2018-03-09 02:00 | 10215.3042 | -0.048233 | 12.33 | 23.19 | 6.99 | 19.46 | 3 | 0.45 | 9.22 | 2.01
2018-03-09 03:00 | 11558.5291 | -0.048233 | 12.17 | 12.17 | 5.73 | 18.36 | 3 | 0.97 | 8.93 | 1.11
2018-03-09 04:00 | 10747.3042 | -0.048233 | 13.9 | 15.5 | 5.67 | 18.82 | 3 | 0.97 | 1.61 | 1.51
2018-03-09 05:00 | 11771.4042 | -0.048233 | 47.06 | 47.06 | 6.96 | 20.09 | 5 | 0.97 | 10.78 | 2.25
2018-03-09 06:00 | 15073.7891 | -0.048233 | 98.67 | 98.67 | 10.97 | 20.97 | 35.91 | 13.85 | 30.29 | 35.91
2018-03-09 07:00 | 14285.7005 | 29.5795 | 14.97 | 19.75 | 37.66 | 24.03 | 19.42 | 14.39 | 2.11 | 19.26
2018-03-09 08:00 | 14392.3412 | 69.8328 | 15.08 | 19.66 | 37.24 | 23.87 | 4.86 | 7.94 | 2 | 3.83
2018-03-09 09:00 | 14873.6532 | 408.477 | 13.15 | 24.03 | 39.32 | 24.29 | 4.53 | 7.5 | 2 | 2.19
2018-03-09 10:00 | 15262.9679 | 717.282 | 13.54 | 28.37 | 40.65 | 26.76 | 5.72 | 7.5 | 2.61 | 3.23
2018-03-09 11:00 | 15279.6432 | 656.835 | 70.89 | 70.89 | 36.9 | 28.7 | 5.09 | 8.57 | 2.11 | 3.39
2018-03-09 12:00 | 17076.7797 | 208.521 | 65.89 | 65.89 | 34.78 | 31.08 | 5.1 | 8.7 | 2.11 | 4.29
2018-03-09 13:00 | 16335.8675 | 1158.65 | 97.06 | 97.06 | 15.81 | 30.87 | 4.58 | 7.75 | 2.11 | 3.29
2018-03-09 14:00 | 15470.1856 | 178.683 | 43.38 | 43.38 | 15.26 | 34.11 | 4.03 | 9.39 | 1 | 4.03
2018-03-09 15:00 | 15109.0137 | 345.34 | 68.51 | 68.51 | 14.92 | 35 | 3.34 | 0.99 | 1.44 | 3.16
2018-03-09 16:00 | 12900.144 | 87.0989 | 98.07 | 98.07 | 15.16 | 37.44 | 3.88 | 0.99 | 1.01 | 3.54
2018-03-09 17:00 | 13699.5598 | 39.3647 | 62.72 | 62.72 | 38.22 | 38.38 | 5.98 | 1.61 | 2 | 3.89
2018-03-09 18:00 | 13445.0092 | 3.0845 | 51.98 | 51.98 | 41.5 | 35.33 | 8.02 | 1.61 | 2 | 6
2018-03-09 19:00 | 13224.3741 | -0.048233 | 60.88 | 60.88 | 41.84 | 44.53 | 22.81 | 14.76 | 2 | 21.68
2018-03-09 20:00 | 11684.9542 | -0.048233 | 14.88 | 30.18 | 41.38 | 33.52 | 16.99 | 11.97 | 2 | 16.45
2018-03-09 21:00 | 11309.7042 | -0.048233 | 15.11 | 21.66 | 35 | 29.24 | 6.32 | 0.99 | 4.69 | 2.08
2018-03-09 22:00 | 10944.9042 | -0.048233 | 15.41 | 19.36 | 12.64 | 27.07 | 4.69 | 0.99 | 10.03 | 4
2018-03-09 23:00 | 11859.2041 | -0.048233 | 12.03 | 17.95 | 9.32 | 25.17 | 5 | 0.45 | 12 | 3.61
2018-03-10 | 11656.6441 | -0.048233 | 396.3957 | 16.21 | 5.34 | 23.33 | 3 | 0.45 | 11 | 3
2018-03-10 01:00 | 11678.7991 | -0.048233 | 15.67 | 15.67 | 8.39 | 23.93 | 3 | 0.45 | 11 | 2.5
2018-03-10 02:00 | 11579.6291 | -0.048233 | 806.5311 | 16.23 | 6.95 | 21.63 | 2.85 | 0.45 | 12.43 | 1.5
2018-03-10 03:00 | 10316.0042 | -0.048233 | 13.51 | 16.11 | 5.94 | 19.35 | 2.85 | 0.97 | 14.15 | 1.5
2018-03-10 04:00 | 11562.7491 | -0.048233 | 13.9 | 16.08 | 6.48 | 22.16 | 3 | 0.97 | 2.07 | 1.5
2018-03-10 05:00 | 12300.1941 | -0.048233 | 17.5 | 17.5 | 6.67 | 21.72 | 3.11 | 0.97 | 28.98 | 2.11
2018-03-10 06:00 | 13865.8141 | -0.048233 | 13.99 | 17.96 | 37.57 | 25.55 | 25.01 | 0.97 | 15 | 25.01
2018-03-10 07:00 | 15212.2366 | 26.1816 | 47.38 | 19.23 | 11.14 | 31.05 | 22.05 | 10 | 11 | 22.05
2018-03-10 08:00 | 15536.1505 | 83.209 | 18.91 | 18.91 | 23.46 | 28.21 | 4.31 | 7.5 | 11 | 3.31
2018-03-10 09:00 | 14055.7459 | 137.522 | 61.56 | 21.53 | 30.51 | 27.8 | 4.01 | 7.5 | 3.4 | 3.46
2018-03-10 10:00 | 13911.2471 | 178.418 | 72.32 | 72.32 | 15.08 | 32 | 4.01 | 7.54 | 2.11 | 3.04
2018-03-10 11:00 | 15377.2042 | 393.549 | 15.82 | 21.87 | 23.5 | 33.18 | 4.55 | 7.5 | 2.11 | 4.39
2018-03-10 12:00 | 13499.5598 | 261.063 | 15.66 | 21.52 | 15.34 | 35.24 | 3.67 | 6.95 | 2 | 3.24
2018-03-10 13:00 | 14567.1509 | 210.726 | 19.18 | 25.46 | 16.35 | 38.57 | 3.47 | 9.83 | 2.06 | 3.44
2018-03-10 14:00 | 14140.1587 | 189.994 | 15.9 | 24.22 | 15.78 | 39.97 | 3 | 10.27 | 1 | 3
2018-03-10 15:00 | 12197.8537 | 150.846 | 16.54 | 26.1 | 15.17 | 41.25 | 2.96 | 1.25 | 1 | 2.96
2018-03-10 16:00 | 13094.9786 | 101.302 | 15.71 | 28.49 | 15.38 | 37.41 | 3.25 | 1.25 | 1 | 2.96
2018-03-10 17:00 | 11604.5853 | 111.353 | 15.57 | 24.32 | 15.36 | 37 | 4.13 | 1.25 | 2 | 3.49
2018-03-10 18:00 | 12421.7228 | 5.1449 | 19.61 | 28.66 | 30.15 | 35.82 | 4.97 | 1.42 | 2 | 4
2018-03-10 19:00 | 10934.4542 | -0.048233 | 46.39 | 26.5 | 35.56 | 44.27 | 18.11 | 2 | 2 | 17.95
2018-03-10 20:00 | 12032.2241 | -0.048233 | 17.75 | 27.78 | 32.2 | 36.75 | 7.99 | 1.48 | 2 | 5
2018-03-10 21:00 | 10608.6042 | -0.048233 | 17.75 | 24.3 | 16.27 | 33.55 | 5.32 | 0.99 | 11 | 3.94
2018-03-10 22:00 | 11290.5591 | -0.048233 | 19.14 | 23.66 | 14.02 | 28.94 | 3.25 | 0.99 | 11 | 2.58
2018-03-10 23:00 | 9766.9042 | -0.048233 | 17.1 | 22.72 | 10.01 | 28.07 | 3 | 0.45 | 20 | 1.06
2018-03-11 | 9594.9542 | -0.048233 | 12.14 | 26.42 | 9.42 | 27.12 | 3.13 | 0.45 | 13.66 | 3.13
2018-03-11 01:00 | 10486.6491 | -0.048233 | 11.28 | 22.06 | 6.95 | 26.3 | 3 | 0.45 | 13.37 | 3
2018-03-11 02:00 | 10578.4341 | -0.048233 | 10.34 | 19.99 | 5.18 | 24.63 | 2.75 | 0.45 | 12.97 | 2.75
2018-03-11 03:00 | 10481.3741 | -0.048233 | 10.12 | 19.67 | 4.22 | 19.72 | 2.75 | 0.99 | 12.78 | 2.54
2018-03-11 04:00 | 10429.6791 | -0.048233 | 10.82 | 19.72 | 3.76 | 19.54 | 3.01 | 0.99 | 2.5 | 2.11
2018-03-11 05:00 | 10985.6641 | -0.048233 | 11.22 | 21.09 | 5.34 | 19.09 | 4 | 0.99 | 12.73 | 3.8
2018-03-11 06:00 | 11360.1891 | -0.048233 | 11.66 | 21.41 | 10.05 | 22.27 | 26.83 | 15.25 | 37 | 26.83
2018-03-11 07:00 | 10400.4599 | 29.8525 | 14.36 | 20.75 | 13.46 | 25.41 | 24.67 | 12.61 | 12 | 24.66
2018-03-11 08:00 | 10544.9026 | 73.8975 | 39.57 | 39.57 | 16.73 | 25.83 | 4.11 | 8.45 | 4 | 4
2018-03-11 09:00 | 11868.0031 | 128.292 | 14.95 | 31.1 | 24.12 | 28.56 | 4.91 | 10 | 2.11 | 3.98
2018-03-11 10:00 | 11621.5224 | 249.661 | 312.7957 | 268.47 | 33 | 32.18 | 7.5 | 7.5 | 1 | 5.79
2018-03-11 11:00 | 11241.9207 | 200.849 | 160.49 | 160.49 | 34.58 | 35.97 | 6 | 9.09 | 1 | 5.56
2018-03-11 12:00 | 11640.7561 | 212.892 | 54.01 | 54.01 | 35.08 | 37.02 | 5.55 | 8.76 | 1 | 4.22
2018-03-11 13:00 | 11039.5747 | 206.605 | 49.1 | 49.1 | 32.17 | 37.2 | 4.97 | 8.45 | 1 | 4.94
2018-03-11 14:00 | 11874.2381 | 221.202 | 15.7 | 27.95 | 15.04 | 35.05 | 4.7 | 7.88 | 1 | 4.33
2018-03-11 15:00 | 11514.1466 | 174.883 | 15.81 | 24.22 | 13.07 | 33.25 | 4.09 | 1.04 | 1 | 3.13
2018-03-11 16:00 | 11651.5966 | 91.1674 | 15.38 | 20.96 | 13.46 | 32.95 | 5.55 | 1.23 | 1 | 3.76
2018-03-11 17:00 | 11361.9901 | 38.6589 | 16.92 | 24.29 | 15.03 | 31.41 | 6 | 1.63 | 2.11 | 3
2018-03-11 18:00 | 11334.0008 | 3.1287 | 13.98 | 13.98 | 35.7 | 31.15 | 6.25 | 1.5 | 3.48 | 3
2018-03-11 19:00 | 10262.8042 | -0.048233 | 18.59 | 18.59 | 42.19 | 34.14 | 35.43 | 9.91 | 2 | 32.74
2018-03-11 20:00 | 10105.1042 | -0.048233 | 17.1 | 21.61 | 41.79 | 30.57 | 21.08 | 6.62 | 2 | 19.08
2018-03-11 21:00 | 9841.0042 | -0.048233 | 17.82 | 20.93 | 37.51 | 27.02 | 8 | 1.26 | 9.04 | 3.91
2018-03-11 22:00 | 9676.6542 | -0.048233 | 15.48 | 17.49 | 34.54 | 25.09 | 4.99 | 1.12 | 12 | 4.11
2018-03-11 23:00 | 10573.1591 | -0.048233 | 14.32 | 17.63 | 10 | 24.09 | 3.14 | 0.45 | 30 | 3.01
2018-03-12 | 10482.4291 | -0.048233 | 13.28 | 17.58 | 10.21 | 22.89 | 2.85 | 0.45 | 11 | 2.61
2018-03-12 01:00 | 9412.5542 | -0.048233 | 15.07 | 16.95 | 15.73 | 20.75 | 2.5 | 0.45 | 12 | 1.24
2018-03-12 02:00 | 10389.5891 | -0.048233 | 14.62 | 16.625 | 15.15 | 19.39 | 2 | 0.45 | 12 | 1.37
2018-03-12 03:00 | 9298.5542 | -0.048233 | 14.16 | 16.3 | 10.62 | 17.59 | 2 | 0.99 | 9.53 | 1.53
2018-03-12 04:00 | 10229.2291 | -0.048233 | 13.98 | 16.66 | 10.16 | 18.17 | 2.75 | 0.99 | 12 | 2.11
2018-03-12 05:00 | 10207.0741 | -0.048233 | 12.6 | 16.15 | 10.5 | 19.81 | 3.75 | 0.99 | 37 | 3.75
2018-03-12 06:00 | 9224.4542 | -0.048233 | 13.31 | 16.33 | 32.57 | 23.09 | 27.9 | 8.43 | 17.97 | 27.9
2018-03-12 07:00 | 9171.8881 | 69.6191 | 13.64 | 17.89 | 32.96 | 24.91 | 4 | 9.36 | 11 | 17.78
2018-03-12 08:00 | 10055.0045 | 104.81 | 14.77 | 18.76 | 33.9 | 25.19 | 4.29 | 7.5 | 2.11 | 4
2018-03-12 09:00 | 9997.4226 | 170.23 | 16.66 | 19.78 | 34.52 | 27.76 | 5.72 | 10.59 | 2.06 | 4.72
2018-03-12 10:00 | 8963.1911 | 182.938 | 17.06 | 20.43 | 34.44 | 34.26 | 16 | 14.25 | 2 | 15.15
2018-03-12 11:00 | 8861.8042 | 209.215 | 16.85 | 20.96 | 34.49 | 32.36 | 17.32 | 12.43 | 2 | 15.32
2018-03-12 12:00 | 9828.3747 | 219.995 | 17.53 | 19.3 | 32.12 | 29.83 | 20.05 | 14 | 2 | 18.05
2018-03-12 13:00 | 9829.4867 | 212.049 | 17.17 | 19.78 | 23.81 | 27.25 | 4.91 | 10 | 2 | 3.91
2018-03-12 14:00 | 9758.5506 | 190.811 | 16.26 | 19.58 | 10.11 | 25.93 | 4 | 0.99 | 1 | 3
2018-03-12 15:00 | 8918.6769 | 322.081 | 16.04 | 18.41 | 8.74 | 25.79 | 3.8 | 1.13 | 1.44 | 3.38
2018-03-12 16:00 | 8922.0608 | 260.643 | 14.93 | 17.89 | 25.45 | 23.96 | 4 | 1.15 | 1 | 2.71
2018-03-12 17:00 | 9772.7868 | 221.305 | 13.85 | 17.53 | 32.35 | 25.14 | 5.11 | 1.15 | 3.5 | 3.56
2018-03-12 18:00 | 9591.5121 | 11.4807 | 13.57 | 17.36 | 37.29 | 26.72 | 5.97 | 1.56 | 3.5 | 4.09
2018-03-12 19:00 | 9703.8391 | -0.048233 | 13.66 | 17.62 | 43.58 | 31.89 | 15.74 | 11.34 | 2 | 15.74
2018-03-12 20:00 | 8785.5542 | -0.048233 | 11.93 | 19.04 | 40.08 | 27.67 | 5.17 | 1.48 | 2 | 3.91
2018-03-12 21:00 | 8786.5042 | -0.048233 | 2.93 | 19.58 | 34.17 | 24.67 | 3.81 | 1.15 | 12 | 3
2018-03-12 22:00 | 8745.6542 | -0.048233 | 6.44 | 18.34 | 32.14 | 22 | 3.98 | 0.45 | 30 | 3
2018-03-12 23:00 | 9522.3791 | -0.048233 | 3.2 | 19.48 | 8.99 | 21.53 | 3 | 0.5 | 19.75 | 3
2018-03-13 | 8480.6042 | -0.048233 | 2.09 | 19.22 | 6.65 | 16.67 | 3 | 0.45 | 12.79 | 3
2018-03-13 01:00 | 9464.3541 | -0.048233 | 5.39 | 21.5 | 11.5 | 16.81 | 2.61 | 0.45 | 14.03 | 2.61
2018-03-13 02:00 | 9493.8941 | -0.048233 | 1.955 | 19.82 | 9.8 | 16.9 | 2.61 | 0.99 | 15 | 2.61
2018-03-13 03:00 | 9432.7041 | -0.048233 | -1.48 | 19.85 | 9.88 | 17.33 | 2.35 | 0.99 | 9.73 | 2.16
2018-03-13 04:00 | 8774.1542 | -0.048233 | -1.86 | 19.7 | 10.04 | 19.52 | 2.75 | 0.99 | 18 | 2.75
2018-03-13 05:00 | 10920.2541 | -0.048233 | -2.12 | 19.84 | 9.9 | 23.63 | 26.5 | 0.99 | 38.37 | 23.5
2018-03-13 06:00 | 12928.9741 | -0.048233 | -4.05 | 19.45 | 39.3 | 31.42 | 17.89 | 11.85 | 17.99 | 17.89
2018-03-13 07:00 | 14041.2309 | 77.2236 | -19.99 | 19.53 | 50.48 | 31.12 | 18.43 | 12.42 | 15.82 | 18.43
2018-03-13 08:00 | 13290.4382 | 507.935 | -1.98 | 18.76 | 42.77 | 27.83 | 6.99 | 10 | 12.97 | 5.51
2018-03-13 09:00 | 15176.597 | 757.4 | 0 | 19.92 | 40.28 | 25.16 | 6.67 | 8.74 | 2 | 3.05
2018-03-13 10:00 | 13451.5773 | 606.555 | 2.74 | 20.01 | 34.91 | 25.76 | 5.05 | 7.5 | 2.11 | 3.26
2018-03-13 11:00 | 15169.75 | 1115.91 | 0.07 | 20.32 | 34.1 | 24.88 | 4.48 | 6.58 | 2.61 | 2.11
2018-03-13 12:00 | 14749.3675 | 1158.65 | 9.7 | 19.8 | 32.33 | 25.13 | 4.04 | 6.1 | 3.13 | 2.11
2018-03-13 13:00 | 15371.3437 | 791.994 | 9.76 | 19.41 | 32.36 | 25.67 | 4.01 | 7.53 | 2.11 | 2.11
2018-03-13 14:00 | 14256.0462 | 1023.84 | 9.45 | 18.93 | 30.68 | 26.55 | 3.75 | 1.06 | 2.11 | 2.71
2018-03-13 15:00 | 11890.6303 | 900.453 | 12.35 | 19.44 | 30.55 | 26.86 | 3.46 | 1.15 | 2.11 | 1.72
2018-03-13 16:00 | 12726.5789 | 510.108 | 13.54 | 19.31 | 29.3 | 27.71 | 3.75 | 0.99 | 1 | 2.16
2018-03-13 17:00 | 10741.6262 | 241.975 | 14.78 | 19.65 | 32.27 | 29.03 | 4.46 | 1.82 | 3.21 | 3.78
2018-03-13 18:00 | 11294.0485 | 11.2592 | 15.96 | 19.76 | 35.03 | 32.61 | 22.51 | 8.1 | 4.11 | 21.84
2018-03-13 19:00 | 10248.5542 | -0.048233 | 16.91 | 20.39 | 40.09 | 45.02 | 30.69 | 8.1 | 2.11 | 29.73
2018-03-13 20:00 | 10328.3542 | -0.048233 | 20.14 | 24.95 | 35.63 | 33.2 | 18.1 | 1.45 | 2.11 | 16.1
2018-03-13 21:00 | 11263.1291 | -0.048233 | 17.12 | 20.73 | 32 | 25.24 | 5.7 | 1.42 | 10 | 3.91
2018-03-13 22:00 | 9817.2542 | -0.048233 | 15.12 | 21.7 | 12.4 | 22.66 | 5 | 0.45 | 30 | 4.5
2018-03-13 23:00 | 10506.6941 | -0.048233 | 13.06 | 19.64 | 11.05 | 21.13 | 3.01 | 0.45 | 30 | 3.01
2018-03-14 | 10285.1441 | -0.048233 | 10.8 | 19.85 | 5.14 | 18.66 | 3 | 0.45 | 12.39 | 2.98
2018-03-14 01:00 | 10171.2041 | -0.048233 | 0 | 19.92 | 4.01 | 17.65 | 2.8 | 0.45 | 10.12 | 2.5
2018-03-14 02:00 | 9083.8542 | -0.048233 | -0.55 | 19.72 | 3.7 | 17.64 | 2.85 | 1 | 11.73 | 2.53
2018-03-14 03:00 | 10096.2991 | -0.048233 | -0.57 | 20.3 | 3.96 | 17.35 | 2.75 | 0.99 | 9.55 | 2.5
2018-03-14 04:00 | 9513.2542 | -0.048233 | -0.58 | 19.85 | 4.03 | 18.36 | 2.75 | 0.99 | 15 | 2.51
2018-03-14 05:00 | 11707.2841 | -0.048233 | -0.49 | 18.02 | 8.22 | 20.67 | 25 | 1 | 14.85 | 22
2018-03-14 06:00 | 13392.4657 | 1.2803 | 2.51 | 19.6 | 12.26 | 29.87 | 20 | 12.45 | 21.72 | 20
2018-03-14 07:00 | 12982.5508 | 107.843 | 11.43 | 20.62 | 40.98 | 29.38 | 7.66 | 9.26 | 3.91 | 6.66
2018-03-14 08:00 | 12960.052 | 115.16 | 5.65 | 19.79 | 35.72 | 25.01 | 5.5 | 19.54 | 2.11 | 19.34
2018-03-14 09:00 | 13669.5766 | 630.028 | 10.37 | 22.02 | 35.97 | 24.03 | 3.78 | 8.87 | 2.87 | 2.78
2018-03-14 10:00 | 13853.7113 | 953.854 | 11.77 | 20.93 | 36.98 | 23.08 | 2.77 | 8.87 | 2.87 | 1.77
2018-03-14 11:00 | 14950.4472 | 1104.04 | 12.06 | 19.65 | 37.02 | 23.35 | 2.81 | 9.67 | 3.01 | 1.57
2018-03-14 12:00 | 13986.9631 | 771.119 | 11.54 | 17.63 | 40.02 | 23.44 | 3.79 | 10.58 | 2.11 | 1.5
2018-03-14 13:00 | 14099.4082 | 382.368 | 11.96 | 18.35 | 36.39 | 25.75 | 4 | 14.25 | 2.11 | 1.94
2018-03-14 14:00 | 13495.7615 | 580.191 | 12.04 | 19.57 | 34.44 | 26.05 | 3.5 | 1.22 | 1 | 1.86
2018-03-14 15:00 | 11614.1803 | 402.453 | 13.32 | 19.73 | 34.25 | 26.98 | 3.75 | 1.44 | 1 | 2.16
2018-03-14 16:00 | 12108.1358 | 257.906 | 13.63 | 20.3 | 34.32 | 29.28 | 28.9 | 1.22 | 0.76 | 26.9
2018-03-14 17:00 | 11733.3872 | 106.694 | 13.77 | 20.36 | 35.01 | 28.6 | 29.39 | 1.22 | 2.49 | 27.75
2018-03-14 18:00 | 10338.6236 | 7.7617 | 12.56 | 19.76 | 39.62 | 31.05 | 18.02 | 10.01 | 2.87 | 17.58
2018-03-14 19:00 | 11612.3341 | -0.048233 | 9.77 | 19.57 | 39.62 | 36.81 | 16.09 | 8.17 | 2 | 14.49
2018-03-14 20:00 | 11588.0691 | -0.048233 | 8.49 | 19.26 | 34.25 | 27.46 | 4.66 | 9.35 | 2 | 2.71
2018-03-14 21:00 | 11453.0291 | -0.048233 | 6.7 | 17.68 | 15.49 | 24.23 | 5.25 | 1.4 | 7.88 | 3
2018-03-14 22:00 | 11239.9191 | -0.048233 | 5.67 | 18.03 | 15.2 | 20.93 | 4.3 | 0.45 | 27 | 4.87
2018-03-14 23:00 | 10903.3741 | -0.048233 | 2.92 | 17.21 | 8.92 | 20.8 | 3.11 | 0.45 | 27 | 3.11
2018-03-15 | 9582.6042 | -0.048233 | 2.78 | 17.63 | 5.15 | 18.3 | 3 | 0.45 | 20 | 3
2018-03-15 01:00 | 10559.4441 | -0.048233 | 1.74 | 17.15 | 5.37 | 17.51 | 3 | 0.45 | 18 | 2.71
2018-03-15 02:00 | 10489.8141 | -0.048233 | -1.29 | 19.21 | 4.52 | 17.65 | 3 | 0.97 | 18.81 | 2.71
2018-03-15 03:00 | 10529.9041 | -0.048233 | -6.25 | 19.63 | 4.44 | 18 | 3 | 0.97 | 16.84 | 2.71
2018-03-15 04:00 | 10811.5891 | -0.048233 | -6.15 | 19.69 | 5.31 | 19.41 | 3 | 0.97 | 19.75 | 3
2018-03-15 05:00 | 11943.6041 | -0.048233 | -2.33 | 20.54 | 8.09 | 21.83 | 5 | 0.97 | 20 | 5
2018-03-15 06:00 | 13362.9335 | 1.2876 | -2.12 | 20.64 | 17.02 | 30.59 | 20 | 10.16 | 21.52 | 20
2018-03-15 07:00 | 14483.3987 | 43.34 | 7.6 | 30.42 | 15.68 | 27.52 | 6.55 | 8.97 | 3.46 | 5.55
2018-03-15 08:00 | 14756.3673 | 128.078 | 6.34 | 23.73 | 32.7 | 26.45 | 17.44 | 16.53 | 2.61 | 4.8
2018-03-15 09:00 | 14997.0592 | 209.222 | 11.38 | 40.68 | 32.42 | 26.73 | 20 | 8.57 | 2.23 | 5.11
2018-03-15 10:00 | 13550.8902 | 270.095 | 12.91 | 31.11 | 31.82 | 25.24 | 6.62 | 8 | 2.23 | 4.41
2018-03-15 11:00 | 15366.0761 | 309.001 | 14.62 | 27.8 | 31.69 | 25 | 6.2 | 9.09 | 3.01 | 3.91
2018-03-15 12:00 | 16870.9439 | 325.416 | 72.6 | 23.56 | 30.76 | 22.62 | 4.19 | 14.66 | 2.11 | 3.1
2018-03-15 13:00 | 14992.4299 | 316.834 | 19.25 | 27.16 | 17.73 | 23.63 | 22.83 | 21.94 | 1.44 | 21.94
2018-03-15 14:00 | 12837.7974 | 280.471 | 33.51 | 22.07 | 17.46 | 23.21 | 25.44 | 0.99 | 1 | 22.44
2018-03-15 15:00 | 13649.2123 | 224.642 | 20 | 21.13 | 15.53 | 21.42 | 38.3 | 0.99 | 1 | 35.64
2018-03-15 16:00 | 12908.0157 | 148.086 | 20 | 20 | 16.94 | 21.32 | 80.2641 | 0.99 | 1 | 49.28
2018-03-15 17:00 | 11391.7331 | 168.298 | 18.5 | 18.5 | 31.38 | 21.52 | 40.22 | 0.99 | 2 | 35.33
2018-03-15 18:00 | 11067.704 | 5.2148 | 17.99 | 17.99 | 35.11 | 23.49 | 25.6 | 11.13 | 2 | 22.57
2018-03-15 19:00 | 11029.4542 | -0.048233 | 17.99 | 17.99 | 42.76 | 23.4 | 20.29 | 8.21 | 2 | 19.85
2018-03-15 20:00 | 12305.4691 | -0.048233 | 30.1 | 20.17 | 36.64 | 25.47 | 19.75 | 8.15 | 3.01 | 19.54
2018-03-15 21:00 | 10892.6542 | -0.048233 | 19.17 | 19.17 | 29.52 | 21.87 | 8 | 0.99 | 3.77 | 4.59
2018-03-15 22:00 | 11795.9041 | -0.048233 | 18.98 | 18.98 | 11.31 | 19.9 | 4.74 | 0.45 | 22 | 4.74
2018-03-15 23:00 | 11444.5891 | -0.048233 | 16.69 | 16.69 | 8.5 | 17.05 | 3.75 | 0.45 | 16.15 | 3.15
2018-03-16 | 10159.2542 | -0.048233 | 15.59 | 15.59 | 17.16 | 18.59 | 3 | 0.3 | 25 | 3
2018-03-16 01:00 | 11244.1391 | -0.048233 | 10.72 | 10.72 | 15.92 | 15.91 | 3 | 0.3 | 8.11 | 2.14
2018-03-16 02:00 | 10949.7941 | -0.048233 | 12.03 | 12.03 | 14.34 | 15.62 | 3 | 0.97 | 8.61 | 1.54
2018-03-16 03:00 | 9859.0542 | -0.048233 | 10.88 | 10.88 | 14.09 | 16.26 | 3 | 0.97 | 6.48 | 1.47
2018-03-16 04:00 | 10144.0542 | -0.048233 | 10.98 | 10.98 | 13.43 | 19.45 | 3 | 0.97 | 10.79 | 2.1
2018-03-16 05:00 | 12203.1341 | -0.048233 | 9.93 | 9.93 | 37.64 | 20.7 | 5.1 | 0.97 | 57.6962 | 4.25
2018-03-16 06:00 | 14092.9339 | 1.2312 | 14.28 | 15.14 | 41.49 | 24.36 | 24.68 | 17.1 | 12.01 | 24.69
2018-03-16 07:00 | 14818.6054 | 30.0715 | 17.27 | 17.27 | 38.69 | 25.34 | 17.41 | 15.41 | 4.01 | 17.41
2018-03-16 08:00 | 15382.058 | 81.1498 | 15.79 | 16.72 | 35.96 | 22.02 | 5.34 | 7.69 | 2 | 4
2018-03-16 09:00 | 14036.1635 | 135.909 | 17.24 | 17.67 | 33.47 | 21.55 | 4.6 | 8.41 | 2 | 4.11
2018-03-16 10:00 | 15482.6071 | 217.457 | 17.5 | 17.81 | 32.19 | 22.66 | 5.37 | 7.58 | 2 | 3.1
2018-03-16 11:00 | 13547.2394 | 206.252 | 16.05 | 16.91 | 32.72 | 23.75 | 6.15 | 8.45 | 2 | 3.05
2018-03-16 12:00 | 13902.7684 | 216.493 | 16.3 | 18.74 | 31.55 | 24.03 | 5.65 | 9.66 | 2 | 3.1
2018-03-16 13:00 | 14033.7923 | 208.413 | 16.85 | 19.43 | 30.5 | 25.03 | 6 | 10 | 2 | 4.33
2018-03-16 14:00 | 15358.2648 | 186.597 | 19.46 | 19.47 | 16.96 | 24.62 | 6.17 | 0.99 | 1.33 | 3.1
2018-03-16 15:00 | 13010.8903 | 145.674 | 83.36 | 19.18 | 16.96 | 25.89 | 6.48 | 0.99 | 1.63 | 2.75
2018-03-16 16:00 | 13360.6019 | 94.0776 | 136.8 | 19.91 | 16.9 | 25.31 | 25.15 | 0.99 | 1.83 | 22.92
2018-03-16 17:00 | 13182.5046 | 39.265 | 19.01 | 19.01 | 31.7 | 24.23 | 19.33 | 6.59 | 2 | 17.2
2018-03-16 18:00 | 11755.1584 | 3.851 | 18.76 | 18.76 | 38.03 | 23.02 | 15.95 | 9.87 | 2 | 15.74
2018-03-16 19:00 | 11570.9542 | -0.048233 | 19.16 | 19.16 | 45.62 | 22.23 | 19.03 | 10.48 | 2 | 19.03
2018-03-16 20:00 | 11524.4042 | -0.048233 | 19.15 | 19.15 | 39.45 | 23.22 | 14.23 | 8.1 | 2 | 4.11
2018-03-16 21:00 | 11317.3042 | -0.048233 | 19.17 | 19.17 | 35 | 21.62 | 7.27 | 0.99 | 7.71 | 4.5
2018-03-16 22:00 | 11935.1641 | -0.048233 | 16.44 | 17.62 | 14.31 | 17.25 | 4.01 | 0.3 | 30 | 4
2018-03-16 23:00 | 11561.6941 | -0.048233 | 14.17 | 15.6 | 12.29 | 14.94 | 3.15 | 0.3 | 25 | 3.15
2018-03-17 | 11370.7391 | -0.048233 | 10.63 | 10.63 | 10.03 | 11.18 | 3 | 0.3 | 15.26 | 3
2018-03-17 01:00 | 10185.8542 | -0.048233 | 3.9 | 3.9 | 5.47 | 9.97 | 2.75 | 0.3 | 14 | 2.25
2018-03-17 02:00 | 11259.9641 | -0.048233 | -0.15 | -0.15 | 5.72 | 8.24 | 3 | 0.99 | 14 | 2.11
2018-03-17 03:00 | 11247.3041 | -0.048233 | -0.23 | -0.23 | 5.41 | 8.22 | 3.6 | 0.99 | 10 | 1.98
2018-03-17 04:00 | 10260.9042 | -0.048233 | -0.35 | -0.35 | 5.46 | 9.88 | 4 | 0.99 | 14 | 2.4
2018-03-17 05:00 | 12395.1441 | -0.048233 | 2.62 | 2.62 | 11.1 | 14.08 | 5 | 0.99 | 57.6962 | 18
2018-03-17 06:00 | 14190.7541 | -0.048233 | 13.77 | 13.77 | 30.47 | 19.82 | 25 | 21 | 11.45 | 25
2018-03-17 07:00 | 13702.2282 | 33.3981 | 17.1 | 17.34 | 39.56 | 21.03 | 7.32 | 10.46 | 8.46 | 12.26
2018-03-17 08:00 | 16152.9404 | 90.844 | 13.67 | 13.67 | 33.28 | 21.25 | 6.13 | 8.45 | 3.5 | 4.5
2018-03-17 09:00 | 16055.7728 | 145.742 | 16.85 | 17.01 | 31.54 | 21.71 | 8 | 10 | 2.73 | 4.5
2018-03-17 10:00 | 14078.9088 | 189.904 | 15.76 | 15.76 | 29.52 | 22.22 | 6.76 | 10.85 | 2.9 | 4.5
2018-03-17 11:00 | 13803.9332 | 215.456 | 16.48 | 16.48 | 23.43 | 23.48 | 7.11 | 10.6 | 2 | 1.86
2018-03-17 12:00 | 15835.703 | 325.145 | 18.01 | 18.01 | 22.21 | 25.06 | 5.31 | 12.06 | 2 | 2.25
2018-03-17 13:00 | 13959.6724 | 315.392 | 20.41 | 20.41 | 22.66 | 29.32 | 8.02 | 13.08 | 2 | 5.11
2018-03-17 14:00 | 13714.9343 | 806.773 | 84.07 | 25.29 | 22.61 | 34.5 | 11.94 | 1.12 | 1 | 7.1
2018-03-17 15:00 | 14393.8725 | 665.481 | 246.8357 | 165.96 | 15.74 | 36.64 | 16.92 | 8.15 | 1 | 10
2018-03-17 16:00 | 13769.3494 | 500.516 | 247.3657 | 23.79 | 22.84 | 38.75 | 19 | 7.98 | 0.33 | 11.46
2018-03-17 17:00 | 13351.6738 | 250.615 | 20.56 | 22.82 | 29.79 | 32.42 | 17.99 | 1.34 | 2.64 | 10.92
2018-03-17 18:00 | 11793.6472 | 12.3655 | 19.67 | 19.67 | 32.1 | 27.69 | 13.96 | 8.9 | 4.37 | 11.3
2018-03-17 19:00 | 12899.4341 | -0.048233 | 17.42 | 17.42 | 33.64 | 29.53 | 19.19 | 16.19 | 2 | 19.19
2018-03-17 20:00 | 12758.0641 | -0.048233 | 47.06 | 20.33 | 33.61 | 25.77 | 10.3 | 8.45 | 2 | 3.1
2018-03-17 21:00 | 12538.6241 | -0.048233 | 18.35 | 18.35 | 24.3 | 23.02 | 5.76 | 1.2 | 7.61 | 4.5
2018-03-17 22:00 | 10816.6542 | -0.048233 | 17.19 | 19.57 | 28.52 | 20.66 | 6.22 | 0.45 | 24.88 | 5.42
2018-03-17 23:00 | 11643.9841 | -0.048233 | 15.39 | 16.99 | 11.06 | 19.96 | 5.51 | 0.45 | 15.12 | 4.91
2018-03-18 | 10194.4042 | -0.048233 | 14.69 | 16.2 | 9.57 | 19.28 | 3 | 0.45 | 24.11 | 2.4
2018-03-18 01:00 | 10093.7042 | -0.048233 | 14.32 | 15.67 | 5.71 | 17.15 | 2.75 | 0.45 | 36.77 | 1.5
2018-03-18 02:00 | 11297.9441 | -0.048233 | 13.28 | 15.85 | 5.51 | 16.17 | 2.75 | 1 | 8.75 | 1.5
2018-03-18 03:00 | 11358.0791 | -0.048233 | 12.43 | 16.11 | 5.63 | 16.31 | 2.75 | 1.11 | 3.52 | 1.5
2018-03-18 04:00 | 10276.1042 | -0.048233 | 12.35 | 16.34 | 5.5 | 17.07 | 2.75 | 1.22 | 14.11 | 2.11
2018-03-18 05:00 | 11854.9841 | -0.048233 | 13.01 | 16.65 | 13.09 | 18.03 | 2.91 | 1 | 12.5 | 3.86
2018-03-18 06:00 | 11087.6161 | 1.1748 | 13.14 | 17.77 | 49.81 | 21.51 | 28.68 | 9.26 | 11 | 28.68
2018-03-18 07:00 | 12468.9735 | 29.9322 | 14.9 | 18.13 | 47.75 | 22.21 | 3.35 | 7.5 | 2 | 3.35
2018-03-18 08:00 | 11149.3288 | 84.1356 | 14.55 | 18.27 | 49.08 | 23.09 | 4 | 7.5 | 3.5 | 2.85
2018-03-18 09:00 | 11553.2939 | 137.362 | 15.64 | 19.6 | 56.13 | 26.84 | 6.3 | 7.97 | 3.5 | 5.3
2018-03-18 10:00 | 11707.3155 | 179.49 | 16.75 | 19.87 | 46.17 | 29.27 | 6.68 | 9.55 | 2.84 | 6.36
2018-03-18 11:00 | 12957.1239 | 206.634 | 17.49 | 22.89 | 49.46 | 30.67 | 8.49 | 9.5 | 2 | 6.44
2018-03-18 12:00 | 11692.8736 | 217.288 | 17.02 | 28.51 | 48.38 | 31.13 | 8.28 | 10 | 2 | 6.63
2018-03-18 13:00 | 11674.3125 | 210.75 | 74.36 | 28.52 | 43.44 | 38.79 | 15.28 | 8.91 | 2 | 13.83
2018-03-18 14:00 | 11078.6635 | 187.751 | 17.48 | 23.94 | 42.14 | 42.77 | 17.06 | 0.99 | 1.23 | 15.98
2018-03-18 15:00 | 12043.6732 | 148.804 | 253.2657 | 23.61 | 42.08 | 46.78 | 21.4 | 0.99 | 1.47 | 19.33
2018-03-18 16:00 | 10833.5393 | 96.7256 | 257.2357 | 83.29 | 45.02 | 45.53 | 19.96 | 1.02 | 1 | 16.31
2018-03-18 17:00 | 12139.6772 | 149.803 | 151.8 | 30.49 | 50 | 36.81 | 14.38 | 9.09 | 2.11 | 4.97
2018-03-18 18:00 | 10851.4636 | 9.5933 | 19.63 | 25.11 | 53.89 | 31.02 | 14.98 | 12.57 | 2.6 | 14.98
2018-03-18 19:00 | 11957.3191 | -0.048233 | 18.55 | 22.85 | 56.38 | 30.98 | 19.78 | 15.78 | 2.43 | 19.78
2018-03-18 20:00 | 10896.4542 | -0.048233 | 972.8311 | 705.22 | 49.05 | 28.14 | 6.11 | 10.48 | 2.59 | 4.31
2018-03-18 21:00 | 11822.2791 | -0.048233 | 15.72 | 19.8 | 51.29 | 25.63 | 4 | 0.99 | 11 | 3.64
2018-03-18 22:00 | 10456.6042 | -0.048233 | 15.66 | 17.03 | 46.22 | 22.41 | 8.43 | 0.45 | 12.5 | 5.58
2018-03-18 23:00 | 10107.0042 | -0.048233 | 13.38 | 16.27 | 33.08 | 20.57 | 6.85 | 0.45 | 11.81 | 4.85
2018-03-19 | 9999.6542 | -0.048233 | 10.18 | 15.99 | 42.53 | 16.15 | 3 | 0.45 | 8.83 | 4.11
2018-03-19 01:00 | 9993.0042 | -0.048233 | 12.08 | 15.56 | 37.87 | 14.28 | 3 | 0.45 | 14.98 | 2.11
2018-03-19 02:00 | 10966.6741 | -0.048233 | 3.32 | 9.36 | 35.68 | 11.61 | 3 | 0.99 | 11.52 | 2.11
2018-03-19 03:00 | 10966.6741 | -0.048233 | 2.33 | 7.12 | 35.79 | 10.62 | 2.89 | 0.99 | 9.68 | 2.11
2018-03-19 04:00 | 10871.7241 | -0.048233 | 4.39 | 7.16 | 37.97 | 10.23 | 3 | 0.99 | 12.2 | 2.61
2018-03-19 05:00 | 11022.5891 | -0.048233 | 8.84 | 12.11 | 59.12 | 13.05 | 3.11 | 0.99 | 17.95 | 13.85
2018-03-19 06:00 | 11226.4735 | 3.2071 | 11.9 | 15.96 | 60.81 | 18.72 | 39.08 | 15.01 | 34.08 | 84.1962
2018-03-19 07:00 | 10183.0509 | 107.001 | 9.15 | 15.81 | 56.96 | 18.94 | 4 | 10.18 | 3.33 | 4.5
2018-03-19 08:00 | 11438.3364 | 453.025 | 9.92 | 13.1 | 52.3 | 20.82 | 4 | 12.45 | 1.62 | 4.5
2018-03-19 09:00 | 10950.575 | 872.921 | 6.2 | 16.09 | 53.57 | 21.39 | 4 | 13.07 | 2.11 | 4.11
2018-03-19 10:00 | 11171.2856 | 941.248 | 12.4 | 15.85 | 51.68 | 22.62 | 3.75 | 11.47 | 2.11 | 3.75
2018-03-19 11:00 | 11321.2735 | 1009.13 | 13.21 | 16.46 | 48.93 | 24.97 | 3.62 | 11.76 | 3.01 | 2.42
2018-03-19 12:00 | 12667.29 | 1010.91 | 11.21 | 18.69 | 40.88 | 25.5 | 4 | 10 | 2.02 | 2.4
2018-03-19 13:00 | 11601.4 | 1156 | 14.62 | 21.15 | 38.45 | 27.75 | 4.42 | 10 | 2 | 2.4
2018-03-19 14:00 | 11542.9085 | 1031.43 | 16.02 | 23.06 | 35.15 | 33.67 | 5.42 | 0.99 | 1 | 3.17
2018-03-19 15:00 | 11397.8359 | 741.722 | 14.2 | 23.98 | 35.14 | 41.86 | 17.12 | 0.99 | 1 | 3.77
2018-03-19 16:00 | 12358.1793 | 534.914 | 14.55 | 32.5 | 39.39 | 45.06 | 18.94 | 1.28 | 1 | 12.2
2018-03-19 17:00 | 12006.13 | 219.218 | 40.2 | 40.2 | 42.3 | 35 | 14.22 | 1.42 | 2 | 13.01
2018-03-19 18:00 | 11897.7113 | 12.4515 | 15.53 | 25.46 | 52.12 | 28.51 | 14.07 | 9.07 | 3.5 | 13.07
2018-03-19 19:00 | 10571.5542 | -0.048233 | 15.6 | 21.19 | 54.53 | 27.25 | 27.55 | 12.73 | 2.11 | 27.55
2018-03-19 20:00 | 10736.8542 | -0.048233 | 17.83 | 23.89 | 53.51 | 25.39 | 20.98 | 8.18 | 2 | 20.04
2018-03-19 21:00 | 11773.7491 | -0.048233 | 16.42 | 19.67 | 48.63 | 24.41 | 3.92 | 0.99 | 10 | 2.92
2018-03-19 22:00 | 11497.3391 | -0.048233 | 16.32 | 20.29 | 44.29 | 18.6 | 6 | 0.45 | 30 | 4
2018-03-19 23:00 | 10180.1542 | -0.048233 | 15.3 | 15.3 | 37.82 | 16.8 | 4 | 0.45 | 12.5 | 3.11
2018-03-20 | 11190.3341 | -0.048233 | 7.66 | 7.66 | 37.25 | 15.14 | 21.56 | 0.45 | 10.03 | 20.56
2018-03-20 01:00 | 10025.3042 | -0.048233 | 8.67 | 8.67 | 36.14 | 10.88 | 4 | 0.45 | 10.29 | 2.4
2018-03-20 02:00 | 9821.0542 | -0.048233 | 6.65 | 6.65 | 34.13 | 9.73 | 3.51 | 1.24 | 10.11 | 19.11
2018-03-20 03:00 | 9495.2042 | -0.048233 | 5.21 | 5.21 | 34.21 | 9.03 | 3.51 | 1.25 | 8.18 | 2.4
2018-03-20 04:00 | 9847.6542 | -0.048233 | 5.23 | 5.23 | 36.87 | 11 | 4 | 1.17 | 10.11 | 4.66
2018-03-20 05:00 | 12060.7091 | -0.048233 | 6.73 | 6.73 | 37.39 | 16.36 | 20.02 | 1.35 | 23.66 | 20.02
2018-03-20 06:00 | 12546.2367 | 3.5649 | 8.87 | 8.87 | 52.14 | 22.18 | 35 | 9.41 | 12.14 | 35
2018-03-20 07:00 | 13835.8256 | 127.027 | 16.48 | 17.2 | 45.07 | 21.88 | 7.11 | 10.34 | 2.79 | 6.51
2018-03-20 08:00 | 16408.7399 | 476.308 | 12.76 | 12.76 | 45.72 | 22.25 | 4.82 | 13.7 | 2.21 | 3.2
2018-03-20 09:00 | 16006.4274 | 704.871 | 16.84 | 16.84 | 43.97 | 23.89 | 21.07 | 20.05 | 2.47 | 20.22
2018-03-20 10:00 | 18251.116 | 966.636 | 13.26 | 13.26 | 42.14 | 25.24 | 20.01 | 15.2 | 2 | 19.5
2018-03-20 11:00 | 16863.8057 | 1158.65 | 14.5 | 14.5 | 39.54 | 30.32 | 6.45 | 9.8 | 2 | 3.2
2018-03-20 12:00 | 16165.8175 | 1158.65 | 18.25 | 18.76 | 34.83 | 32.34 | 6.88 | 7.41 | 2 | 4.77
2018-03-20 13:00 | 17881.8808 | 1158.65 | 17.91 | 22.93 | 30.86 | 38.45 | 5.25 | 9.28 | 1 | 3.77
2018-03-20 14:00 | 14221.101 | 990.58 | 16.9 | 21.77 | 29.97 | 45 | 14.84 | 10.44 | 1 | 12.32
2018-03-20 15:00 | 13714.7044 | 901.531 | 17.28 | 23.67 | 19.51 | 61.52 | 32.58 | 15 | 1 | 27.58
2018-03-20 16:00 | 14425.8495 | 579.791 | 54.55 | 54.55 | 29.98 | 63.4 | 33.91 | 15 | 1 | 28.53
2018-03-20 17:00 | 13895.2541 | 242.857 | 31.1 | 31.1 | 32.67 | 49.95 | 24.75 | 10.53 | 2 | 18.56
2018-03-20 18:00 | 13407.2058 | 14.2519 | 17.22 | 26.33 | 38.36 | 35 | 13.94 | 9.94 | 2 | 13.94
2018-03-20 19:00 | 13233.8691 | -0.048233 | 19.74 | 20.6 | 42.6 | 33.55 | 34.86 | 14.59 | 2 | 34.68
2018-03-20 20:00 | 11939.5542 | -0.048233 | 22.45 | 22.45 | 37.89 | 32.28 | 13.45 | 8.33 | 2 | 12.33
2018-03-20 21:00 | 11603.2542 | -0.048233 | 20.29 | 20.29 | 37.71 | 28.71 | 6.67 | 1.4 | 10.03 | 6
2018-03-20 22:00 | 11189.0542 | -0.048233 | 19.09 | 20.77 | 30.43 | 21.17 | 20.61 | 0.3 | 12.5 | 13.4
2018-03-20 23:00 | 11923.5591 | -0.048233 | 13.47 | 13.47 | 18 | 18.18 | 6.86 | 0.3 | 10.11 | 5.61
2018-03-21 | 11598.6191 | -0.048233 | 8.82 | 8.82 | 17.47 | 14.52 | 3 | 0.3 | 23.12 | 21.13
2018-03-21 01:00 | 10376.8042 | -0.048233 | 9.18 | 9.18 | 17.61 | 11.73 | 3 | 0.3 | 25 | 2.11
2018-03-21 02:00 | 10424.3042 | -0.048233 | 5.89 | 5.89 | 16.35 | 8.99 | 3 | 0.99 | 12 | 2.11
2018-03-21 03:00 | 10286.5542 | -0.048233 | 7.25 | 7.25 | 15.87 | 10.55 | 3 | 0.99 | 10.53 | 2.11
2018-03-21 04:00 | 10681.7542 | -0.048233 | 9.86 | 9.86 | 17.48 | 13.08 | 3 | 0.99 | 37.99 | 3.05
2018-03-21 05:00 | 11618.4542 | -0.048233 | 12.12 | 14.87 | 19.72 | 17.05 | 4 | 0.99 | 27.33 | 23
2018-03-21 06:00 | 13211.6943 | 4.0466 | 13.93 | 13.93 | 22.9 | 22.04 | 31.23 | 54.3173 | 12.33 | 31.23
2018-03-21 07:00 | 16522.1366 | 127.793 | 17.55 | 17.55 | 22.8 | 22.22 | 31.95 | 53.4573 | 3.5 | 31.94
2018-03-21 08:00 | 17637.0174 | 441.552 | 16.79 | 16.79 | 32.45 | 22.28 | 25.69 | 24.45 | 2.18 | 24.84
2018-03-21 09:00 | 15875.9288 | 763.504 | 166.66 | 19.73 | 31.19 | 24.04 | 18.79 | 17.9 | 2.63 | 18.59
2018-03-21 10:00 | 16911.7955 | 1002.89 | 72.44 | 19.38 | 35 | 25.34 | 12.67 | 12.43 | 3.41 | 12.47
2018-03-21 11:00 | 17067.2519 | 1079.49 | 13.92 | 15.42 | 31.7 | 30.5 | 14.51 | 14.11 | 2 | 14.31
2018-03-21 12:00 | 15274.043 | 955.94 | 14.89 | 19.93 | 30.21 | 32.56 | 12.66 | 12.45 | 2 | 12.45
2018-03-21 13:00 | 15004.6382 | 698.356 | 14.93 | 25.2 | 20.22 | 44.26 | 18.38 | 22.55 | 2 | 11.76
2018-03-21 14:00 | 16505.2345 | 832.772 | 36 | 27.56 | 20 | 50.04 | 22.39 | 21.76 | 2 | 15.81
2018-03-21 15:00 | 14056.5553 | 637.374 | 13.8 | 30.44 | 19.74 | 65.58 | 39.29 | 60.4573 | 2 | 30.65
2018-03-21 16:00 | 13169.3864 | 411.512 | 44.26 | 44.26 | 20.04 | 77.21 | 52.64 | 66.8073 | 2 | 42.71
2018-03-21 17:00 | 14220.2321 | 112.893 | 12.71 | 36.13 | 22.98 | 52.16 | 28.78 | 8.62 | 2 | 19.42
2018-03-21 18:00 | 13906.1698 | 12.2036 | 10.5 | 24.99 | 23.54 | 38.49 | 20.06 | 7.25 | 2 | 16.06
2018-03-21 19:00 | 13847.8791 | -0.048233 | 10.43 | 17.44 | 30.62 | 36.42 | 20 | 17 | 2 | 20
2018-03-21 20:00 | 12397.4542 | -0.048233 | 14.54 | 20.73 | 32.56 | 34.01 | 27.33 | 22.33 | 2 | 27.33
2018-03-21 21:00 | 11893.9542 | -0.048233 | 48.02 | 16.7 | 20.2 | 30.16 | 7.86 | 1 | 10.77 | 11.97
2018-03-21 22:00 | 12707.4241 | -0.048233 | 12.51 | 20.97 | 19.82 | 24.7 | 22.32 | 0.45 | 12.5 | 22.12
2018-03-21 23:00 | 12240.0591 | -0.048233 | 12.43 | 19.17 | 19.7 | 20.64 | 19.74 | 0.45 | 15 | 19.74
2018-03-22 | 11813.8391 | -0.048233 | 7.83 | 17.7 | 4.7 | 18.91 | 25 | 0.45 | 25.72 | 2.01
2018-03-22 01:00 | 10552.5542 | -0.048233 | 5.99 | 17.35 | 8.1 | 18.38 | 25 | 0.45 | 26.39 | 2.01
2018-03-22 02:00 | 10582.0042 | -0.048233 | 3.04 | 13.64 | 4.16 | 17.74 | 28.17 | 1 | 11.96 | 2.01
2018-03-22 03:00 | 11765.3091 | -0.048233 | 5.81 | 13.37 | 4.19 | 18.08 | 25 | 1 | 7 | 1.5
2018-03-22 04:00 | 10889.8042 | -0.048233 | 9.27 | 17.2 | 4.19 | 18.32 | 25.16 | 1 | 38.07 | 2.11
2018-03-22 05:00 | 11921.5042 | -0.048233 | 11.59 | 17.75 | 16.96 | 19.57 | 26.11 | 1 | 26.11 | 26.11
2018-03-22 06:00 | 15168.0029 | 3.2539 | 16.79 | 19.1 | 22.85 | 25.16 | 37.89 | 58.7973 | 14.68 | 37.89
2018-03-22 07:00 | 14315.4044 | 80.8467 | 18.42 | 20.66 | 20.51 | 23.72 | 21.75 | 19.75 | 3.5 | 21.55
2018-03-22 08:00 | 16615.0505 | 392.863 | 14.29 | 20.04 | 28.82 | 24.09 | 21.79 | 19.35 | 3.5 | 20.55
2018-03-22 09:00 | 15319.3105 | 278.59 | 16.3 | 21.2 | 32.46 | 27.13 | 20.27 | 19.37 | 3.5 | 19.37
2018-03-22 10:00 | 15654.2833 | 351.193 | 14.04 | 20.07 | 42.88 | 29.87 | 7.52 | 11.89 | 2 | 4.63
2018-03-22 11:00 | 17316.5569 | 698.798 | 12.61 | 18.36 | 43.37 | 30.39 | 13.4 | 12.5 | 2 | 5.78
2018-03-22 12:00 | 18044.4868 | 413.779 | 12.35 | 25.22 | 36.99 | 36.63 | 17.42 | 17.21 | 2 | 5.32
2018-03-22 13:00 | 17047.7133 | 399.97 | 11.1 | 28.5 | 32.64 | 40.51 | 25.35 | 24.45 | 2 | 12.75
2018-03-22 14:00 | 15843.9404 | 415.832 | 10.32 | 29.43 | 32.21 | 45.08 | 18.82 | 10 | 2 | 4.54
2018-03-22 15:00 | 15484.0884 | 550.861 | 11.08 | 27.15 | 31.38 | 61 | 36.53 | 2.5 | 2 | 27.1
2018-03-22 16:00 | 14514.5402 | 159.858 | 9.79 | 27.37 | 32.65 | 56.71 | 31.16 | 6.25 | 2 | 23.19
2018-03-22 17:00 | 14217.5756 | 74.375 | 9.91 | 25.07 | 33.27 | 36.09 | 32 | 2.5 | 2 | 4
2018-03-22 18:00 | 14168.7921 | 7.1347 | 8.28 | 17.22 | 37.64 | 29.91 | 32 | 9.29 | 2 | 13.26
2018-03-22 19:00 | 12710.0042 | -0.048233 | 8.16 | 15.35 | 45.74 | 29.8 | 30 | 7.25 | 3.5 | 29.99
2018-03-22 20:00 | 12542.8042 | -0.048233 | 21.18 | 21.18 | 40.22 | 30.31 | 33.37 | 7.25 | 2 | 32.07
2018-03-22 21:00 | 12256.8542 | -0.048233 | 10.98 | 21.3 | 38.87 | 24.47 | 7.9 | 1 | 9.16 | 4
2018-03-22 22:00 | 11872.1042 | -0.048233 | 10.33 | 18.58 | 32.37 | 21.71 | 18.26 | 0.45 | 106.0034 | 18.06
2018-03-22 23:00 | 11392.3542 | -0.048233 | 10.46 | 17.88 | 32.29 | 20.61 | 22 | 0.45 | 27 | 17.08
2018-03-23 | 12421.5191 | -0.048233 | 3.5 | 16.83 | 33.28 | 14.65 | 24 | 0.45 | 18 | 4
2018-03-23 01:00 | 10990.5042 | -0.048233 | 3.38 | 15.67 | 31.65 | 10.85 | 24 | 0.45 | 15 | 2.76
2018-03-23 02:00 | 12016.3991 | -0.048233 | -0.44 | 10.53 | 11.75 | 5.54 | 19.11 | 0.66 | 18 | 2.76
2018-03-23 03:00 | 10823.3042 | -0.048233 | -0.94 | 9.65 | 31.86 | 5.56 | 19.11 | 0.66 | 15 | 2.5
2018-03-23 04:00 | 11195.7042 | -0.048233 | 0.65 | 10.46 | 29.68 | 4.69 | 19.11 | 0.66 | 20.06 | 3.48
2018-03-23 05:00 | 12083.9542 | -0.048233 | 2.07 | 12.07 | 32.21 | 11.18 | 24 | 0.94 | 40.9 | 26.78
2018-03-23 06:00 | 13536.0171 | 4.439 | 9.64 | 20.78 | 49.12 | 20.64 | 33.43 | 29.04 | 18.22 | 88.3362
2018-03-23 07:00 | 14386.8978 | 169.103 | 13.05 | 20.64 | 54.43 | 21.73 | 19 | 16.53 | 18.8 | 14.5
2018-03-23 08:00 | 14993.507 | 514.639 | 11.08 | 15.85 | 56.22 | 22.11 | 20 | 14.45 | 14.75 | 14.46
2018-03-23 09:00 | 17776.4493 | 402.715 | 12.34 | 14.62 | 51.13 | 19.66 | 15 | 16.41 | 2.05 | 7.35
2018-03-23 10:00 | 16973.0278 | 826.178 | 13.81 | 13.81 | 52.27 | 21.03 | 22 | 8.86 | 2 | 6.46
2018-03-23 11:00 | 15372.4392 | 998.515 | 12.87 | 12.87 | 50.04 | 21.6 | 25 | 10.81 | 2 | 5.6
2018-03-23 12:00 | 17358.0205 | 1076.1 | 15.54 | 15.54 | 44.95 | 23.64 | 25 | 9.79 | 1 | 5.6
2018-03-23 13:00 | 15949.2175 | 1158.65 | 14.9 | 14.9 | 49.93 | 27.97 | 12.7 | 14.45 | 1 | 10.7
2018-03-23 14:00 | 16113.8379 | 1075.78 | 14.78 | 14.78 | 45.9 | 32.53 | 14.32 | 12.24 | 1 | 13.74
2018-03-23 15:00 | 15287.8404 | 900.844 | 16.22 | 16.22 | 40.65 | 41.56 | 25 | 1.61 | 0.91 | 16.85
2018-03-23 16:00 | 14402.8874 | 583.026 | 19.66 | 19.66 | 48.41 | 39.99 | 25 | 1.45 | 0.61 | 16.51
2018-03-23 17:00 | 12515.2933 | 266.993 | 35.28 | 17.93 | 50.94 | 32.44 | 17.2 | 9.44 | 2 | 13.11
2018-03-23 18:00 | 12114.3667 | 9.965 | 17.9 | 17.9 | 53.41 | 26.56 | 15.72 | 8.02 | 2 | 15.52
2018-03-23 19:00 | 13425.8791 | -0.048233 | 15.6 | 17.5 | 54.74 | 27.31 | 34.12 | 15.22 | 2 | 33.12
2018-03-23 20:00 | 12080.1542 | -0.048233 | 15.68 | 20.77 | 52.17 | 26.51 | 8.98 | 0.97 | 2 | 3.98
2018-03-23 21:00 | 13197.9991 | -0.048233 | 17.7 | 17.7 | 45.53 | 22.54 | 4.89 | 0.97 | 15 | 4.2
2018-03-23 22:00 | 12785.4941 | -0.048233 | 14.1 | 16.39 | 39.55 | 17.98 | 23 | 0.45 | 31.82 | 23.5
2018-03-23 23:00 | 12493.2591 | -0.048233 | 9.39 | 12.76 | 11.5 | 13.15 | 25.11 | 0.45 | 30.69 | 22
2018-03-24 | 11014.2542 | -0.048233 | 9.37 | 11.17 | 33.67 | 12.36 | 4.51 | 0.45 | 14 | 4
2018-03-24 01:00 | 12030.1141 | -0.048233 | -0.01 | 9.73 | 10.33 | 11.52 | 15 | 0.45 | 20 | 2.75
2018-03-24 02:00 | 10826.1542 | -0.048233 | 0.74 | 10.29 | 8.87 | 10.84 | 15 | 0.97 | 15.28 | 2.61
2018-03-24 03:00 | 11944.6591 | -0.048233 | -0.39 | 12.68 | 8.47 | 10.94 | 4 | 0.99 | 14.22 | 2.61
2018-03-24 04:00 | 12524.9091 | -0.048233 | -0.16 | 12.62 | 10.49 | 11.5 | 4.51 | 0.99 | 15.01 | 4
2018-03-24 05:00 | 13628.4391 | -0.048233 | 0 | 13.57 | 34.16 | 13.14 | 7.23 | 0.99 | 30 | 26.35
2018-03-24 06:00 | 13844.7795 | 2.4521 | 4.91 | 16.03 | 41 | 19.74 | 21.33 | 18.55 | 37.64 | 40
2018-03-24 07:00 | 16797.5739 | 105.871 | 13.51 | 17.57 | 43.78 | 20.53 | 14 | 10 | 18 | 15
2018-03-24 08:00 | 17510.5429 | 298.671 | 14.8 | 15.22 | 41.29 | 19.91 | 5.33 | 9.26 | 2.5 | 5.33
2018-03-24 09:00 | 17021.2991 | 763.157 | 11.67 | 21.08 | 42.16 | 21.78 | 5.49 | 8.26 | 2.11 | 5.29
2018-03-24 10:00 | 16750.5739 | 633.183 | 9.65 | 16.01 | 45 | 25.75 | 17 | 8.2 | 2 | 7.09
2018-03-24 11:00 | 17900.9668 | 851.741 | 11.07 | 18.49 | 36.19 | 25.06 | 15 | 8.34 | 2.5 | 9.54
2018-03-24 12:00 | 19119.5171 | 973.765 | 11.84 | 23.33 | 34.46 | 25.72 | 6.82 | 7.45 | 2 | 5.6
2018-03-24 13:00 | 18350.8356 | 722.157 | 13.46 | 35.43 | 32.18 | 29.45 | 25 | 10.61 | 1 | 10.72
2018-03-24 14:00 | 14951.4724 | 914.392 | 13.41 | 34.8 | 30.86 | 36.21 | 18.2 | 16.1 | 1 | 15
2018-03-24 15:00 | 13942.4679 | 693.282 | 35.92 | 35.92 | 16.96 | 42.88 | 22.5 | 20.11 | 1 | 16.36
2018-03-24 16:00 | 14566.7711 | 362.366 | 49.8 | 20.77 | 17.65 | 41.76 | 24.25 | 21.58 | 0.51 | 19.57
2018-03-24 17:00 | 14066.4933 | 148.169 | 16.83 | 20.09 | 18.26 | 31.34 | 21.36 | 21.16 | 2 | 21.36
2018-03-24 18:00 | 12374.1483 | 13.4193 | 16.82 | 18.66 | 34.62 | 27.5 | 21.17 | 20.71 | 2 | 21.07
2018-03-24 19:00 | 13666.4191 | -0.048233 | 14.33 | 14.33 | 41.14 | 27.2 | 29.99 | 23.1 | 2 | 29.63
2018-03-24 20:00 | 12329.0542 | -0.048233 | 20.95 | 20.95 | 38.09 | 27.53 | 20.5 | 18.87 | 18 | 20
2018-03-24 21:00 | 11936.7042 | -0.048233 | 20.11 | 21.07 | 18.21 | 25.21 | 7.91 | 9.28 | 18 | 4
2018-03-24 22:00 | 11750.5042 | -0.048233 | 15.8 | 15.8 | 14.14 | 24.54 | 5.96 | 0.5 | 22 | 5.44
2018-03-24 23:00 | 11446.5042 | -0.048233 | 11.43 | 11.43 | 11.74 | 22.88 | 4.77 | 0.5 | 18 | 3
2018-03-25 | 11209.0042 | -0.048233 | 12.76 | 12.76 | 8.48 | 20.12 | 3 | 0.45 | 9.54 | 2.8
2018-03-25 01:00 | 11072.2042 | -0.048233 | 13.31 | 16.51 | 5.83 | 19.4 | 3 | 0.45 | 11.91 | 1
2018-03-25 02:00 | 12089.1941 | -0.048233 | 11.91 | 16.87 | 5.74 | 18.51 | 3 | 1 | 8.24 | 1
2018-03-25 03:00 | 10777.7042 | -0.048233 | -0.29 | 16.56 | 5.46 | 16.53 | 3 | 1 | 3.77 | 0.01
2018-03-25 04:00 | 10828.0542 | -0.048233 | 1.66 | 16.62 | 5.43 | 18.89 | 3 | 1 | 9.92 | 1
2018-03-25 05:00 | 11075.0542 | -0.048233 | 9.95 | 16.41 | 7.09 | 18.82 | 3.43 | 1 | 15.27 | 15
2018-03-25 06:00 | 11587.8552 | 3.7423 | 10.76 | 16.84 | 13.45 | 22.6 | 25 | 21 | 34.18 | 33
2018-03-25 07:00 | 11790.3567 | 47.9018 | 12.4 | 16.74 | 17.23 | 22.02 | 5 | 11.6 | 2 | 14
2018-03-25 08:00 | 11911.0183 | 104.914 | 12.96 | 17.42 | 33.35 | 24.43 | 5 | 8.86 | 2.5 | 4.79
2018-03-25 09:00 | 13364.5712 | 169.84 | 19.48 | 19.48 | 30.54 | 27.52 | 6.94 | 7.5 | 2.5 | 6.3
2018-03-25 10:00 | 13104.4662 | 220.295 | 15.13 | 19.56 | 18.31 | 30.36 | 7.66 | 7.45 | 2.5 | 4.4
2018-03-25 11:00 | 13368.1054 | 302.19 | 14.38 | 20.18 | 18.12 | 30.97 | 7.16 | 7.5 | 2 | 6.44
2018-03-25 12:00 | 12011.6071 | 319.797 | 13.68 | 22.18 | 18.14 | 33.94 | 7.35 | 8.16 | 2 | 4.84
2018-03-25 13:00 | 12803.7675 | 1158.65 | 13.85 | 24.68 | 18.15 | 41.44 | 18.39 | 11.53 | 2 | 12.23
2018-03-25 14:00 | 12835.3484 | 274.207 | 13.65 | 27.16 | 15.33 | 51.99 | 26.15 | 15.5 | 1 | 19.64
2018-03-25 15:00 | 12763.409 | 217.018 | 13.62 | 36.5 | 15.5 | 65.96 | 38.43 | 16.25 | 0.94 | 27.61
2018-03-25 16:00 | 11565.0055 | 139.69 | 38.93 | 38.93 | 15.95 | 73.86 | 45.98 | 19.93 | 1 | 35.62
2018-03-25 17:00 | 11483.3504 | 65.7373 | 13.77 | 34.16 | 16.23 | 58.93 | 35.68 | 18.63 | 2 | 28.02
2018-03-25 18:00 | 12716.7469 | 10.7885 | 12.48 | 35.52 | 18.1 | 36.65 | 18.45 | 16.25 | 2 | 17.45
2018-03-25 19:00 | 12578.7141 | -0.048233 | 11.94 | 29.17 | 28.86 | 36.02 | 23.6 | 19.2 | 2 | 23.59
2018-03-25 20:00 | 12453.1691 | -0.048233 | 50.21 | 31.19 | 18.03 | 31.47 | 4.44 | 12.35 | 2 | 3.59
2018-03-25 21:00 | 10890.7542 | -0.048233 | 12.46 | 23.15 | 15.07 | 27.56 | 5.91 | 1.37 | 10.75 | 4
2018-03-25 22:00 | 11908.7891 | -0.048233 | 12.11 | 23.05 | 11.77 | 23.76 | 5.32 | 0.5 | 18 | 4.85
2018-03-25 23:00 | 11785.3541 | -0.048233 | 11.59 | 20.13 | 10.23 | 20.85 | 5.38 | 0.5 | 25 | 3.11
2018-03-26 | 11587.0141 | -0.048233 | 10.38 | 18.53 | 11.73 | 18.76 | 4.09 | 0.5 | 15 | 4
2018-03-26 01:00 | 11531.0991 | -0.048233 | 3.85 | 8.49 | 11.64 | 17.34 | 4.05 | 0.5 | 13.3 | 2.5
2018-03-26 02:00 | 10376.8042 | -0.048233 | 0.34 | 9.26 | 11.58 | 13.75 | 4.05 | 1 | 11.39 | 2.5
2018-03-26 03:00 | 10367.3042 | -0.048233 | -0.55 | 9.07 | 11.57 | 10.24 | 3.45 | 1 | 10.98 | 2.61
2018-03-26 04:00 | 11301.1091 | -0.048233 | -0.57 | 7.64 | 11.64 | 11.91 | 4.05 | 1 | 12 | 4
2018-03-26 05:00 | 10238.1042 | -0.048233 | -0.63 | 9.11 | 11.18 | 13.84 | 16.11 | 1 | 23.94 | 17.11
2018-03-26 06:00 | 11587.672 | 4.5753 | -0.21 | 9.74 | 11.7 | 17.26 | 30.92 | 20.5 | 34.07 | 35.92
2018-03-26 07:00 | 10481.0066 | 68.6385 | 11.71 | 13.28 | 12.61 | 17.53 | 8.11 | 11.16 | 3.32 | 11.17
2018-03-26 08:00 | 11605.787 | 129.746 | 12.54 | 15.78 | 14.01 | 19.14 | 7.11 | 7.5 | 2.5 | 5.8
2018-03-26 09:00 | 10741.0677 | 209.387 | 14.71 | 18.4 | 18.05 | 20.47 | 6.21 | 7.5 | 2.04 | 6.21
2018-03-26 10:00 | 10860.8512 | 270.475 | 14.79 | 17.45 | 17.05 | 21.95 | 6.2 | 7.17 | 2 | 6.2
2018-03-26 11:00 | 11006.3846 | 304.668 | 18.45 | 18.45 | 16.57 | 23.15 | 8.05 | 7.45 | 2.11 | 6.64
2018-03-26 12:00 | 12436.4044 | 319.061 | 20.48 | 20.48 | 14.07 | 24.19 | 6.22 | 8.81 | 2 | 4.11
2018-03-26 13:00 | 12500.3985 | 308.719 | 690.4311 | 20.73 | 13.04 | 27.88 | 7.06 | 10.1 | 2.11 | 5.68
2018-03-26 14:00 | 11497.2401 | 271.358 | 17.58 | 23.64 | 12.05 | 31.95 | 7.64 | 1 | 1 | 2.11
2018-03-26 15:00 | 12884.4059 | 214.707 | 18.74 | 25.47 | 11.79 | 41.26 | 18.41 | 1.91 | 1 | 5.32
2018-03-26 16:00 | 11388.1079 | 140.482 | 12.39 | 28.78 | 12.17 | 50.18 | 28.1 | 2 | 1 | 14.41
2018-03-26 17:00 | 12639.2826 | 76.3627 | 17.1 | 24.9 | 14.03 | 39.89 | 22.1 | 2 | 1.49 | 14.86
2018-03-26 18:00 | 12509.7504 | 16.5833 | 15.62 | 23.53 | 18.68 | 31.74 | 15 | 10.25 | 2.5 | 14
2018-03-26 19:00 | 11134.9042 | -0.048233 | 15.28 | 27.45 | 22.26 | 33.02 | 20.5 | 13.25 | 2.5 | 20.5
2018-03-26 20:00 | 12535.4591 | -0.048233 | 82.55 | 82.55 | 19.26 | 33.87 | 27.97 | 10.25 | 2.5 | 27.97
2018-03-26 21:00 | 11276.4542 | -0.048233 | 15.51 | 30.57 | 15.22 | 27.08 | 4.25 | 0.99 | 3.46 | 4.03
2018-03-26 22:00 | 11020.9042 | -0.048233 | 13.09 | 23.31 | 13.06 | 22.4 | 5.14 | 0.6 | 30 | 4.94
2018-03-26 23:00 | 10833.7542 | -0.048233 | 12.05 | 20.39 | 11.7 | 19.76 | 5 | 0.6 | 30 | 3
2018-03-27 | 10725.4542 | -0.048233 | 14.21 | 20.79 | 19.66 | 20.14 | 3.66 | 0.82 | 10.11 | 2.61
2018-03-27 01:00 | 10529.7542 | -0.048233 | 11.4 | 17.12 | 18.14 | 18.55 | 3.59 | 0.82 | 8.57 | 2.25
2018-03-27 02:00 | 10083.2542 | -0.048233 | 11.85 | 17.6 | 16.2 | 18.05 | 3.59 | 0.99 | 9.92 | 2.24
2018-03-27 03:00 | 11103.8241 | -0.048233 | 0 | 16.69 | 13.51 | 17.78 | 3.28 | 0.99 | 8 | 2.5
2018-03-27 04:00 | 10365.4042 | -0.048233 | -0.43 | 10.39 | 15.14 | 18.14 | 3.59 | 0.99 | 8.18 | 3.59
2018-03-27 05:00 | 11497.8042 | -0.048233 | 0 | 15.59 | 14.08 | 21.48 | 16 | 0.99 | 102.7434 | 28.26
2018-03-27 06:00 | 15369.7625 | 4.4953 | 6.48 | 19.25 | 14.43 | 27.36 | 25 | 14.45 | 25 | 28.45
2018-03-27 07:00 | 16407.6975 | 61.3199 | 15.9 | 21.35 | 13.82 | 29.76 | 11.11 | 12 | 10 | 12.7
2018-03-27 08:00 | 14605.7921 | 121.518 | 14.63 | 19.7 | 14.43 | 26.77 | 7 | 13 | 2 | 4.15
2018-03-27 09:00 | 15165.0761 | 183.238 | 12.31 | 20.26 | 16.45 | 27.25 | 6.41 | 15 | 2 | 5.56
2018-03-27 10:00 | 17048.5774 | 228.789 | 104.79 | 23.95 | 16.41 | 29.57 | 5.06 | 10.95 | 2 | 4.85
2018-03-27 11:00 | 15452.4407 | 311.727 | 15.25 | 27.87 | 16.34 | 32.65 | 4.7 | 11.41 | 2 | 4.7
2018-03-27 12:00 | 16826.6308 | 271.243 | 15.38 | 29.56 | 16 | 39.67 | 4.92 | 15 | 2 | 4.92
2018-03-27 13:00 | 16426.9383 | 262.514 | 16.48 | 30.94 | 14.28 | 50.41 | 20.79 | 19.9 | 1.39 | 14.93
2018-03-27 14:00 | 14394.6194 | 237.231 | 73.57 | 73.57 | 12.27 | 69.97 | 32.71 | 17.13 | 1.43 | 25.65
2018-03-27 15:00 | 15244.1075 | 191.391 | 253.7257 | 209.4 | 12.26 | 78.64 | 37.46 | 20.04 | 1 | 28.28
2018-03-27 16:00 | 14638.9933 | 130.823 | 187.43 | 187.43 | 13.57 | 94.55 | 51.92 | 56.1173 | 1 | 41.27
2018-03-27 17:00 | 12846.9301 | 60.0843 | 34.2 | 34.2 | 16.7 | 70.48 | 30.77 | 15 | 2 | 22.32
2018-03-27 18:00 | 12634.7382 | 6.7244 | 31.22 | 31.22 | 18.45 | 43.01 | 17.43 | 6.51 | 2 | 13.69
2018-03-27 19:00 | 12586.5042 | -0.048233 | 21.37 | 29.33 | 22.22 | 38.53 | 20.38 | 7.19 | 2 | 20.37
2018-03-27 20:00 | 13994.5241 | -0.048233 | 1067.1711 | 30.15 | 22.43 | 35.11 | 18.25 | 5.46 | 2 | 17.96
2018-03-27 21:00 | 13667.4741 | -0.048233 | 21.25 | 21.71 | 17.12 | 31.08 | 8.18 | 1.63 | 20 | 3.33
2018-03-27 22:00 | 11888.2542 | -0.048233 | 18.07 | 20.55 | 13.73 | 27.97 | 4 | 0.82 | 16.74 | 4
2018-03-27 23:00 | 11642.2042 | -0.048233 | 14.18 | 19.33 | 12.54 | 23.19 | 4.79 | 0.82 | 277.7434 | 3
2018-03-28 | 11603.2542 | -0.048233 | 13.36 | 15.72 | 11.72 | 20.79 | 3.59 | 0.82 | 8.61 | 3.59
2018-03-28 01:00 | 11500.6542 | -0.048233 | 1.26 | 11.93 | 13.7 | 16.92 | 3.2 | 0.82 | 8.11 | 1.47
2018-03-28 02:00 | 12661.0041 | -0.048233 | -0.18 | 10.77 | 13.75 | 15.05 | 3.25 | 1 | 8 | 1.47
2018-03-28 03:00 | 11295.4542 | -0.048233 | 8.51 | 10.6 | 13.85 | 14.98 | 3.14 | 1 | 8 | 1.54
2018-03-28 04:00 | 12880.4441 | -0.048233 | 0.08 | 15.08 | 13.93 | 16.91 | 3.25 | 1.27 | 10.05 | 2.5
2018-03-28 05:00 | 13958.6541 | -0.048233 | 11.01 | 16.5 | 13.82 | 18.94 | 6.43 | 1.23 | 49.3962 | 13
2018-03-28 06:00 | 14454.9783 | 3.7666 | 12.74 | 19.29 | 17.35 | 23.05 | 18.46 | 16.06 | 137.7434 | 50.77
2018-03-28 07:00 | 16768.9322 | 46.7225 | 16.6 | 20.05 | 32.63 | 22.5 | 8 | 13.82 | 10.8 | 13.83
2018-03-28 08:00 | 15367.4422 | 110.255 | 14.26 | 19.48 | 42 | 22.19 | 7.94 | 10.02 | 2.5 | 7.94
2018-03-28 09:00 | 17663.136 | 173.309 | 15.24 | 19.7 | 44.84 | 23.77 | 7.69 | 9.79 | 2.5 | 11.95
2018-03-28 10:00 | 17081.646 | 222.68 | 15.43 | 17.49 | 45.54 | 26.25 | 6.05 | 9.25 | 2.5 | 5.93
2018-03-28 11:00 | 17560.7894 | 253.298 | 15.87 | 16.82 | 46.14 | 30.47 | 6.44 | 9.49 | 2.5 | 6.44
2018-03-28 12:00 | 17217.4172 | 259.597 | 15.04 | 20.95 | 39.91 | 32.65 | 5.89 | 14.24 | 2.5 | 5.28
2018-03-28 13:00 | 17036.0602 | 589.695 | 15.61 | 21.16 | 36.34 | 39.6 | 6.6 | 12.59 | 2 | 6.53
2018-03-28 14:00 | 15856.9963 | 879.575 | 15.19 | 26.11 | 32.57 | 50.3 | 3.65 | 1.06 | 2 | 3
2018-03-28 15:00 | 14515.0728 | 459.024 | 15.8 | 28.11 | 18.09 | 57.52 | 19.16 | 7.68 | 1 | 3.23
2018-03-28 16:00 | 13805.7106 | 281.327 | 15.82 | 32.25 | 35.06 | 63.32 | 22.53 | 10.11 | 1 | 13.97
2018-03-28 17:00 | 13351.8952 | 97.6265 | 15.22 | 24.99 | 39.55 | 53.57 | 16.1 | 9.39 | 2 | 4
2018-03-28 18:00 | 12867.1175 | 15.3342 | 14.09 | 21.45 | 45.26 | 40.65 | 4.49 | 8.1 | 2.5 | 4.29
2018-03-28 19:00 | 14379.5991 | -0.048233 | 13.13 | 20.85 | 45.95 | 42.5 | 17.02 | 10.66 | 2.5 | 14.22
2018-03-28 20:00 | 12965.5542 | -0.048233 | 15.85 | 23.51 | 45.38 | 38.64 | 5.14 | 10.36 | 2.5 | 4.48
2018-03-28 21:00 | 12693.8542 | -0.048233 | 13.82 | 23.41 | 43.01 | 32.94 | 3.25 | 1.8 | 32 | 3
2018-03-28 22:00 | 12208.4042 | -0.048233 | 48.91 | 48.91 | 35.53 | 28.87 | 8 | 0.82 | 18.86 | 17.5
2018-03-28 23:00 | 13219.0991 | -0.048233 | 9.61 | 20.48 | 12.81 | 24.05 | 17 | 0.82 | 25 | 3.07
2018-03-29 | 13000.7141 | -0.048233 | 1.35 | 20.47 | 12.74 | 23.36 | 16.11 | 0.97 | 8 | 2.61
2018-03-29 01:00 | 12794.9891 | -0.048233 | -0.57 | 19.03 | 13.11 | 21.25 | 5 | 0.97 | 14.32 | 2.51
2018-03-29 02:00 | 11466.4542 | -0.048233 | -0.79 | 15.62 | 11.17 | 18.47 | 4.25 | 1 | 11.28 | 2.43
2018-03-29 03:00 | 11292.6042 | -0.048233 | -1.04 | 15.23 | 10.8 | 18.44 | 4 | 1 | 10.96 | 2.11
2018-03-29 04:00 | 11652.6542 | -0.048233 | -0.75 | 16.53 | 13.17 | 19.52 | 5 | 1 | 15.72 | 4
2018-03-29 05:00 | 12549.4542 | -0.048233 | 0.01 | 14.05 | 16.6 | 20.49 | 30.14 | 0.99 | 52.0662 | 30.9
2018-03-29 06:00 | 14070.5499 | 3.1052 | 7.27 | 26.7 | 15.53 | 26.26 | 19.11 | 14.81 | 57.6962 | 49.52
2018-03-29 07:00 | 16424.3744 | 43.1274 | 16.29 | 28.82 | 32.83 | 26.17 | 6 | 12 | 10 | 11.9
2018-03-29 08:00 | 16741.7433 | 100.951 | 14.78 | 20.29 | 36.97 | 23 | 6 | 12.5 | 2.5 | 4
2018-03-29 09:00 | 15292.8226 | 152.708 | 14.49 | 29.47 | 38.82 | 23.43 | 5.71 | 12 | 2.25 | 5.71
2018-03-29 10:00 | 16961.6275 | 192.372 | 14.55 | 18.36 | 37.01 | 26.48 | 5.06 | 8.61 | 2.22 | 5
2018-03-29 11:00 | 16758.1876 | 589.538 | 17.23 | 20.78 | 37.25 | 28.56 | 5.64 | 10.88 | 2.11 | 5.09
2018-03-29 12:00 | 18234.2507 | 1158.65 | 15.26 | 18.26 | 32.9 | 30.74 | 6.04 | 8.68 | 1 | 5.09
2018-03-29 13:00 | 14572.9743 | 260.973 | 15.42 | 20.92 | 18.67 | 41.28 | 7.87 | 13.31 | 0.61 | 11.29
2018-03-29 14:00 | 13774.2286 | 280.188 | 13.52 | 21.94 | 16.89 | 50.21 | 3.6 | 1.43 | 0.48 | 3.01
2018-03-29 15:00 | 13101.0994 | 188.631 | 12.46 | 23.53 | 17.16 | 57.47 | 20.46 | 8.71 | 0.25 | 13.26
2018-03-29 16:00 | 14093.9433 | 128.188 | 12.02 | 25.28 | 16.82 | 59.02 | 24.91 | 12.05 | 0.25 | 15.7
2018-03-29 17:00 | 13869.1734 | 89.1359 | 11.04 | 26.94 | 18.55 | 38.69 | 20.18 | 12.08 | 1.59 | 20.18
2018-03-29 18:00 | 12342.1352 | 6.7213 | 10.85 | 37.58 | 33.07 | 27.77 | 20.4 | 12.39 | 2 | 20.4
2018-03-29 19:00 | 12134.3042 | -0.048233 | 9.91 | 26.28 | 41.74 | 30.32 | 21.49 | 15.09 | 1 | 21.49
2018-03-29 20:00 | 13429.0441 | -0.048233 | 653.5111 | 385.9 | 37.44 | 31 | 18.09 | 10 | 1 | 18.09
2018-03-29 21:00 | 13124.1491 | -0.048233 | 12.55 | 25.37 | 18.56 | 26.77 | 4.24 | 2 | 9.19 | 4
2018-03-29 22:00 | 11417.0542 | -0.048233 | 10.74 | 21.22 | 15.53 | 23.93 | 7.11 | 0.97 | 9.74 | 3.01
2018-03-29 23:00 | 12121.8991 | -0.048233 | 7.6 | 20.38 | 14.44 | 21.35 | 4.83 | 0.97 | 22.82 | 4.82
2018-03-30 | 12078.6441 | -0.048233 | 7.21 | 21.18 | 15.42 | 21.51 | 3.7 | 0.66 | 9.61 | 2.61
2018-03-30 01:00 | 10615.2542 | -0.048233 | 1.54 | 18.82 | 15.24 | 19.08 | 3.11 | 0.66 | 8 | 2.8
2018-03-30 02:00 | 11583.8491 | -0.048233 | 6.4 | 13.9 | 12.9 | 17.51 | 3.5 | 0.99 | 3.5 | 2.8
2018-03-30 03:00 | 11683.0191 | -0.048233 | 4.15 | 16.45 | 12.92 | 15.46 | 3.01 | 0.99 | 3.5 | 2.65
2018-03-30 04:00 | 11622.8841 | -0.048233 | 7.14 | 15.36 | 15.46 | 16.23 | 3.7 | 0.99 | 8 | 3.01
2018-03-30 05:00 | 12212.6291 | -0.048233 | 13.08 | 15.5 | 18.76 | 18.47 | 7 | 0.99 | 25 | 25
2018-03-30 06:00 | 13743.2117 | 3.741 | 13.21 | 17.53 | 36.4 | 21.23 | 35.58 | 63.3073 | 25 | 40
2018-03-30 07:00 | 12891.4287 | 135.925 | 15.77 | 18.56 | 39.33 | 21.44 | 6 | 12 | 2.5 | 6
2018-03-30 08:00 | 14334.9908 | 155.669 | 15.81 | 16.31 | 38.86 | 21.9 | 5.11 | 12 | 2.28 | 5.11
2018-03-30 09:00 | 15029.2029 | 228.69 | 16.32 | 18.67 | 36.04 | 21.78 | 3.5 | 12 | 2.11 | 3.58
2018-03-30 10:00 | 16879.7679 | 1141.78 | 15.77 | 19.06 | 34.95 | 23.12 | 7 | 10.15 | 2 | 6.63
2018-03-30 11:00 | 14441.8697 | 325.976 | 17.48 | 19.02 | 35.5 | 24.61 | 5.88 | 12 | 2.03 | 5.88
2018-03-30 12:00 | 15645.1647 | 1112.54 | 19.79 | 19.79 | 17.48 | 26.6 | 7.64 | 11.01 | 2 | 10.98
2018-03-30 13:00 | 15298.2554 | 862.716 | 18.31 | 19.96 | 16.25 | 27.67 | 6.12 | 10.25 | 1 | 3.91
2018-03-30 14:00 | 14660.2346 | 816.957 | 17.08 | 21.48 | 15.14 | 32.8 | 5.61 | 10 | 1 | 3.91
2018-03-30 15:00 | 13207.1299 | 869.242 | 73.31 | 22.67 | 14.89 | 44.55 | 17.52 | 10.28 | 0.96 | 3.62
2018-03-30 16:00 | 11891.8625 | 342.75 | 34.08 | 23.23 | 15.92 | 51.01 | 23.05 | 15.7 | 0.55 | 23.05
2018-03-30 17:00 | 12705.2337 | 83.8755 | 43.73 | 31.84 | 16.89 | 42.02 | 23.56 | 14.88 | 2 | 23.56
2018-03-30 18:00 | 11343.6959 | 9.7325 | 15.89 | 29.39 | 37.63 | 35.42 | 16.56 | 10.67 | 2.04 | 16.56
2018-03-30 19:00 | 11303.0542 | -0.048233 | 16.03 | 27.8 | 37.89 | 35.28 | 21.97 | 11.3 | 2 | 21.97
2018-03-30 20:00 | 12580.8241 | -0.048233 | 58.48 | 36.22 | 31.85 | 33.37 | 7.38 | 10 | 2 | 4.99
2018-03-30 21:00 | 11018.0542 | -0.048233 | 16.58 | 23.14 | 17.64 | 26.54 | 3.5 | 2 | 3.5 | 2.71
2018-03-30 22:00 | 11903.5141 | -0.048233 | 14.47 | 19.49 | 14.19 | 22.33 | 4.64 | 0.66 | 12 | 4.64
2018-03-30 23:00 | 10513.6042 | -0.048233 | 13.6 | 17.88 | 14.75 | 20.45 | 4 | 0.66 | 8.11 | 3.11
2018-03-31 | 11487.8441 | -0.048233 | 7.94 | 7.94 | 12.6 | 15.48 | 3.59 | 0.61 | 8 | 3.52
2018-03-31 01:00 | 10260.9042 | -0.048233 | 10.69 | 10.69 | 11.73 | 11.64 | 3.01 | 0.61 | 8.61 | 2.11
2018-03-31 02:00 | 11311.6591 | -0.048233 | 3.87 | 8.33 | 11.25 | 9.64 | 3.01 | 0.99 | 10.1 | 2.11
2018-03-31 03:00 | 10122.2042 | -0.048233 | 9.87 | 10.72 | 11.73 | 9.24 | 3.01 | 0.99 | 3.5 | 2.11
2018-03-31 04:00 | 11601.7841 | -0.048233 | 11.14 | 12.08 | 11.89 | 10.53 | 3.01 | 0.99 | 10.53 | 2.84
2018-03-31 05:00 | 12576.6041 | -0.048233 | 12.22 | 13.78 | 13.33 | 16.5 | 5 | 0.99 | 30 | 15
2018-03-31 06:00 | 14244.2381 | 5.6475 | 13.81 | 14.73 | 37.2 | 21.79 | 29.93 | 12 | 8.61 | 29.93
2018-03-31 07:00 | 15164.9401 | 72.3508 | 15.9 | 18.96 | 34.14 | 21.45 | 6.51 | 10 | 1.61 | 6.51
2018-03-31 08:00 | 14476.2463 | 159.154 | 15.23 | 18.28 | 28.25 | 21.08 | 4.34 | 8.34 | 1 | 4.34
2018-03-31 09:00 | 14164.0601 | 233.537 | 15.83 | 19.78 | 29.23 | 22.61 | 7.31 | 7.5 | 2.5 | 4.91
2018-03-31 10:00 | 14476.2729 | 289.182 | 16.71 | 19.96 | 31.49 | 23.35 | 5.17 | 8.81 | 2.5 | 5.3
2018-03-31 11:00 | 14485.4832 | 319.877 | 19.99 | 19.99 | 31.46 | 24.93 | 5 | 10 | 2.5 | 4.94
2018-03-31 12:00 | 14590.7887 | 333.725 | 36.42 | 20.37 | 24.3 | 26.87 | 8 | 11.97 | 2.11 | 12.01
2018-03-31 13:00 | 14521.7997 | 325.105 | 79.24 | 19.77 | 22.88 | 31.46 | 13.9 | 13.86 | 2 | 13.9
2018-03-31 14:00 | 14998.8274 | 291.898 | 1041.4111 | 21.32 | 16.48 | 34.19 | 15.23 | 10.73 | 2.5 | 13.93
2018-03-31 15:00 | 12747.5408 | 237.464 | 328.2757 | 21.77 | 15.23 | 47.83 | 23.61 | 12.56 | 2 | 18.08
2018-03-31 16:00 | 13891.1365 | 166.954 | 1355.6511 | 28.83 | 16.41 | 48.99 | 26.24 | 15.07 | 2 | 24.24
2018-03-31 17:00 | 12309.188 | 102.04 | 107.52 | 26.61 | 23.48 | 34.68 | 22.9 | 13.08 | 2 | 21.9
2018-03-31 18:00 | 13675.5375 | 12.5948 | 20.24 | 20.24 | 24.13 | 26.77 | 19.47 | 11.25 | 12.7 | 18.45
2018-03-31 19:00 | 13465.9691 | -0.048233 | 16.46 | 16.46 | 36.81 | 25.78 | 22.84 | 11.79 | 2.5 | 21.84
2018-03-31 20:00 | 12090.6042 | -0.048233 | 18.56 | 18.56 | 33.55 | 27.94 | 14 | 11.25 | 2.5 | 14
2018-03-31 21:00 | 13177.9541 | -0.048233 | 15 | 15 | 16.46 | 24.57 | 6.62 | 2 | 3.5 | 5.65
2018-03-31 22:00 | 11408.5042 | -0.048233 | 14.28 | 14.28 | 11.06 | 20.34 | 4.82 | 0.61 | 14.49 | 4.48
2018-03-31 23:00 | 11103.5542 | -0.048233 | 13.13 | 13.13 | 12.79 | 18.71 | 3.01 | 0.61 | 2.53 | 3
2018-04-01 | 12183.0891 | -0.048233 | 13.46 | 13.46 | 11.76 | 14.86 | 5 | 0.01 | 35 | 2.61
2018-04-01 01:00 | 11924.6141 | -0.048233 | 11.16 | 11.16 | 10.99 | 13.73 | 5 | 0.01 | 12.91 | 1.6
2018-04-01 02:00 | 10639.0042 | -0.048233 | 6.96 | 6.96 | 7.96 | 14.07 | 3.55 | 1.5 | 14.43 | 1
2018-04-01 03:00 | 10541.1542 | -0.048233 | 13.32 | 15.71 | 7.05 | 14.84 | 3.55 | 1.5 | 10.11 | 1.31
2018-04-01 04:00 | 11853.9291 | -0.048233 | 12.28 | 17.65 | 9.2 | 14.35 | 5 | 1.5 | 11.06 | 1.76
2018-04-01 05:00 | 12034.3341 | -0.048233 | 12.21 | 17.87 | 11.93 | 16.56 | 15 | 2 | 25 | 16
2018-04-01 06:00 | 12531.7623 | 3.4477 | 13.49 | 17.6 | 14.33 | 18.86 | 34.34 | 10.5 | 19.64 | 34.34
2018-04-01 07:00 | 11690.8083 | 226.114 | 15.75 | 17.3 | 33.31 | 18.96 | 6 | 8.61 | 2.11 | 3.25
2018-04-01 08:00 | 14407.5948 | 527.488 | 15.65 | 18.35 | 31.72 | 21.37 | 5.26 | 10.24 | 2.7 | 3.92
2018-04-01 09:00 | 14579.2982 | 825.24 | 15.28 | 18.5 | 30.11 | 22.84 | 5.79 | 8.51 | 2.92 | 2.61
2018-04-01 10:00 | 12588.564 | 1050.12 | 15.47 | 18.54 | 27.94 | 23.96 | 5 | 0.99 | 1.69 | 3
2018-04-01 11:00 | 12681.2175 | 1158.65 | 14.5 | 19.05 | 23.74 | 26.68 | 5 | 0.99 | 0.36 | 3
2018-04-01 12:00 | 14087.0457 | 1158.65 | 13.52 | 19.71 | 23.45 | 31.44 | 5 | 0.99 | 1 | 3
2018-04-01 13:00 | 13785.3157 | 1158.65 | 13.43 | 19.9 | 17.62 | 36.9 | 5 | 0.99 | 1 | 3.5
2018-04-01 14:00 | 12143.185 | 1082.3 | 13.54 | 25.52 | 17.5 | 47.8 | 20 | 1.49 | 2 | 3
2018-04-01 15:00 | 12018.9668 | 876.544 | 11.41 | 28.43 | 17.09 | 51.78 | 27.46 | 10.5 | 1 | 3
2018-04-01 16:00 | 12973.1757 | 587.849 | 12.2 | 27.13 | 16.47 | 52.6 | 33 | 11.25 | 2 | 18.08
2018-04-01 17:00 | 11444.1037 | 247.425 | 12.73 | 21.09 | 15.36 | 37.91 | 29.63 | 1 | 2.5 | 18.73
2018-04-01 18:00 | 11186.1534 | 14.8983 | 12.34 | 18.6 | 15.41 | 28.09 | 29 | 1 | 15.83 | 28
2018-04-01 19:00 | 12187.3091 | -0.048233 | 11.79 | 17.77 | 30.54 | 27.1 | 23.11 | 1.01 | 3.5 | 18.1
2018-04-01 20:00 | 11034.2042 | -0.048233 | 14.33 | 18.85 | 22.47 | 29.12 | 16.93 | 1.02 | 3 | 16.93
2018-04-01 21:00 | 12155.6591 | -0.048233 | 13.64 | 19.33 | 15 | 24.86 | 5 | 0.99 | 8.49 | 3.25
2018-04-01 22:00 | 11937.2741 | -0.048233 | 13.15 | 18.33 | 13.51 | 24.31 | 19.61 | 0.01 | 25 | 12
2018-04-01 23:00 | 10582.0042 | -0.048233 | 53.9 | 15.83 | 12.88 | 22.9 | 8.11 | 0.01 | 13.69 | 11.43
2018-04-02 | 10534.5042 | -0.048233 | 12.13 | 16.25 | 13.67 | 24.14 | 7 | 0.01 | 25 | 12.29
2018-04-02 01:00 | 10468.0042 | -0.048233 | 9.77 | 9.77 | 10.74 | 20.07 | 4 | 0.01 | 8 | 2.61
2018-04-02 02:00 | 10345.4542 | -0.048233 | 11.99 | 14.31 | 9.91 | 18.56 | 4 | 2 | 8 | 2.11
2018-04-02 03:00 | 11457.2491 | -0.048233 | 12.05 | 17.77 | 9.92 | 19.59 | 4.46 | 2 | 7.6 | 2.2
2018-04-02 04:00 | 11503.6691 | -0.048233 | 12.42 | 18.07 | 10.59 | 19.79 | 5.7 | 2 | 8.29 | 2.81
2018-04-02 05:00 | 10484.1542 | -0.048233 | 12.53 | 18.19 | 10.78 | 21.35 | 18 | 2 | 21.68 | 18
2018-04-02 06:00 | 10483.374 | 2.1305 | 11.69 | 19.19 | 10.86 | 22.07 | 36.93 | 11 | 25 | 36.93
2018-04-02 07:00 | 11912.5713 | 91.5368 | 13.43 | 19.36 | 10.69 | 21.59 | 8.89 | 8.69 | 2.5 | 5.43
2018-04-02 08:00 | 10871.7544 | 114.952 | 12.76 | 18.61 | 15.78 | 22.73 | 15 | 9.79 | 9.6 | 10.75
2018-04-02 09:00 | 11145.0542 | 216.636 | 17.81 | 18.97 | 19.17 | 25.63 | 19.02 | 12.32 | 2.5 | 13.22
2018-04-02 10:00 | 12976.3966 | 638.902 | 18.23 | 20.67 | 18.93 | 28.76 | 6.64 | 0.99 | 1 | 5.94
2018-04-02 11:00 | 12112.1105 | 1108.59 | 16.1 | 22.52 | 18.6 | 29.86 | 7.05 | 0.99 | 1 | 5.01
2018-04-02 12:00 | 13294.7407 | 1158.65 | 15.65 | 32.82 | 17.82 | 27.96 | 6.61 | 0.99 | 1 | 4.5
2018-04-02 13:00 | 13572.2057 | 1158.65 | 41.57 | 41.57 | 16.63 | 32 | 8.38 | 0.99 | 2.31 | 13.04
2018-04-02 14:00 | 12117.4875 | 1025.25 | 15.48 | 30.98 | 16.56 | 34.36 | 16.33 | 11.31 | 2 | 3
2018-04-02 15:00 | 12071.2282 | 780.556 | 16.05 | 28.85 | 16.51 | 38.91 | 22 | 17.14 | 2 | 21.34
2018-04-02 16:00 | 13209.2741 | 533.639 | 16.05 | 31 | 18.01 | 38.76 | 26.15 | 20.44 | 2 | 26.04
2018-04-02 17:00 | 13101.2812 | 239.276 | 39.55 | 39.55 | 17.84 | 34.56 | 19.22 | 11.25 | 2 | 19.22
2018-04-02 18:00 | 12865.0649 | 13.3743 | 163.91 | 163.91 | 19.23 | 32.63 | 18.32 | 11.12 | 10 | 18.32
2018-04-02 19:00 | 12835.0791 | -0.048233 | 16.15 | 32.93 | 25.54 | 36.63 | 18 | 11.25 | 8.61 | 17.05
2018-04-02 20:00 | 11441.7542 | -0.048233 | 1022.9611 | 755.35 | 19.37 | 45.58 | 26.29 | 11.25 | 2.61 | 21.41
2018-04-02 21:00 | 10742.5542 | -0.048233 | 16.76 | 29.88 | 19.08 | 28.78 | 8.59 | 0.99 | 13.83 | 10.4
2018-04-02 22:00 | 10306.5042 | -0.048233 | 14.82 | 24.36 | 16.58 | 25.46 | 15.02 | 0.01 | 30 | 15.02
2018-04-02 23:00 | 9974.9542 | -0.048233 | 12.89 | 19.85 | 15.81 | 22.96 | 17.95 | 0.01 | 30 | 17.75
2018-04-03 | 10879.1091 | -0.048233 | 11.65 | 19.61 | 15.68 | 22.33 | 4.29 | 0.01 | 25 | 4.29
2018-04-03 01:00 | 10630.1291 | -0.048233 | 12.01 | 18.79 | 15.48 | 19.81 | 3.95 | 0.01 | 8 | 3.42
2018-04-03 02:00 | 9480.9542 | -0.048233 | 11.06 | 17.74 | 15.46 | 17.67 | 3.5 | 7.5 | 4.12 | 1.68
2018-04-03 03:00 | 9435.3542 | -0.048233 | 9.6 | 17.52 | 14 | 16.19 | 3.5 | 7.5 | 3.5 | 1.76
2018-04-03 04:00 | 10807.3691 | -0.048233 | 10.83 | 17.72 | 14.05 | 17.36 | 3.56 | 1.95 | 8.83 | 2.61
2018-04-03 05:00 | 10422.4042 | -0.048233 | 11.19 | 17.9 | 14.98 | 20.62 | 25 | 7.5 | 14.18 | 25
2018-04-03 06:00 | 11703.8803 | 4.874 | 10.39 | 38.01 | 15.68 | 24.45 | 27.01 | 25.01 | 37.47 | 38
2018-04-03 07:00 | 12579.3832 | 230.456 | 11.95 | 19.93 | 16.66 | 26.87 | 7.61 | 7.4 | 3.46 | 2.75
2018-04-03 08:00 | 14799.3216 | 526.793 | 12.27 | 19.37 | 17.05 | 27.94 | 7.61 | 7.4 | 14.11 | 11
2018-04-03 09:00 | 15604.3657 | 842.868 | 14.28 | 20.04 | 22.48 | 27.88 | 15.01 | 14.8 | 15 | 5.12
2018-04-03 10:00 | 15917.6184 | 1047.79 | 14.63 | 22.67 | 22.1 | 30.69 | 7.1 | 1.45 | 2 | 3.1
2018-04-03 11:00 | 14436.8175 | 1158.65 | 12.4 | 21.08 | 22.27 | 33.65 | 5.97 | 1.38 | 1.21 | 4.41
2018-04-03 12:00 | 17072.6957 | 1158.65 | 12.18 | 21.84 | 29.13 | 40.97 | 4.53 | 1.42 | 1.21 | 3.1
2018-04-03 13:00 | 16410.1557 | 1158.65 | 12.14 | 29.22 | 19.52 | 44.81 | 3.47 | 1.22 | 12.92 | 3
2018-04-03 14:00 | 14131.5825 | 1036.35 | 12.31 | 29.72 | 19.55 | 60.13 | 18.81 | 1.34 | 2.11 | 3
2018-04-03 15:00 | 13632.6349 | 845.142 | 12.58 | 35.55 | 18.79 | 93.5 | 39.51 | 12.58 | 1.3 | 23.11
2018-04-03 16:00 | 12937.8324 | 565.771 | 250.9657 | 206.64 | 18.98 | 119.88 | 90.0941 | 56.5173 | 2.11 | 44.44
2018-04-03 17:00 | 12278.883 | 243.14 | 137.51 | 137.51 | 21.31 | 101.66 | 49.54 | 25.59 | 2.61 | 36.33
2018-04-03 18:00 | 11990.0368 | 14.0914 | 47.65 | 47.65 | 21.76 | 46.05 | 19.95 | 10.95 | 15 | 19.95
2018-04-03 19:00 | 11932.9042 | -0.048233 | 16.13 | 31.65 | 30.1 | 42.82 | 18 | 7.39 | 15 | 16.39
2018-04-03 20:00 | 13333.0391 | -0.048233 | 30.68 | 29.69 | 30.08 | 38.13 | 15.82 | 2 | 15 | 15.81
2018-04-03 21:00 | 11799.9042 | -0.048233 | 15.99 | 23.17 | 21.52 | 30.45 | 7 | 1.24 | 15 | 3.19
2018-04-03 22:00 | 11345.8042 | -0.048233 | 13.7 | 21.44 | 19.63 | 30.13 | 19.24 | 0.25 | 24.78 | 19.24
2018-04-03 23:00 | 12220.0141 | -0.048233 | 12 | 20.16 | 16.88 | 25.9 | 21.55 | 0.01 | 25.99 | 21.55
2018-04-04 | 11860.2591 | -0.048233 | -0.36 | 17.9 | 17.15 | 19.73 | 30.01 | 0.01 | 25 | 33.01
2018-04-04 01:00 | 10557.3042 | -0.048233 | -0.31 | 8.96 | 17.82 | 15.77 | 25.01 | 0.01 | 18.64 | 3.56
2018-04-04 02:00 | 11527.9341 | -0.048233 | -0.44 | 8.62 | 14.88 | 12.8 | 25.01 | 1.95 | 14.09 | 2.76
2018-04-04 03:00 | 11383.3991 | -0.048233 | -0.02 | 10.11 | 14.7 | 12.56 | 25.01 | 1.69 | 10.53 | 2.76
2018-04-04 04:00 | 10492.7042 | -0.048233 | 3.1 | 14.71 | 14.88 | 15.4 | 25.01 | 1.64 | 9.04 | 5.5
2018-04-04 05:00 | 11381.9042 | -0.048233 | 6.87 | 17.82 | 16.87 | 19.19 | 26 | 1.25 | 22 | 25
2018-04-04 06:00 | 13047.5854 | 6.3004 | 5.93 | 20.13 | 17.19 | 25.13 | 97.4041 | 24.34 | 57.6962 | 91.1362
2018-04-04 07:00 | 14081.8253 | 240.974 | 12.84 | 22.06 | 22.39 | 27.2 | 21.07 | 7.5 | 10.12 | 6.5
2018-04-04 08:00 | 16300.6235 | 564.828 | 12.51 | 20.87 | 22.33 | 28.6 | 21.84 | 9 | 15.53 | 21.04
2018-04-04 09:00 | 15577.1975 | 880.05 | 15.9 | 22.55 | 22.87 | 28.35 | 16.2 | 10.19 | 9.32 | 6.7
2018-04-04 10:00 | 15923.1305 | 1092.19 | 15.79 | 20.67 | 23.03 | 29.35 | 8.08 | 0.99 | 1 | 7.88
2018-04-04 11:00 | 15679.4175 | 1158.65 | 15.2 | 20.49 | 23.11 | 39.5 | 94.8141 | 1 | 1 | 12.79
2018-04-04 12:00 | 17685.6508 | 1158.65 | 15.44 | 20.71 | 22.48 | 38.02 | 9.11 | 0.99 | 1 | 9.8
2018-04-04 13:00 | 17897.7058 | 1158.65 | 15.99 | 23.62 | 21.96 | 50.22 | 17.93 | 1 | 1 | 12.93
2018-04-04 14:00 | 15413.6645 | 1113.91 | 18.25 | 31.4 | 22.43 | 59.29 | 18.97 | 1 | 1 | 11.35
2018-04-04 15:00 | 14425.0042 | 888.215 | 308.9557 | 264.63 | 19.33 | 83.13 | 33.94 | 18.59 | 1 | 26.77
2018-04-04 16:00 | 15439.9978 | 599.069 | 398.7657 | 354.44 | 19.31 | 81.27 | 34.82 | 27.27 | 2.11 | 27.27
2018-04-04 17:00 | 14782.6157 | 249.958 | 83.05 | 83.05 | 22.54 | 61.94 | 27.83 | 21.21 | 2.11 | 21.52
2018-04-04 18:00 | 14413.6554 | 16.2326 | 41.18 | 41.18 | 23.83 | 39.65 | 19 | 6.25 | 15 | 19
2018-04-04 19:00 | 12841.1042 | -0.048233 | 18.65 | 28.89 | 31.72 | 37.8 | 15.25 | 6.25 | 11.49 | 3.07
2018-04-04 20:00 | 12995.9542 | -0.048233 | 17.54 | 24.06 | 23.84 | 39.3 | 19 | 8.09 | 9 | 19
2018-04-04 21:00 | 14040.9441 | -0.048233 | 14.44 | 22.68 | 21.76 | 29.55 | 18.66 | 1.82 | 15 | 18.66
2018-04-04 22:00 | 13701.2341 | -0.048233 | 12.72 | 21.17 | 20.54 | 26.31 | 32.84 | 0.01 | 33.86 | 32.84
2018-04-04 23:00 | 12103.9042 | -0.048233 | 8.08 | 19.76 | 20.32 | 22.84 | 20.01 | 0.01 | 25.35 | 20.01
2018-04-05 | 13120.9841 | -0.048233 | 1039.7911 | 772.18 | 17.56 | 19.36 | 23.17 | 0.01 | 30 | 23.17
2018-04-05 01:00 | 11452.2042 | -0.048233 | 9.73 | 19.49 | 16.99 | 18.62 | 26 | 0.01 | 16.26 | 19.47
2018-04-05 02:00 | 12578.7141 | -0.048233 | 7.86 | 20.94 | 16.43 | 16.4 | 26 | 1.95 | 18.38 | 2.61
2018-04-05 03:00 | 12563.9441 | -0.048233 | 5.17 | 21.76 | 16.11 | 14.6 | 26 | 1.95 | 12.7 | 5.5
2018-04-05 04:00 | 12838.2441 | -0.048233 | 7.4 | 21.73 | 16.2 | 14.46 | 24.43 | 1.95 | 9.74 | 19.11
2018-04-05 05:00 | 13777.1941 | -0.048233 | 10.84 | 19.22 | 16.52 | 17.85 | 27.72 | 1.25 | 93.6034 | 50
2018-04-05 06:00 | 13384.8485 | 7.3142 | 714.2411 | 446.63 | 31.53 | 24.22 | 90.5141 | 20.5 | 27.21 | 89.6162
2018-04-05 07:00 | 15164.2345 | 245.682 | 11.88 | 21.14 | 32.63 | 21.7 | 7.5 | 7.5 | 3.5 | 6.5
2018-04-05 08:00 | 13911.326 | 553.501 | 11.23 | 19.35 | 33.5 | 22.15 | 22.06 | 10.23 | 14.3 | 12.72
2018-04-05 09:00 | 15520.0892 | 841.985 | 12.25 | 18.95 | 30.49 | 22.53 | 22.69 | 9 | 11.49 | 9.62
2018-04-05 10:00 | 15256.5554 | 1045.19 | 12.3 | 18.48 | 31.66 | 23.45 | 50 | 0.99 | 2.5 | 3
2018-04-05 11:00 | 13677.7675 | 1158.65 | 13.12 | 17.22 | 25 | 24.79 | 5.01 | 1 | 2 | 3
2018-04-05 12:00 | 14248.7175 | 1158.65 | 12.24 | 17.1 | 23.06 | 26.05 | 7.31 | 1 | 2.5 | 3
2018-04-05 13:00 | 16080.9957 | 1158.65 | 12.69 | 19.28 | 18.3 | 28.44 | 7.97 | 1 | 2.5 | 3.6
2018-04-05 14:00 | 12765.8938 | 995.783 | 13.78 | 19.43 | 18.24 | 29.47 | 8.08 | 1 | 2 | 3.1
2018-04-05 15:00 | 12159.2656 | 752.227 | 13.81 | 19.8 | 18.11 | 32.09 | 14.82 | 2 | 2.11 | 4.79
2018-04-05 16:00 | 12990.0167 | 534.812 | 18.94 | 20.7 | 18.24 | 31.76 | 8.26 | 1.52 | 2.11 | 2.01
2018-04-05 17:00 | 12421.8243 | 215.241 | 16.42 | 21.37 | 23.03 | 32.63 | 13.21 | 2 | 3.31 | 4
2018-04-05 18:00 | 12202.6089 | 15.4539 | 14.41 | 21.81 | 29.99 | 29.91 | 17.98 | 8.98 | 14.11 | 2.74
2018-04-05 19:00 | 12059.6541 | -0.048233 | 11.76 | 22.66 | 31.75 | 40.55 | 20.28 | 6.1 | 11.83 | 15.1
2018-04-05 20:00 | 12059.6541 | -0.048233 | 116.52 | 116.52 | 34.16 | 44.84 | 25.63 | 9.36 | 12.09 | 19.74
2018-04-05 21:00 | 11724.1641 | -0.048233 | 13.15 | 30.82 | 23.08 | 30.48 | 8.33 | 1.6 | 15 | 12.78
2018-04-05 22:00 | 10209.6042 | -0.048233 | 11.09 | 28.84 | 19.91 | 26.86 | 20.36 | 0.01 | 52.6962 | 25.03
2018-04-05 23:00 | 9913.2042 | -0.048233 | 8.02 | 21.04 | 18.23 | 23.77 | 30.45 | 0.01 | 33.26 | 30.45
2018-04-06 | 10779.9391 | -0.048233 | 2.09 | 20.99 | 31.93 | 22.98 | 16.29 | 0.01 | 30.77 | 16.29
2018-04-06 01:00 | 9704.2042 | -0.048233 | -0.53 | 20.41 | 14.96 | 20.23 | 19.11 | 0.01 | 15 | 19.11
2018-04-06 02:00 | 10662.8341 | -0.048233 | 4.39 | 20.28 | 14.53 | 19.93 | 3.11 | 2 | 9.16 | 2.61
2018-04-06 03:00 | 9457.2042 | -0.048233 | -0.16 | 19.35 | 14.42 | 19.41 | 3.11 | 1.44 | 4.87 | 2.61
2018-04-06 04:00 | 9626.3042 | -0.048233 | 11.17 | 19.94 | 14.95 | 20.2 | 3.5 | 1.68 | 3.64 | 15
2018-04-06 05:00 | 11680.9091 | -0.048233 | 0.17 | 21.4 | 23.3 | 22.86 | 25 | 1.78 | 25 | 25
2018-04-06 06:00 | 12086.7296 | 7.8733 | 13.06 | 22.25 | 32.08 | 28.83 | 32.69 | 13.92 | 16.33 | 79.2862
2018-04-06 07:00 | 14233.2076 | 234.192 | 12.84 | 25.25 | 35.13 | 27.9 | 8.11 | 7.5 | 2 | 3.84
2018-04-06 08:00 | 14800.8798 | 508.27 | 13.74 | 21.82 | 33.54 | 27.13 | 7.61 | 8 | 9.96 | 7.41
2018-04-06 09:00 | 15110.8378 | 538.069 | 17.76 | 23.03 | 35.77 | 28.04 | 7.11 | 7.5 | 9 | 2.61
2018-04-06 10:00 | 13925.5332 | 745.456 | 14.64 | 21.69 | 28.6 | 28.44 | 6.73 | 0.97 | 1 | 2.61
2018-04-06 11:00 | 14832.8727 | 460.595 | 13.39 | 21.96 | 23.7 | 28.12 | 6.96 | 0.99 | 0.61 | 2.82
2018-04-06 12:00 | 13337.316 | 409.28 | 15.45 | 21.72 | 27.85 | 29.89 | 7 | 0.99 | 0.61 | 3.1
2018-04-06 13:00 | 13564.8438 | 214.783 | 19.13 | 22.68 | 22.74 | 33.03 | 8.2 | 1.25 | 1 | 5.01
2018-04-06 14:00 | 13657.8317 | 189.812 | 18.92 | 24.07 | 22.28 | 39.28 | 15 | 1.25 | 1.08 | 5.01
2018-04-06 15:00 | 12904.3528 | 171.614 | 22.77 | 26.69 | 22.45 | 46.18 | 20.66 | 10.5 | 1 | 15
2018-04-06 16:00 | 11099.341 | 79.5168 | 34.64 | 34.64 | 22.36 | 51.13 | 26.39 | 10.54 | 1.22 | 17.04
2018-04-06 17:00 | 11134.4355 | 81.4584 | 31.44 | 31.44 | 22.52 | 40.95 | 22.19 | 7.7 | 2.11 | 18.2
2018-04-06 18:00 | 10871.5363 | 14.7224 | 21.51 | 25.29 | 22.29 | 30.3 | 16.27 | 8.25 | 10 | 16.08
2018-04-06 19:00 | 11887.6891 | -0.048233 | 20.84 | 23.14 | 31.27 | 29.52 | 14.48 | 2 | 3.5 | 3.35
2018-04-06 20:00 | 10919.2542 | -0.048233 | 394.5357 | 26.01 | 30.76 | 33.46 | 22.28 | 9.99 | 3.44 | 22.28
2018-04-06 21:00 | 10495.5542 | -0.048233 | 22.37 | 26.94 | 20.49 | 26.8 | 9 | 0.99 | 19.51 | 10.04
2018-04-06 22:00 | 11320.0991 | -0.048233 | 17.19 | 20.28 | 18.82 | 23.28 | 7.39 | 0.01 | 30 | 6.05
2018-04-06 23:00 | 9948.3542 | -0.048233 | 15.02 | 18.8 | 18.09 | 21.15 | 9 | 0.01 | 25 | 9.2
2018-04-07 | 9685.2042 | -0.048233 | 11.2 | 17.34 | 17.36 | 18.33 | 4.29 | 0.01 | 24.83 | 18
2018-04-07 01:00 | 9564.5542 | -0.048233 | -0.43 | 17.14 | 17.44 | 14.57 | 4.29 | 0.01 | 13.53 | 1.91
2018-04-07 02:00 | 9594.9542 | -0.048233 | -8.11 | 16.24 | 17.15 | 12.34 | 3 | 0.99 | 9.94 | 0.77
2018-04-07 03:00 | 10712.4191 | -0.048233 | -22.42 | 15.36 | 17.16 | 12.86 | 3 | 0.99 | 0.5 | 1
2018-04-07 04:00 | 9719.4042 | -0.048233 | -22.4 | 16.66 | 17.44 | 14.22 | 3.5 | 0.99 | 3 | 2.01
2018-04-07 05:00 | 10645.6542 | -0.048233 | -0.59 | 17.12 | 18.33 | 20.59 | 19.47 | 1.25 | 52.6962 | 19.27
2018-04-07 06:00 | 13483.9041 | -0.048233 | 10.71 | 18.52 | 21.63 | 28.12 | 28.04 | 10.87 | 19.5 | 453.5606
2018-04-07 07:00 | 14212.9969 | 147.035 | 10.04 | 18.72 | 23.34 | 24.88 | 7.11 | 7.5 | 2.15 | 3.01
2018-04-07 08:00 | 14392.4477 | 267.945 | 8.47 | 19.23 | 23.36 | 25.27 | 7.71 | 7.5 | 3.01 | 3.75
2018-04-07 09:00 | 15800.8911 | 356.148 | 12.71 | 20.25 | 23.13 | 26.68 | 7.41 | 7.5 | 2.5 | 3.64
2018-04-07 10:00 | 16777.8243 | 540.151 | 12.81 | 19.31 | 23.26 | 26.7 | 6.21 | 0.99 | 2.11 | 4.19
2018-04-07 11:00 | 14731.5122 | 785.855 | 13.2 | 18.68 | 22.29 | 28.16 | 7 | 0.99 | 1.5 | 5.2
2018-04-07 12:00 | 17394.9983 | 1034.15 | 14.94 | 19.48 | 22.06 | 30.88 | 8.97 | 0.99 | 2.06 | 12.69
2018-04-07 13:00 | 15460.4869 | 1138.49 | 16.24 | 20.28 | 22.47 | 32.65 | 13.86 | 0.99 | 1.32 | 11.74
2018-04-07 14:00 | 12928.1225 | 1047.55 | 71.34 | 21.29 | 19.37 | 38.13 | 20.08 | 8.49 | 1.27 | 18.38
2018-04-07 15:00 | 12342.0903 | 835.674 | 119.89 | 22.03 | 19.59 | 43.75 | 33.89 | 21.44 | 1 | 24.25
2018-04-07 16:00 | 11849.6559 | 567.322 | 136.69 | 22.99 | 19.04 | 46.69 | 50.24 | 27 | 1 | 37.43
2018-04-07 17:00 | 11363.1809 | 217.243 | 39.19 | 23 | 22.51 | 38.22 | 42.17 | 27 | 1 | 31.18
2018-04-07 18:00 | 11195.8479 | 17.1031 | 13.5 | 21.66 | 21.95 | 29.5 | 18.83 | 11.33 | 2.04 | 18.83
2018-04-07 19:00 | 12328.6791 | -0.048233 | 11.78 | 20.16 | 30.51 | 28.44 | 12.38 | 6.75 | 2.61 | 11.36
2018-04-07 20:00 | 12472.1591 | -0.048233 | 13.55 | 20.85 | 22.28 | 31.55 | 16.07 | 0.99 | 2.11 | 12.74
2018-04-07 21:00 | 12051.2141 | -0.048233 | 12.51 | 20.23 | 19.72 | 25.37 | 25.17 | 0.97 | 25 | 24.37
2018-04-07 22:00 | 10330.2542 | -0.048233 | 11.2 | 17.83 | 18.04 | 21.38 | 45.01 | 0.01 | 53.8862 | 44.21
2018-04-07 23:00 | 10018.6542 | -0.048233 | 11.01 | 16.25 | 16.99 | 18.29 | 23.16 | 0.01 | 25 | 51.21
2018-04-08 | 9770.7042 | -0.048233 | 10.67 | 15.4 | 16.07 | 17.02 | 25.71 | 0.25 | 137.7434 | 26.71
2018-04-08 01:00 | 10771.4991 | -0.048233 | 10.44 | 15.6 | 15.36 | 15.94 | 18 | 0.25 | 18 | 4
2018-04-08 02:00 | 10813.6991 | -0.048233 | 10.4 | 14.32 | 14.32 | 14.87 | 18 | 1.43 | 18 | 2.61
2018-04-08 03:00 | 10671.2741 | -0.048233 | 8.61 | 14.13 | 14.14 | 13.51 | 3 | 1.42 | 16.46 | 2.61
2018-04-08 04:00 | 9661.4542 | -0.048233 | 10.39 | 13.66 | 15.35 | 13.96 | 3.58 | 1.41 | 14.8 | 3.58
2018-04-08 05:00 | 10939.2441 | -0.048233 | 12.83 | 12.92 | 18.95 | 14.93 | 27.05 | 1.26 | 25 | 28.69
2018-04-08 06:00 | 10083.2542 | -0.048233 | 14.56 | 14.83 | 38.79 | 21.15 | 23 | 6.6 | 32.55 | 79.7762
2018-04-08 07:00 | 11276.3323 | 87.4666 | 15.91 | 18.15 | 37.16 | 19.75 | 5.59 | 6 | 15.15 | 3.68
2018-04-08 08:00 | 10240.0509 | 122.001 | 14.74 | 20.63 | 33.42 | 24.18 | 7 | 6 | 8.54 | 5.8
2018-04-08 09:00 | 12093.8817 | 299.395 | 15.31 | 19.42 | 35.04 | 24.53 | 6.13 | 6 | 9 | 4.64
2018-04-08 10:00 | 11377.4898 | 722.305 | 16.15 | 19.29 | 33.16 | 26.07 | 4.46 | 1.19 | 2.44 | 4
2018-04-08 11:00 | 10961.252 | 441.16 | 19.6 | 19.6 | 30.42 | 29.05 | 5.01 | 1.02 | 0.71 | 4.15
2018-04-08 12:00 | 11588.7175 | 1158.65 | 18.12 | 20.11 | 30.43 | 28.48 | 5.01 | 0.99 | 2 | 3.77
2018-04-08 13:00 | 11511.7675 | 1158.65 | 17.47 | 20.43 | 30.43 | 31.38 | 6.13 | 1.42 | 2 | 4.37
2018-04-08 14:00 | 11290.199 | 1044.42 | 17.54 | 21.68 | 30.29 | 37.06 | 21.62 | 1.25 | 1 | 15
2018-04-08 15:00 | 11239.2362 | 826.775 | 16.49 | 23.23 | 23.82 | 49.12 | 30.79 | 15.23 | 1.41 | 25
2018-04-08 16:00 | 12343.8819 | 569.362 | 16.88 | 29.92 | 25.38 | 45.43 | 29.19 | 12 | 1.28 | 23.63
2018-04-08 17:00 | 11949.4575 | 242.5 | 15.8 | 23.22 | 30.5 | 33.28 | 21.21 | 0.99 | 2 | 16.43
2018-04-08 18:00 | 11788.7521 | 18.1726 | 12.29 | 22.27 | 32.39 | 27.51 | 20 | 1.39 | 9.48 | 4.27
2018-04-08 19:00 | 11842.3241 | -0.048233 | 10.99 | 22.27 | 32.79 | 26.06 | 6.68 | 1.4 | 11.06 | 6.47
2018-04-08 20:00 | 10632.3542 | -0.048233 | 14.21 | 20.46 | 29.63 | 27.94 | 8.02 | 1.22 | 9.82 | 10
2018-04-08 21:00 | 11533.2091 | -0.048233 | 11.19 | 20.95 | 23.54 | 24.15 | 4.87 | 0.99 | 23.68 | 3.69
2018-04-08 22:00 | 10239.0542 | -0.048233 | 10.52 | 20.61 | 20.86 | 21.26 | 13.5 | 0.25 | 107.7434 | 13.5
2018-04-08 23:00 | 11200.8841 | -0.048233 | 11.17 | 19.54 | 19.4 | 18.43 | 8 | 0.25 | 25 | 10.43
2018-04-09 | 9905.6042 | -0.048233 | 8.91 | 18.36 | 19.47 | 16.89 | 30.01 | 0.25 | 30 | 25.01
2018-04-09 01:00 | 10932.9141 | -0.048233 | 12.09 | 15.08 | 18.81 | 16.55 | 35.01 | 0.25 | 18 | 15
2018-04-09 02:00 | 10848.5141 | -0.048233 | 10.58 | 11.39 | 19.44 | 13.98 | 20.66 | 1.67 | 20.08 | 3
2018-04-09 03:00 | 9728.9042 | -0.048233 | 0.02 | 12.68 | 18.96 | 12.42 | 18.98 | 1.67 | 18 | 3
2018-04-09 04:00 | 9762.1542 | -0.048233 | 11.85 | 12.73 | 19.44 | 11 | 25.43 | 1.43 | 18 | 25.43
2018-04-09 05:00 | 9818.2042 | -0.048233 | 9.69 | 9.69 | 19.78 | 13.56 | 27.5 | 1.27 | 62.6962 | 87.1162
2018-04-09 06:00 | 9782.1042 | -0.048233 | 13.27 | 13.27 | 18.85 | 16.55 | 30 | 7.5 | 25 | 87.1162
2018-04-09 07:00 | 11040.0602 | 254.512 | 5.24 | 5.24 | 30.4 | 17.11 | 7 | 7.5 | 10.4 | 6
2018-04-09 08:00 | 10283.4241 | 556.657 | 13.05 | 17.27 | 29.36 | 19.75 | 7 | 7.5 | 12 | 13.05
2018-04-09 09:00 | 10909.0372 | 849.197 | 13.18 | 18.69 | 28.96 | 22.66 | 17.02 | 7.5 | 10.11 | 6
2018-04-09 10:00 | 12313.7595 | 1049.81 | 15.33 | 18.91 | 21.03 | 24.09 | 7.52 | 0.99 | 2.11 | 4
2018-04-09 11:00 | 12528.8107 | 1158.65 | 13.74 | 19.32 | 21 | 26.23 | 20 | 0.99 | 1 | 4
2018-04-09 12:00 | 11610.5675 | 1158.65 | 13.14 | 19.58 | 20.61 | 26.6 | 13.25 | 0.99 | 2 | 4.87
2018-04-09 13:00 | 11704.6175 | 1158.65 | 99.15 | 99.15 | 19.38 | 27.42 | 27.09 | 0.99 | 2 | 5.24
2018-04-09 14:00 | 13072.9481 | 1073.42 | 13.95 | 20.61 | 19.06 | 34.59 | 21.23 | 17.38 | 1 | 20.58
2018-04-09 15:00 | 12904.0479 | 867.325 | 13.91 | 22.15 | 19.41 | 42.39 | 33.85 | 29.36 | 1 | 32.56
2018-04-09 16:00 | 11399.3967 | 592.365 | 13.97 | 22.83 | 19.66 | 42.16 | 47.51 | 64.3173 | 1 | 46.51
2018-04-09 17:00 | 11133.2068 | 249.165 | 13.88 | 22.78 | 20.63 | 31.44 | 32.6 | 25 | 12.03 | 32.2
2018-04-09 18:00 | 12119.491 | 19.6692 | 11.2 | 20.83 | 20.58 | 31.57 | 30.01 | 14.06 | 11.56 | 21.06
2018-04-09 19:00 | 12119.7891 | -0.048233 | 10.75 | 20.69 | 22.57 | 38.41 | 26.69 | 0.99 | 12 | 12.49
2018-04-09 20:00 | 12270.6541 | -0.048233 | 17.68 | 23.59 | 21.74 | 46 | 26.74 | 0.99 | 12 | 21.09
2018-04-09 21:00 | 12240.0591 | -0.048233 | 13.37 | 22.72 | 21.61 | 30.24 | 16.97 | 0.99 | 25 | 16.77
2018-04-09 22:00 | 10830.9042 | -0.048233 | 11.45 | 21.34 | 20 | 24.42 | 17.48 | 0.25 | 107.7434 | 17.48
2018-04-09 23:00 | 10767.2542 | -0.048233 | 10.73 | 20.18 | 19.59 | 22.07 | 22 | 0.25 | 30 | 22
2018-04-10 | 11895.0741 | -0.048233 | 8.29 | 19.18 | 17.8 | 20.55 | 23.25 | 0.25 | 62.6962 | 25
2018-04-10 01:00 | 11661.9191 | -0.048233 | 7.57 | 18.24 | 17.98 | 19.67 | 23.25 | 0.25 | 25 | 3
2018-04-10 02:00 | 10456.6042 | -0.048233 | 0.58 | 18.03 | 17.33 | 18.68 | 3 | 1.5 | 10.42 | 3
2018-04-10 03:00 | 10434.7542 | -0.048233 | 1.68 | 17.85 | 17.31 | 18.2 | 3 | 1.5 | 2.11 | 3
2018-04-10 04:00 | 10705.5042 | -0.048233 | 3.74 | 18.53 | 17.98 | 19.13 | 23.25 | 1.5 | 9.91 | 3
2018-04-10 05:00 | 11765.7042 | -0.048233 | 0.45 | 19.53 | 19.51 | 22.18 | 25 | 1.5 | 119.8934 | 25
2018-04-10 06:00 | 15118.0991 | -0.048233 | 10.12 | 20.81 | 21.63 | 26.9 | 30 | 25 | 62.6962 | 40.85
2018-04-10 07:00 | 14916.7081 | 262.798 | 9.23 | 33.96 | 21.7 | 23.96 | 6 | 10.5 | 15.98 | 10.5
2018-04-10 08:00 | 17573.9927 | 557.813 | 12.9 | 21.77 | 21.68 | 25.2 | 18.62 | 10.2 | 18.13 | 11.8
2018-04-10 09:00 | 17498.0357 | 860.985 | 12.67 | 20.76 | 21.83 | 25.55 | 22.51 | 9 | 17.51 | 3.01
2018-04-10 10:00 | 17436.3475 | 1071.05 | 12.51 | 20.51 | 22.08 | 27.39 | 7.31 | 1.49 | 2.11 | 3.01
2018-04-10 11:00 | 16509.7175 | 1158.65 | 13.35 | 20.86 | 22.24 | 29.12 | 5.01 | 0.99 | 1 | 3.01
2018-04-10 12:00 | 19047.6558 | 1158.65 | 14.29 | 22.25 | 21.26 | 33.28 | 8.5 | 0.99 | 1 | 4
2018-04-10 13:00 | 17465.4175 | 1158.65 | 13.36 | 23.14 | 21.03 | 38.16 | 12.27 | 0.99 | 2.11 | 4.07
2018-04-10 14:00 | 17928.2902 | 1077.64 | 12.97 | 23.76 | 20.91 | 44.43 | 16.69 | 0.99 | 2 | 13.08
2018-04-10 15:00 | 15801.7858 | 886.996 | 13.95 | 30.65 | 21.03 | 52.39 | 22.98 | 10.52 | 2 | 15.03
2018-04-10 16:00 | 14176.4976 | 594.629 | 14.37 | 31.93 | 21.21 | 46.16 | 19.11 | 1.2 | 1 | 3.01
2018-04-10 17:00 | 14633.0578 | 249.197 | 11.94 | 30.67 | 21.22 | 37.05 | 11.92 | 0.99 | 1.14 | 4
2018-04-10 18:00 | 12796.9684 | 19.4931 | 45.22 | 45.22 | 21.82 | 28.91 | 8.05 | 1.1 | 12 | 4
2018-04-10 19:00 | 12527.6042 | -0.048233 | 45.11 | 45.11 | 22.85 | 32.45 | 8.62 | 1.04 | 12 | 5.01
2018-04-10 20:00 | 12625.4542 | -0.048233 | 39.33 | 39.33 | 23.08 | 35 | 21.55 | 0.99 | 12 | 21.35
2018-04-10 21:00 | 13497.6191 | -0.048233 | 12.5 | 31.46 | 21.25 | 26.59 | 6.69 | 1.15 | 17.57 | 4.02
2018-04-10 22:00 | 11463.6042 | -0.048233 | 14.8 | 23.54 | 20.26 | 24.24 | 18.04 | 0.3 | 63.0962 | 28.93
2018-04-10 23:00 | 11235.6042 | -0.048233 | 12.43 | 25.81 | 18.33 | 22.5 | 17 | 0.3 | 50.2362 | 17
2018-04-11 | 11039.9042 | -0.048233 | 10.19 | 20.24 | 17.64 | 22.3 | 19.11 | 0.01 | 62.6962 | 20.24
2018-04-11 01:00 | 12271.7091 | -0.048233 | 13.98 | 19.72 | 17.33 | 19.41 | 20 | 0.01 | 11.6 | 1.98
2018-04-11 02:00 | 10914.5042 | -0.048233 | 16.01 | 19.21 | 17.24 | 18.2 | 3.5 | 1.22 | 4.01 | 2.11
2018-04-11 03:00 | 10754.9042 | -0.048233 | 14.99 | 19.15 | 16.03 | 18.27 | 3.5 | 1.25 | 2.9 | 2.11
2018-04-11 04:00 | 11108.3042 | -0.048233 | 14.55 | 19.35 | 16.37 | 19.07 | 3.9 | 1.25 | 3.44 | 2.6
2018-04-11 05:00 | 13349.9191 | -0.048233 | 13.46 | 20.65 | 16.02 | 21.71 | 25 | 1.44 | 29.72 | 25
2018-04-11 06:00 | 15520.0541 | -0.048233 | 14.71 | 20.6 | 16.81 | 26.81 | 25.2 | 14 | 61.9462 | 78.3362
2018-04-11 07:00 | 17235.3177 | 257.794 | 18.1 | 21.95 | 17.2 | 22.94 | 4.36 | 8.97 | 3.5 | 4
2018-04-11 08:00 | 15624.2424 | 577.571 | 15.47 | 25.75 | 18.24 | 23.91 | 6.9 | 5 | 3.5 | 6
2018-04-11 09:00 | 16362.4209 | 881.601 | 777.3911 | 509.78 | 19.8 | 24.89 | 6.63 | 5.42 | 3.46 | 4
2018-04-11 10:00 | 16366.3435 | 1101.73 | 15.22 | 24.78 | 20.11 | 25.08 | 6.75 | 1.02 | 1 | 3.27
2018-04-11 11:00 | 16034.7175 | 1158.65 | 15.6 | 25.97 | 19.15 | 27.02 | 7.36 | 0.99 | 0.82 | 3.01
2018-04-11 12:00 | 18951.6508 | 1158.65 | 116.38 | 116.38 | 18.45 | 28.28 | 8.66 | 0.99 | 1 | 4
2018-04-11 13:00 | 19537.1758 | 1158.65 | 82.01 | 82.01 | 17.61 | 30.14 | 18.16 | 1.02 | 1.57 | 13.17
2018-04-11 14:00 | 17611.5687 | 1094.43 | 17.83 | 25.56 | 17.61 | 36.75 | 28.83 | 10.53 | 0.71 | 20.61
2018-04-11 15:00 | 14242.7961 | 874.417 | 19.91 | 24.94 | 17.26 | 37.18 | 50 | 20.5 | 1 | 28.43
2018-04-11 16:00 | 13949.1578 | 579.324 | 20.69 | 31.32 | 16.72 | 41.03 | 91.4241 | 20.5 | 1 | 38.67
2018-04-11 17:00 | 14725.613 | 242.927 | 184.41 | 184.41 | 17.6 | 28.53 | 41.28 | 15.64 | 1 | 31.46
2018-04-11 18:00 | 14059.0126 | 20.0783 | 19.45 | 22.09 | 18.31 | 26.46 | 23.58 | 1.34 | 10 | 5
2018-04-11 19:00 | 12103.9042 | -0.048233 | 18.71 | 20.4 | 21.73 | 26.69 | 8.16 | 1.36 | 3.5 | 3.17
2018-04-11 20:00 | 11690.6542 | -0.048233 | 20.95 | 20.95 | 21.66 | 33.61 | 16.23 | 1.02 | 2.33 | 11.58
2018-04-11 21:00 | 11301.1542 | -0.048233 | 20.07 | 22.36 | 19.14 | 25.85 | 6.14 | 0.99 | 8.11 | 5.75
2018-04-11 22:00 | 12312.8541 | -0.048233 | 14.78 | 19.67 | 18.39 | 23.06 | 7.35 | 0.01 | 26.66 | 25
2018-04-11 23:00 | 11899.2941 | -0.048233 | 14.3 | 17.92 | 16.55 | 22.1 | 16.38 | 0.01 | 22 | 20.85
2018-04-12 | 11674.5791 | -0.048233 | 14.18 | 16.56 | 14.52 | 20.86 | 4.25 | 0.01 | 12.06 | 4
2018-04-12 01:00 | 10381.5542 | -0.048233 | 13.02 | 15.17 | 14.18 | 19.29 | 3.99 | 0.01 | 7.81 | 2.01
2018-04-12 02:00 | 10431.9042 | -0.048233 | 12.77 | 16.91 | 9.83 | 18.88 | 3.58 | 1.62 | 3.5 | 1
2018-04-12 03:00 | 10493.6542 | -0.048233 | 12.66 | 18.55 | 9.69 | 19.1 | 3.8 | 1.62 | 3 | 1.11
2018-04-12 04:00 | 11818.0591 | -0.048233 | 13.97 | 17.4 | 9.66 | 19.91 | 4.11 | 1.8 | 2.82 | 2.01
2018-04-12 05:00 | 12769.6691 | -0.048233 | 17.02 | 18.35 | 11.3 | 21.28 | 4.25 | 1.82 | 25.98 | 20.14
2018-04-12 06:00 | 14774.1691 | -0.048233 | 96.47 | 19.78 | 13.85 | 27.37 | 7.75 | 7.18 | 27.07 | 451.4006
2018-04-12 07:00 | 16218.8283 | 265.297 | 16.87 | 21.17 | 14.04 | 24.24 | 4.45 | 5.61 | 8.54 | 4.45
2018-04-12 08:00 | 15761.2154 | 553.753 | 17.51 | 20.77 | 16.97 | 25.66 | 5.11 | 8.39 | 9 | 5.11
2018-04-12 09:00 | 18272.5778 | 820.979 | 18.47 | 20.61 | 17.77 | 26.44 | 6 | 7.12 | 9 | 5.91
2018-04-12 10:00 | 17402.436 | 1035.2 | 19.09 | 20.92 | 18.11 | 26.05 | 6.61 | 1.45 | 1.77 | 4
2018-04-12 11:00 | 17449.3308 | 1158.65 | 19.35 | 21.54 | 17.69 | 26.1 | 6.89 | 1.42 | 1 | 4
2018-04-12 12:00 | 16169.6175 | 1158.65 | 21.34 | 21.62 | 17.55 | 27.59 | 5.86 | 1.36 | 1 | 3.1
2018-04-12 13:00 | 18039.0757 | 1158.65 | 50.51 | 23.46 | 16.39 | 30.58 | 7.21 | 1.93 | 2.11 | 3.52
2018-04-12 14:00 | 15142.8005 | 1056.79 | 18.02 | 22.57 | 15.52 | 33.41 | 15 | 1.55 | 1 | 3.33
2018-04-12 15:00 | 16269.8207 | 829.631 | 17.37 | 22.08 | 15.52 | 35.55 | 21.04 | 9.04 | 1 | 15.47
2018-04-12 16:00 | 15345.6987 | 547.686 | 34.71 | 24.24 | 15.67 | 36.67 | 19.58 | 1.65 | 1 | 14.56
2018-04-12 17:00 | 13173.5445 | 238.889 | 49.15 | 22.22 | 17.64 | 29.79 | 16.72 | 1.3 | 2 | 11.61
2018-04-12 18:00 | 14124.1721 | 20.8409 | 16.51 | 22.57 | 19.3 | 26.31 | 16.81 | 13.81 | 3.5 | 16.81
2018-04-12 19:00 | 12612.1542 | -0.048233 | 15.29 | 21.07 | 21.44 | 29.62 | 16.19 | 14.39 | 2.8 | 16.19
2018-04-12 20:00 | 13643.2091 | -0.048233 | 18.88 | 29.79 | 21.03 | 39.16 | 27 | 25 | 2.41 | 27
2018-04-12 21:00 | 13423.7691 | -0.048233 | 20.09 | 25.84 | 18.53 | 25.82 | 7.61 | 9.71 | 8 | 11.52
2018-04-12 22:00 | 12913.1491 | -0.048233 | 17.29 | 24.78 | 17.61 | 22.86 | 19.07 | 0.01 | 17.92 | 19.07
2018-04-12 23:00 | 12368.7691 | -0.048233 | 339.9857 | 24.73 | 15.59 | 21.43 | 4.51 | 0.01 | 16.72 | 17.49
2018-04-13 | 12012.1791 | -0.048233 | 778.7311 | 21.54 | 13.83 | 18.69 | 4 | 0.01 | 17.34 | 16.11
2018-04-13 01:00 | 10615.2542 | -0.048233 | 14.03 | 20.86 | 13.83 | 17.69 | 3.5 | 0.01 | 3.5 | 2.61
2018-04-13 02:00 | 10455.6542 | -0.048233 | 14.01 | 19.63 | 13.6 | 17.51 | 3.5 | 9.5 | 3.89 | 0.5
2018-04-13 03:00 | 11730.4941 | -0.048233 | 13.38 | 19.87 | 13.73 | 17.47 | 4 | 9 | 3.5 | 1
2018-04-13 04:00 | 12014.2891 | -0.048233 | 13.41 | 19.68 | 14.48 | 17.67 | 4 | 9.5 | 3.11 | 3.8
2018-04-13 05:00 | 13011.2641 | -0.048233 | 14.88 | 20.32 | 15.21 | 19.62 | 15 | 13.43 | 19.5 | 20.14
2018-04-13 06:00 | 13337.9542 | -0.048233 | 314.1457 | 269.82 | 19.51 | 24.44 | 34.55 | 58.4573 | 10.88 | 77.1862
2018-04-13 07:00 | 16532.5644 | 94.6772 | 50.6 | 50.6 | 21.22 | 23 | 6 | 14.23 | 2 | 14.43
2018-04-13 08:00 | 16765.9271 | 94.874 | 16.02 | 23.39 | 19.63 | 24.12 | 19.54 | 18.27 | 3.5 | 19.17
2018-04-13 09:00 | 16881.8209 | 126.726 | 102.56 | 102.56 | 20.78 | 25.94 | 18.3 | 17.5 | 2.52 | 17.5
2018-04-13 10:00 | 16113.7005 | 471.79 | 15.84 | 31.43 | 22.77 | 25.61 | 7.92 | 0.99 | 2.31 | 4
2018-04-13 11:00 | 15414.8026 | 529.108 | 15.41 | 23.72 | 20.96 | 30.48 | 14.75 | 0.99 | 2 | 10
2018-04-13 12:00 | 15784.401 | 751.159 | 15.45 | 29.29 | 20.63 | 28.46 | 16.9 | 0.99 | 2 | 3.96
2018-04-13 13:00 | 16448.832 | 1105.56 | 15.57 | 29.4 | 19.88 | 30.91 | 18.11 | 15.51 | 1 | 18.11
2018-04-13 14:00 | 16475.168 | 998.273 | 37.41 | 37.41 | 19.84 | 35.82 | 25.06 | 21.46 | 0.85 | 25.06
2018-04-13 15:00 | 13981.7912 | 820.675 | 17.09 | 27.88 | 19.08 | 41.3 | 27.03 | 16.54 | 1 | 21.04
2018-04-13 16:00 | 14770.3133 | 544.297 | 171.66 | 28.38 | 19.26 | 40.07 | 31.61 | 11.57 | 1 | 17.17
2018-04-13 17:00 | 13967.854 | 233.672 | 51.09 | 22.97 | 19.19 | 31.04 | 28.6 | 7 | 1 | 14.05
2018-04-13 18:00 | 12030.1802 | 19.3476 | 145.26 | 19.68 | 19.56 | 27.04 | 34.37 | 7.14 | 2.31 | 4.08
2018-04-13 19:00 | 11783.7542 | -0.048233 | 20 | 20.85 | 22.32 | 26.1 | 29.45 | 1.61 | 3.98 | 3.1
2018-04-13 20:00 | 11866.4042 | -0.048233 | 85.35 | 21.7 | 22.74 | 31.07 | 19.41 | 10.65 | 2.11 | 12.65
2018-04-13 21:00 | 11645.0542 | -0.048233 | 18.64 | 21.19 | 18.42 | 24.77 | 6.62 | 0.99 | 8.05 | 6.38
2018-04-13 22:00 | 11195.7042 | -0.048233 | 54.48 | 24.48 | 16.61 | 21.86 | 8 | 0.01 | 23.49 | 15
2018-04-13 23:00 | 10812.8542 | -0.048233 | 13.12 | 23.33 | 17.06 | 20.18 | 19.83 | 0.01 | 22 | 17.47
2018-04-14 | 10628.5542 | -0.048233 | 11.65 | 21.19 | 14.73 | 19.7 | 3.25 | 0.01 | 15 | 3.05
2018-04-14 01:00 | 10524.0542 | -0.048233 | 10.72 | 19.6 | 13.88 | 16.91 | 3.01 | 0.01 | 10.32 | 2.01
2018-04-14 02:00 | 11520.5491 | -0.048233 | 4.56 | 16.22 | 13.2 | 14.72 | 3 | 1.25 | 14 | 1.11
2018-04-14 03:00 | 10323.6042 | -0.048233 | 10.2 | 13.02 | 13.12 | 14.07 | 3 | 1.38 | 0.61 | 2.01
2018-04-14 04:00 | 10582.9542 | -0.048233 | 10.1 | 10.1 | 13.55 | 15.57 | 3.25 | 1.38 | 9.42 | 2.5
2018-04-14 05:00 | 11516.8042 | -0.048233 | 11.77 | 18.78 | 15.93 | 18.69 | 4.65 | 1.39 | 15.8 | 20
2018-04-14 06:00 | 14488.2641 | -0.048233 | 16.69 | 19.83 | 18.44 | 22.54 | 8 | 9 | 13.55 | 17.15
2018-04-14 07:00 | 13909.2948 | 132.363 | 16.08 | 19.22 | 20.15 | 21.3 | 6 | 7.8 | 2 | 3.15
2018-04-14 08:00 | 15435.8527 | 162.14 | 15.43 | 17.96 | 20.69 | 22.38 | 6.66 | 6.51 | 2.72 | 6.66
2018-04-14 09:00 | 14167.6682 | 166.335 | 16.72 | 18.87 | 21.17 | 22.94 | 6.61 | 6 | 2.55 | 5.62
2018-04-14 10:00 | 15938.2374 | 560.334 | 18.53 | 20.46 | 21.61 | 24.31 | 7.65 | 0.97 | 2.11 | 4.05
2018-04-14 11:00 | 15920.2528 | 617.287 | 18.91 | 21.14 | 21.59 | 25.11 | 8.11 | 0.99 | 2 | 5.63
2018-04-14 12:00 | 15408.6675 | 1158.65 | 19.59 | 21.27 | 21.17 | 25.58 | 6.61 | 0.99 | 2 | 3.1
2018-04-14 13:00 | 16582.1207 | 1158.65 | 254.9557 | 22.09 | 21.01 | 28.56 | 8.11 | 9.91 | 2 | 3.1
2018-04-14 14:00 | 15275.7174 | 673.353 | 21.06 | 24.85 | 19.45 | 32.27 | 15 | 11.59 | 1.95 | 4.76
2018-04-14 15:00 | 12815.6197 | 369.126 | 20.68 | 20.68 | 19.21 | 35.18 | 16.47 | 12.67 | 2 | 15.08
2018-04-14 16:00 | 12418.7534 | 249.372 | 19.94 | 19.94 | 19.34 | 36 | 17.34 | 14 | 2 | 16.41
2018-04-14 17:00 | 13555.8153 | 105.114 | 20.71 | 20.71 | 20.43 | 29.08 | 14.96 | 11.33 | 12 | 13.74
2018-04-14 18:00 | 13137.5749 | 21.6776 | 18.38 | 18.38 | 20.85 | 24.67 | 14.54 | 10.34 | 12 | 2.64
2018-04-14 19:00 | 11878.7542 | -0.048233 | 15.56 | 18.57 | 21.55 | 24.3 | 13.8 | 10.84 | 12 | 12.43
2018-04-14 20:00 | 13260.2441 | -0.048233 | 17.42 | 20.34 | 21.62 | 25.76 | 21.98 | 21.98 | 12 | 21.98
2018-04-14 21:00 | 12818.1991 | -0.048233 | 14.97 | 19.55 | 19.36 | 24.52 | 8 | 0.99 | 12 | 10.74
2018-04-14 22:00 | 11033.2542 | -0.048233 | 12.53 | 18.54 | 18.6 | 22.7 | 9.71 | 0.01 | 36.89 | 9.99
2018-04-14 23:00 | 11810.6741 | -0.048233 | 14.14 | 18.51 | 18.41 | 21.5 | 8.23 | 0.01 | 15.31 | 9.8
2018-04-15 | 11717.8341 | -0.048233 | 1.58 | 19.82 | 13.89 | 18.68 | 7.97 | 0.01 | 26.52 | 15
2018-04-15 01:00 | 10424.3042 | -0.048233 | -0.24 | 18.94 | 10.79 | 15.93 | 5.12 | 0.01 | 22.94 | 3.5
2018-04-15 02:00 | 11501.5591 | -0.048233 | -0.03 | 17.95 | 8.85 | 12.84 | 3.48 | 1.42 | 14 | 2.61
2018-04-15 03:00 | 11322.2091 | -0.048233 | -0.01 | 17.78 | 8.44 | 12.45 | 3.48 | 1.42 | 13.93 | 3.11
2018-04-15 04:00 | 10166.8542 | -0.048233 | 7.51 | 17.53 | 10.88 | 10.5 | 4.22 | 1.42 | 14 | 4
2018-04-15 05:00 | 11449.8641 | -0.048233 | 11.57 | 17.65 | 14.39 | 16.37 | 25 | 1.56 | 33.65 | 25
2018-04-15 06:00 | 11612.3341 | -0.048233 | 12.03 | 18.15 | 18.05 | 19.51 | 14.5 | 7.78 | 16.92 | 20
2018-04-15 07:00 | 11757.63 | 131.673 | 13.24 | 17.78 | 17.93 | 19.43 | 7.11 | 4 | 3.11 | 4
2018-04-15 08:00 | 10672.5812 | 161.296 | 13.33 | 18.13 | 18.98 | 21.52 | 17.78 | 7.81 | 9.07 | 6.94
2018-04-15 09:00 | 10922.8083 | 228.693 | 12.62 | 20.59 | 20.08 | 21.93 | 5.08 | 6 | 9 | 4.89
2018-04-15 10:00 | 10855.9625 | 195.329 | 12.14 | 20.6 | 20.44 | 24.08 | 3.99 | 1 | 2.61 | 3.79
2018-04-15 11:00 | 12156.6606 | 329.901 | 11.89 | 20.13 | 19.34 | 27.01 | 3.84 | 1.12 | 2 | 3.64
2018-04-15 12:00 | 12501.9789 | 465.217 | 13.21 | 19.66 | 17.68 | 28.3 | 5.06 | 1.25 | 2.5 | 4
2018-04-15 13:00 | 12884.1136 | 719.43 | 15.84 | 20.25 | 17.46 | 29.09 | 5.25 | 10.25 | 2.11 | 4.14
2018-04-15 14:00 | 12843.7462 | 836.167 | 16.06 | 20.96 | 16.45 | 32.73 | 23 | 19.59 | 2 | 20.18
2018-04-15 15:00 | 12776.3781 | 738.311 | 17.1 | 21.43 | 16.46 | 37.35 | 28.71 | 25.01 | 1 | 26.95
2018-04-15 16:00 | 12486.27 | 475.327 | 18.96 | 21.84 | 16.98 | 39.47 | 24.74 | 21.33 | 2 | 21.38
2018-04-15 17:00 | 11073.2484 | 216.051 | 21.64 | 21.64 | 17.74 | 32.37 | 19 | 15.59 | 2 | 18
2018-04-15 18:00 | 12111.8277 | 20.4054 | 18.67 | 20.46 | 18.88 | 25.84 | 6.65 | 10.25 | 9 | 4
2018-04-15 19:00 | 12094.4691 | -0.048233 | 11.28 | 20.27 | 20.03 | 26.3 | 8.46 | 1 | 9 | 5
2018-04-15 20:00 | 12131.3941 | -0.048233 | 11.96 | 21.31 | 21.26 | 27.74 | 12.25 | 10.25 | 3.11 | 12.25
2018-04-15 21:00 | 12002.6841 | -0.048233 | 11.26 | 20.37 | 18.57 | 26.15 | 8.04 | 0.99 | 12 | 7.84
2018-04-15 22:00 | 10657.0542 | -0.048233 | 12.33 | 20.07 | 17.9 | 22.16 | 9 | 0.01 | 30 | 10
2018-04-15 23:00 | 10516.4542 | -0.048233 | 9.99 | 21.2 | 17.52 | 21.32 | 9 | 0.01 | 62.6962 | 11
2018-04-16 | 10275.1542 | -0.048233 | 6.32 | 18.52 | 16.02 | 18.71 | 4.5 | 0.01 | 137.7434 | 18
2018-04-16 01:00 | 11325.3741 | -0.048233 | 5.55 | 17.68 | 17.02 | 17.32 | 4.5 | 0.01 | 23.83 | 3
2018-04-16 02:00 | 11179.7841 | -0.048233 | 0.01 | 17.59 | 16.72 | 16.86 | 3.45 | 1.51 | 9.5 | 3.25
2018-04-16 03:00 | 10022.4542 | -0.048233 | 0 | 17.35 | 15.62 | 16.38 | 3.45 | 1.62 | 2.45 | 3.45
2018-04-16 04:00 | 10026.2542 | -0.048233 | 0 | 16.9 | 15.92 | 16.72 | 4 | 1.25 | 10.3 | 4
2018-04-16 05:00 | 11161.8491 | -0.048233 | 8.78 | 17.49 | 17.48 | 18.26 | 25 | 1.71 | 52.1762 | 25
2018-04-16 06:00 | 10067.1042 | -0.048233 | 12.18 | 18.13 | 16.43 | 19.56 | 15.07 | 12.87 | 31.82 | 79.6762
2018-04-16 07:00 | 11162.9283 | 92.9747 | 8.63 | 18.55 | 16.95 | 19.32 | 5.92 | 6.42 | 3.55 | 4.49
2018-04-16 08:00 | 10217.3707 | 133.127 | 12.28 | 19.94 | 17.86 | 20.82 | 7.11 | 8.14 | 15.25 | 6.75
2018-04-16 09:00 | 10991.7698 | 744.284 | 13.25 | 19.91 | 17.62 | 22.83 | 6.05 | 5.6 | 33.43 | 5.73
2018-04-16 10:00 | 11324.9785 | 1012.03 | 13 | 19.69 | 17.58 | 23.7 | 5.36 | 0.99 | 3.46 | 4.31
2018-04-16 11:00 | 11484.2175 | 1158.65 | 12.7 | 19.9 | 18.96 | 24.78 | 6.37 | 0.99 | 2 | 4
2018-04-16 12:00 | 12873.5847 | 1111.45 | 16.21 | 20.69 | 19.03 | 25.97 | 21.01 | 0.99 | 1.92 | 3.1
2018-04-16 13:00 | 13014.4483 | 1065.97 | 17.7 | 20.82 | 18.76 | 27.34 | 26.25 | 12.99 | 2 | 3.08
2018-04-16 14:00 | 11225.9847 | 637.826 | 15.3 | 22.22 | 18.7 | 33.28 | 24.37 | 11.17 | 2 | 4
2018-04-16 15:00 | 12525.7207 | 607.721 | 13.66 | 22.41 | 18.44 | 36.65 | 29.56 | 15.28 | 1 | 20
2018-04-16 16:00 | 11221.875 | 456.5 | 13.94 | 22.28 | 19.69 | 42.08 | 34.16 | 14.88 | 1.09 | 20
2018-04-16 17:00 | 12108.5526 | 115.301 | 11.47 | 21.98 | 19.04 | 33.8 | 25.66 | 12.05 | 2 | 15.25
2018-04-16 18:00 | 10910.8634 | 26.1194 | 12.68 | 20.39 | 19.85 | 26.05 | 15.25 | 10.25 | 11.32 | 2.61
2018-04-16 19:00 | 10769.1542 | -0.048233 | 12.7 | 20.17 | 21.58 | 26.98 | 9 | 0.99 | 9 | 3.1
2018-04-16 20:00 | 10921.1542 | -0.048233 | 311.3557 | 20.75 | 21.71 | 33.43 | 17.11 | 12.43 | 2.45 | 14.43
2018-04-16 21:00 | 12037.4991 | -0.048233 | 16.04 | 20.42 | 19.88 | 25.43 | 7.61 | 0.99 | 32 | 5.86
2018-04-16 22:00 | 10633.3042 | -0.048233 | 18.1 | 20.26 | 17.64 | 23.24 | 7.61 | 0.12 | 51.0562 | 11.15
2018-04-16 23:00 | 10532.6042 | -0.048233 | 255.7257 | 19.92 | 16.54 | 22.01 | 7.11 | 0.12 | 18.47 | 7
2018-04-17 | 11559.5841 | -0.048233 | 15.06 | 18.62 | 15.88 | 20.11 | 4 | 0.25 | 20.09 | 3.96
2018-04-17 01:00 | 10263.7542 | -0.048233 | 12.9 | 18.29 | 12.99 | 18.73 | 3.5 | 0.25 | 3.5 | 2.4
2018-04-17 02:00 | 11325.3741 | -0.048233 | 13.07 | 18.9 | 11.55 | 18.51 | 3 | 1.5 | 3.5 | 2.11
2018-04-17 03:00 | 11364.4091 | -0.048233 | 12.76 | 18.95 | 11.09 | 18.54 | 3 | 1.5 | 1.32 | 2.11
2018-04-17 04:00 | 10637.1042 | -0.048233 | 12.99 | 20.09 | 12.97 | 18.77 | 3.79 | 1.53 | 3.22 | 2.61
2018-04-17 05:00 | 11591.8542 | -0.048233 | 12.96 | 19.91 | 16.15 | 21.03 | 4.07 | 2 | 13.8 | 4.72
2018-04-17 06:00 | 13111.8542 | -0.048233 | 15.18 | 19.8 | 17.49 | 24.64 | 8.41 | 12 | 20.58 | 45.85
2018-04-17 07:00 | 13759.3145 | 168.489 | 15.78 | 20.53 | 17.59 | 24.3 | 5.01 | 7.66 | 2.11 | 4.61
2018-04-17 08:00 | 15664.9016 | 154.248 | 15.19 | 20.68 | 18.87 | 25.19 | 7.38 | 7.63 | 9 | 6.86
2018-04-17 09:00 | 15795.9875 | 223.5 | 15.15 | 21.6 | 19.87 | 27.87 | 4.01 | 8.91 | 9 | 3.66
2018-04-17 10:00 | 16034.3922 | 299.476 | 15.56 | 28.46 | 18.85 | 29.72 | 5.48 | 1.2 | 2.11 | 3.92
2018-04-17 11:00 | 14405.2252 | 731.395 | 16.89 | 25.17 | 18.7 | 30.62 | 6.14 | 1.25 | 1 | 3.91
2018-04-17 12:00 | 14570.2307 | 528.085 | 30.54 | 29.32 | 18.55 | 34.47 | 8.01 | 1.25 | 1 | 5.5
2018-04-17 13:00 | 16055.6715 | 360.646 | 20.04 | 25.76 | 18.56 | 38.03 | 14.84 | 11.64 | 2 | 14.84
2018-04-17 14:00 | 15336.726 | 355.181 | 17.76 | 24.86 | 17.48 | 42.65 | 23.94 | 12.25 | 2 | 23.64
2018-04-17 15:00 | 14470.0466 | 283.684 | 16.54 | 23.46 | 17.41 | 48.63 | 25.48 | 18.5 | 2 | 25
2018-04-17 16:00 | 14142.0724 | 308.808 | 17.78 | 23.34 | 18.3 | 47.6 | 25.06 | 16.05 | 2 | 24.55
2018-04-17 17:00 | 13845.3668 | 95.5704 | 17.79 | 21.23 | 19.19 | 35.74 | 16 | 11.5 | 2 | 16
2018-04-17 18:00 | 12343.371 | 22.0221 | 16.63 | 20 | 19.12 | 31.54 | 9.32 | 8.48 | 9 | 3.69
2018-04-17 19:00 | 12304.3542 | -0.048233 | 16.52 | 19.46 | 19.32 | 29.96 | 9.01 | 1.51 | 9 | 3.7
2018-04-17 20:00 | 13673.8041 | -0.048233 | 20.88 | 20.88 | 22.17 | 34.16 | 23.81 | 10.35 | 2.11 | 23.81
2018-04-17 21:00 | 12011.7542 | -0.048233 | 17.56 | 20.36 | 18.52 | 28.08 | 7.61 | 1.32 | 14.61 | 4
2018-04-17 22:00 | 12711.6441 | -0.048233 | 42.68 | 20.2 | 17.66 | 25.53 | 5.77 | 0.25 | 25.01 | 13
2018-04-17 23:00 | 11125.4042 | -0.048233 | 14.24 | 18.67 | 16.79 | 23.2 | 5.79 | 0.25 | 17 | 13.32
2018-04-18 | 10949.6542 | -0.048233 | 12.15 | 17.73 | 13.29 | 19.46 | 3.63 | 0.12 | 55.0362 | 12
2018-04-18 01:00 | 10883.1542 | -0.048233 | 10.87 | 16.77 | 13.15 | 18.37 | 3 | 0.01 | 3.5 | 2.61
2018-04-18 02:00 | 10952.5042 | -0.048233 | 10.31 | 16.71 | 11.42 | 17.59 | 3 | 2 | 3.5 | 2.5
2018-04-18 03:00 | 12112.4041 | -0.048233 | 9.93 | 17.03 | 11.01 | 17.58 | 3 | 2 | 1.08 | 2.5
2018-04-18 04:00 | 12542.8441 | -0.048233 | 9.89 | 17.39 | 11.01 | 18.42 | 3 | 2 | 3.45 | 2.76
2018-04-18 05:00 | 13530.3241 | -0.048233 | 10.46 | 18.02 | 12.43 | 20.37 | 4.11 | 2 | 61.3062 | 19.29
2018-04-18 06:00 | 15659.3141 | -0.048233 | 12.2 | 19.65 | 13.13 | 24.3 | 6 | 7.8 | 61.1062 | 79.0662
2018-04-18 07:00 | 16684.2463 | 75.4515 | 15.27 | 20.29 | 17.04 | 24.4 | 4.95 | 1.5 | 2.11 | 4
2018-04-18 08:00 | 15331.5266 | 167.449 | 19.9 | 20.32 | 19.05 | 25.02 | 5.85 | 7.14 | 18 | 5.65
2018-04-18 09:00 | 17566.5412 | 131.75 | 16.91 | 20.57 | 20.49 | 27.12 | 5.65 | 8.41 | 16.85 | 5
2018-04-18 10:00 | 17669.1864 | 158.044 | 19.64 | 20.56 | 20.27 | 30.59 | 6.5 | 1 | 2.89 | 4
2018-04-18 11:00 | 15589.5874 | 176.092 | 31.52 | 21.72 | 20.86 | 33.74 | 8 | 1 | 1 | 5.5
2018-04-18 12:00 | 15788.3682 | 254.335 | 49.71 | 22.06 | 20 | 35.67 | 7.59 | 1.25 | 1 | 4.97
2018-04-18 13:00 | 17904.5538 | 220.141 | 255.2157 | 22.2 | 19.53 | 38.66 | 15.09 | 1.18 | 1 | 5.42
2018-04-18 14:00 | 16901.8723 | 395.732 | 159.73 | 22.69 | 19.07 | 45.01 | 16.98 | 10.25 | 1.58 | 16.66
2018-04-18 15:00 | 15769.5439 | 224.435 | 23.88 | 25.85 | 18.72 | 47.5 | 22.28 | 11.59 | 1 | 20.57
2018-04-18 16:00 | 13539.6869 | 209.302 | 20.6 | 26.33 | 18.23 | 54.61 | 26.04 | 11.82 | 1 | 22.8
2018-04-18 17:00 | 13099.0883 | 115.514 | 19.35 | 28.2 | 19.18 | 39.65 | 19.02 | 10.41 | 2 | 18.68
2018-04-18 18:00 | 12755.7113 | 23.0645 | 17.62 | 25.98 | 18.35 | 33.41 | 14.37 | 10.25 | 8.11 | 3.91
2018-04-18 19:00 | 12799.3042 | -0.048233 | 18.38 | 22.14 | 20.01 | 29.13 | 7.47 | 10.25 | 5 | 3.91
2018-04-18 20:00 | 14069.4291 | -0.048233 | 21.66 | 22.45 | 21.98 | 30.8 | 20 | 10.25 | 3.82 | 20
2018-04-18 21:00 | 13451.1991 | -0.048233 | 19.33 | 21.84 | 18.75 | 30 | 7.3 | 0.99 | 14.11 | 6.7
2018-04-18 22:00 | 12914.2041 | -0.048233 | 18.2 | 18.2 | 15.87 | 21.9 | 4.79 | 0.12 | 25 | 4.2
2018-04-18 23:00 | 11380.0042 | -0.048233 | 16.67 | 16.67 | 13.24 | 19.9 | 5.5 | 0.01 | 19.76 | 4.11
2018-04-19 | 11384.7542 | -0.048233 | 13.74 | 15.5 | 16.88 | 17.48 | 4 | 0.01 | 15 | 3.91
2018-04-19 01:00 | 11222.3042 | -0.048233 | 11.94 | 12.71 | 17.75 | 15.75 | 3.5 | 0.01 | 5 | 3
2018-04-19 02:00 | 10978.1542 | -0.048233 | 11.57 | 11.57 | 15.03 | 14.79 | 3.79 | 1.91 | 5 | 3
2018-04-19 03:00 | 10917.3542 | -0.048233 | 11.97 | 11.97 | 13.68 | 15.5 | 3.79 | 1 | 3.5 | 3
2018-04-19 04:00 | 11232.7542 | -0.048233 | 12.04 | 12.04 | 14.98 | 16.58 | 3.79 | 1 | 4.11 | 3
2018-04-19 05:00 | 13601.0091 | -0.048233 | 12.81 | 12.81 | 16.16 | 19.39 | 4 | 2 | 56.6962 | 24
2018-04-19 06:00 | 15675.1391 | -0.048233 | 9.73 | 15.22 | 15.26 | 23.64 | 4.79 | 9.79 | 113.2734 | 51.59
2018-04-19 07:00 | 16716.0287 | 187.577 | 15.44 | 18.07 | 16.02 | 22.34 | 4.01 | 7 | 1.45 | 4.11
2018-04-19 08:00 | 17343.7105 | 509.536 | 17 | 17.89 | 18.55 | 22.33 | 4.76 | 7.32 | 24.46 | 5.06
2018-04-19 09:00 | 18188.7433 | 861.515 | 18.66 | 18.67 | 18.54 | 25.16 | 5.3 | 9 | 32.25 | 5.2
2018-04-19 10:00 | 16308.4885 | 1104.83 | 18.86 | 18.94 | 19.64 | 27.11 | 7.09 | 0.99 | 1 | 3.38
2018-04-19 11:00 | 16227.5675 | 1158.65 | 18.96 | 20.76 | 19.38 | 32.22 | 9.02 | 0.99 | 1 | 4
2018-04-19 12:00 | 18381.9507 | 1158.65 | 59.86 | 20.73 | 18.83 | 31.61 | 6.61 | 0.99 | 1 | 3.17
2018-04-19 13:00 | 16519.2175 | 1158.65 | 101.79 | 25.53 | 18.47 | 33.76 | 16.02 | 10.25 | 1.37 | 4.46
2018-04-19 14:00 | 16054.449 | 1093.42 | 30.95 | 30.95 | 18.48 | 40.4 | 21.73 | 11.22 | 2 | 19.8
2018-04-19 15:00 | 16412.3713 | 873.75 | 29.09 | 26.84 | 18.51 | 43.01 | 25.36 | 15.96 | 2 | 23.34
2018-04-19 16:00 | 13992.5699 | 584.021 | 46.6 | 33.4 | 17.58 | 46.05 | 27.83 | 18.71 | 1.11 | 25.21
2018-04-19 17:00 | 14904.2203 | 251.223 | 56.22 | 31.89 | 19.45 | 36.75 | 27.81 | 19.51 | 2 | 25.68
2018-04-19 18:00 | 13010.8397 | 24.6207 | 22.65 | 24.33 | 20 | 28.83 | 33.97 | 24.86 | 3.5 | 33.97
2018-04-19 19:00 | 14299.4191 | -0.048233 | 20.46 | 21.38 | 21.65 | 27.14 | 23.45 | 18.74 | 4.91 | 21.74
2018-04-19 20:00 | 12917.1042 | -0.048233 | 48.61 | 22.9 | 21.92 | 27.37 | 29.62 | 23.22 | 2.31 | 29.62
2018-04-19 21:00 | 12865.8042 | -0.048233 | 19.05 | 19.94 | 19.94 | 24.72 | 19.18 | 10.23 | 11.33 | 19.18
2018-04-19 22:00 | 12562.7542 | -0.048233 | 17.36 | 18.91 | 18.85 | 21.65 | 5.5 | 0.01 | 18.11 | 13
2018-04-19 23:00 | 13553.5341 | -0.048233 | 14.27 | 15.79 | 17 | 18.77 | 5.5 | 0.01 | 15.12 | 31.02
2018-04-20 | 11790.4042 | -0.048233 | 13.28 | 13.28 | 13.75 | 17.86 | 4 | 0.01 | 21.24 | 4
2018-04-20 01:00 | 12953.2391 | -0.048233 | 12.18 | 12.18 | 11.66 | 14.85 | 4 | 0.01 | 8.11 | 2.11
2018-04-20 02:00 | 12790.7691 | -0.048233 | 11.15 | 11.15 | 10.74 | 13.36 | 3.79 | 1.69 | 2.9 | 1.26
2018-04-20 03:00 | 11711.5542 | -0.048233 | 11.52 | 11.52 | 10.79 | 13.8 | 3.79 | 1.37 | 2.26 | 1.41
2018-04-20 04:00 | 13280.2891 | -0.048233 | 11.76 | 11.76 | 11.98 | 14.63 | 3.82 | 1.48 | 6 | 3
2018-04-20 05:00 | 12816.4042 | -0.048233 | 13.18 | 13.18 | 15.52 | 18.57 | 4 | 2.5 | 10 | 4
2018-04-20 06:00 | 16316.5791 | -0.048233 | 16.26 | 16.26 | 18.98 | 22.33 | 8.16 | 7.41 | 10 | 50.9
2018-04-20 07:00 | 17585.162 | 286.4 | 17.99 | 17.99 | 21.14 | 20.96 | 6.49 | 6.51 | 2.11 | 3
2018-04-20 08:00 | 18255.4647 | 585.758 | 18.93 | 19.13 | 21.64 | 21.94 | 7.31 | 7 | 3.5 | 7
2018-04-20 09:00 | 17260.0228 | 873.445 | 19.28 | 19.28 | 19.96 | 22.94 | 8.4 | 8.98 | 3.5 | 3.05
2018-04-20 10:00 | 19045.398 | 1074.51 | 19.65 | 19.65 | 21.23 | 27.08 | 5.19 | 0.99 | 1 | 3.1
2018-04-20 11:00 | 16731.0675 | 1158.65 | 22.14 | 22.58 | 20.95 | 28.2 | 5.85 | 0.99 | 1 | 4.22
2018-04-20 12:00 | 19002.2908 | 1158.65 | 23.09 | 23.09 | 20.54 | 33.68 | 7.41 | 0.99 | 1 | 5.99
2018-04-20 13:00 | 17128.1675 | 1158.65 | 23.21 | 24.57 | 20.36 | 38.57 | 13.35 | 8.15 | 1 | 4.62
2018-04-20 14:00 | 17936.8779 | 1078.78 | 22.94 | 26.13 | 20.2 | 47.93 | 16.99 | 1.21 | 2 | 12.07
2018-04-20 15:00 | 16829.725 | 864.346 | 30.09 | 30.09 | 19.27 | 59.68 | 27.3 | 11.82 | 1.06 | 18.47
2018-04-20 16:00 | 15999.478 | 582.382 | 145.14 | 145.14 | 20.03 | 66.24 | 34.38 | 20.85 | 2 | 26.77
2018-04-20 17:00 | 15148.2091 | 250.492 | 52.95 | 32.55 | 19.89 | 40.98 | 15.07 | 10.25 | 2 | 12.66
2018-04-20 18:00 | 14311.2121 | 25.13 | 62.66 | 62.66 | 19.94 | 35.72 | 9.76 | 1.51 | 3.5 | 5.01
2018-04-20 19:00 | 13080.5042 | -0.048233 | 22.32 | 23.63 | 23.12 | 31.19 | 7.41 | 0.99 | 4.11 | 4.63
2018-04-20 20:00 | 14772.0591 | -0.048233 | 22.49 | 22.49 | 22.4 | 29.39 | 7.83 | 9.21 | 7.24 | 11.62
2018-04-20 21:00 | 14396.4791 | -0.048233 | 21.23 | 21.99 | 20.38 | 28.92 | 7.02 | 1.33 | 8.11 | 6.42
2018-04-20 22:00 | 12486.7542 | -0.048233 | 15.66 | 20.54 | 18.25 | 23.26 | 5.48 | 0.12 | 25 | 5.5
2018-04-20 23:00 | 12044.0542 | -0.048233 | 13.91 | 19.73 | 15.55 | 20.16 | 4 | 0.01 | 13.89 | 4
2018-04-21 | 11749.5542 | -0.048233 | 11.67 | 19.28 | 16.09 | 21.67 | 4.51 | 0.01 | 21.93 | 12.5
2018-04-21 01:00 | 12819.2541 | -0.048233 | 11.06 | 18.56 | 14.09 | 20.95 | 3.84 | 0.12 | 7.21 | 3
2018-04-21 02:00 | 12598.7591 | -0.048233 | 6.68 | 19.23 | 12.31 | 20.1 | 3.51 | 1.86 | 6.56 | 2.87
2018-04-21 03:00 | 12518.5791 | -0.048233 | 11.64 | 19.06 | 12.48 | 19.71 | 3.51 | 1.58 | 2.31 | 2.61
2018-04-21 04:00 | 11868.3042 | -0.048233 | 12.4 | 18.85 | 14.85 | 19.99 | 3.51 | 1.56 | 3.5 | 3.31
2018-04-21 05:00 | 14203.4141 | -0.048233 | 14.26 | 19.16 | 16.47 | 21.9 | 4.25 | 2 | 21.2 | 16.6
2018-04-21 06:00 | 16128.7891 | -0.048233 | 17.33 | 19.05 | 18.93 | 23.89 | 9.01 | 9 | 36.7 | 38.47
2018-04-21 07:00 | 17380.6724 | 297.571 | 16.86 | 17.1 | 20.44 | 21.82 | 6 | 6.31 | 1.08 | 4.87
2018-04-21 08:00 | 15902.1193 | 601.073 | 17.35 | 19.97 | 20.34 | 22.17 | 7.28 | 7 | 11.61 | 6.76
2018-04-21 09:00 | 19266.1547 | 892.758 | 17.86 | 19.4 | 21.16 | 27.42 | 7.24 | 9 | 10 | 7.04
2018-04-21 10:00 | 18622.8705 | 1103.01 | 16.84 | 20.11 | 21.13 | 29.47 | 7.75 | 0.99 | 1 | 5.41
2018-04-21 11:00 | 16674.0675 | 1158.65 | 16.72 | 21.4 | 21.15 | 32.8 | 7.4 | 0.99 | 1 | 6.4
2018-04-21 12:00 | 17972.7175 | 1158.65 | 16.16 | 25.32 | 21.13 | 36.53 | 7.31 | 0.99 | 1 | 7.31
2018-04-21 13:00 | 18259.5707 | 1158.65 | 16.19 | 30.41 | 21.14 | 35.88 | 7.61 | 0.99 | 2 | 2.11
2018-04-21 14:00 | 15286.773 | 1016.34 | 76.86 | 76.86 | 21.01 | 42.35 | 14.43 | 1 | 1.16 | 4.72
2018-04-21 15:00 | 15803.8747 | 683.976 | 41.82 | 41.82 | 21.05 | 52.08 | 23.96 | 1.57 | 1.65 | 14.55
2018-04-21 16:00 | 13703.883 | 466.14 | 48.5 | 48.5 | 20.53 | 53.03 | 25 | 7.59 | 1.34 | 16.09
2018-04-21 17:00 | 14480.3339 | 170.435 | 94.68 | 31.28 | 20.62 | 38.45 | 13.85 | 1.62 | 2 | 5.6
2018-04-21 18:00 | 12665.1442 | 27.7307 | 60.75 | 60.75 | 20.92 | 31.42 | 7 | 1 | 8.61 | 3.77
2018-04-21 19:00 | 12489.6042 | -0.048233 | 18.23 | 22.35 | 21.64 | 27.73 | 6 | 0.99 | 3 | 3.34
2018-04-21 20:00 | 13892.1891 | -0.048233 | 22.11 | 24.33 | 21.77 | 28.16 | 15.95 | 10.25 | 2.31 | 15.95
2018-04-21 21:00 | 13728.6641 | -0.048233 | 20.48 | 20.48 | 19.68 | 24.56 | 4.34 | 0.99 | 9 | 4
2018-04-21 22:00 | 11808.4542 | -0.048233 | 17.21 | 19.02 | 17.62 | 24.84 | 5.5 | 0.12 | 37.48 | 5.35
2018-04-21 23:00 | 12700.0391 | -0.048233 | 16.05 | 18.16 | 16.5 | 21.03 | 4 | 0.01 | 17.04 | 3
2018-04-22 | 11320.1542 | -0.048233 | 13.95 | 17.18 | 15.92 | 19.36 | 5 | 0.01 | 20 | 12
2018-04-22 01:00 | 11255.5542 | -0.048233 | 13.52 | 16.79 | 15.84 | 17.11 | 4.79 | 0.01 | 13.18 | 1.21
2018-04-22 02:00 | 11043.7042 | -0.048233 | 0 | 14.24 | 15.55 | 14.61 | 3.5 | 2 | 11.64 | 1
2018-04-22 03:00 | 12018.5091 | -0.048233 | 7.83 | 12.67 | 14.69 | 14.6 | 3.5 | 1.9 | 3 | 1.11
2018-04-22 04:00 | 10852.7542 | -0.048233 | 10.9 | 10.9 | 15.28 | 15.65 | 3 | 1.51 | 4.53 | 3
2018-04-22 05:00 | 10886.0042 | -0.048233 | 12.53 | 12.53 | 16.03 | 17.98 | 5.25 | 1.58 | 20 | 19.5
2018-04-22 06:00 | 12064.0932 | 40.1594 | 14.86 | 14.86 | 17.48 | 19.9 | 6 | 7.5 | 20 | 89.5262
2018-04-22 07:00 | 12208.6837 | 304.212 | 17.85 | 18.48 | 18.94 | 21.41 | 4.15 | 6 | 2 | 4.15
2018-04-22 08:00 | 12699.2692 | 620.222 | 18.66 | 19.08 | 18.95 | 24.06 | 5.18 | 7.5 | 9 | 5.18
2018-04-22 09:00 | 11754.0583 | 887.693 | 19.67 | 21.44 | 20.06 | 22.6 | 5.11 | 8.27 | 9 | 5.11
2018-04-22 10:00 | 13406.5074 | 1083.59 | 824.0211 | 556.41 | 21.67 | 26.96 | 6.72 | 1.42 | 1.08 | 4.93
2018-04-22 11:00 | 12269.8675 | 1158.65 | 309.1257 | 264.8 | 20.85 | 28.49 | 6.36 | 1.42 | 0.51 | 6.36
2018-04-22 12:00 | 13677.7057 | 1158.65 | 39.53 | 39.53 | 19.66 | 31.86 | 14.41 | 1.4 | 1 | 10.41
2018-04-22 13:00 | 13879.2107 | 1158.65 | 44.57 | 39.61 | 18.44 | 33.81 | 15.38 | 1.39 | 1 | 10.75
2018-04-22 14:00 | 13787.3413 | 1066.57 | 1332.8311 | 1065.22 | 18.27 | 32.47 | 19.12 | 1.33 | 0.61 | 17.4
2018-04-22 15:00 | 13568.1419 | 870.798 | 42.94 | 38.62 | 18.23 | 32.2 | 24.78 | 2 | 1 | 19.22
2018-04-22 16:00 | 12030.666 | 588.859 | 33.41 | 27.27 | 19.4 | 31.05 | 31.43 | 1.07 | 1 | 22.48
2018-04-22 17:00 | 13000.5498 | 250.796 | 23.09 | 24.7 | 19.61 | 27.15 | 24.63 | 1.17 | 1 | 15.6
2018-04-22 18:00 | 12951.4884 | 26.2923 | 23.03 | 23.03 | 19.18 | 24.26 | 17 | 0.99 | 2.31 | 16.75
2018-04-22 19:00 | 12678.9391 | -0.048233 | 20.09 | 20.94 | 19.92 | 25 | 8.26 | 0.99 | 2.25 | 5
2018-04-22 20:00 | 12382.4841 | -0.048233 | 18.3 | 20.25 | 21.95 | 29.88 | 15.72 | 1.22 | 2.11 | 15.72
2018-04-22 21:00 | 12037.4991 | -0.048233 | 16.83 | 20.69 | 18.74 | 26.2 | 8 | 0.99 | 20 | 5.96
2018-04-22 22:00 | 11312.7141 | -0.048233 | 15.47 | 21.91 | 17.08 | 22.25 | 7.11 | 0.01 | 57.7062 | 10
2018-04-22 23:00 | 10840.0741 | -0.048233 | 13.97 | 20.41 | 17.64 | 20.48 | 6 | 0.01 | 25 | 6
2018-04-23 | 9354.6042 | -0.048233 | 12.2 | 19.71 | 18.25 | 20.59 | 4.15 | 0.12 | 8.11 | 15
2018-04-23 01:00 | 9103.8042 | -0.048233 | 12.84 | 18.43 | 17.67 | 19.95 | 3.06 | 0.12 | 3.5 | 2.43
2018-04-23 02:00 | 9964.4241 | -0.048233 | 10.99 | 18.26 | 17.05 | 18.66 | 3 | 1 | 3.74 | 2.11
2018-04-23 03:00 | 9824.1091 | -0.048233 | 2.41 | 18.54 | 17.24 | 18.5 | 3 | 1.14 | 3.5 | 2.11
2018-04-23 04:00 | 9816.7241 | -0.048233 | -0.59 | 18.43 | 16.54 | 18.79 | 3.51 | 1.56 | 2.7 | 3.51
2018-04-23 05:00 | 9772.4141 | -0.048233 | -0.73 | 18.76 | 17.16 | 19.49 | 25 | 1.65 | 9.29 | 25
2018-04-23 06:00 | 8869.9672 | 57.8076 | -0.13 | 18.78 | 17 | 20.49 | 25.2 | 7.47 | 10.53 | 25
2018-04-23 07:00 | 10078.9552 | 288.512 | 6.92 | 17.82 | 17.55 | 20.7 | 4.2 | 3.6 | 2 | 2.29
2018-04-23 08:00 | 9215.93 | 607.979 | 11.7 | 18.62 | 17.92 | 23.21 | 5.68 | 6.98 | 2.11 | 5.48
2018-04-23 09:00 | 10422.8525 | 893.481 | 13.1 | 19.55 | 19.49 | 24.13 | 6.73 | 5.01 | 2 | 3.7
2018-04-23 10:00 | 10483.4928 | 1087.96 | 12.99 | 19.3 | 19.7 | 23.44 | 7.11 | 0.99 | 2 | 3.2
2018-04-23 11:00 | 10468.3957 | 1158.65 | 12.38 | 20.29 | 18.55 | 23.37 | 6.92 | 0.99 | 1.25 | 3.23
2018-04-23 12:00 | 10609.7657 | 1158.65 | 13.25 | 20.49 | 18.65 | 23.99 | 15.68 | 12.98 | 2 | 3.1
2018-04-23 13:00 | 10706.8257 | 1158.65 | 16.72 | 20.53 | 17.95 | 26.33 | 19.26 | 16.21 | 2.09 | 18.62
2018-04-23 14:00 | 10867.7765 | 1085.21 | 20.81 | 20.81 | 17.2 | 27.06 | 27.9 | 23.7 | 2 | 25.92
2018-04-23 15:00 | 9724.2959 | 861.101 | 18.18 | 22.08 | 17.53 | 27.34 | 29.72 | 24.12 | 2 | 25.56
2018-04-23 16:00 | 9688.651 | 589.58 | 23.89 | 23.89 | 17.86 | 27.97 | 27.62 | 22.02 | 2 | 24.53
2018-04-23 17:00 | 9481.5216 | 253.549 | 23.24 | 26.84 | 18.44 | 28.44 | 21.4 | 17.8 | 2 | 20.23
2018-04-23 18:00 | 10487.5626 | 24.8176 | 14.84 | 26.89 | 18.71 | 26.92 | 12.38 | 1.24 | 4.32 | 3.35
2018-04-23 19:00 | 10607.9741 | -0.048233 | 14.74 | 26.48 | 19.28 | 26.95 | 13.44 | 0.99 | 3.36 | 3.89
2018-04-23 20:00 | 10712.4191 | -0.048233 | 13.37 | 28.55 | 29.03 | 34.4 | 17.44 | 1.23 | 2.25 | 12.81
2018-04-23 21:00 | 9598.7542 | -0.048233 | 12.3 | 23.7 | 20.2 | 26.25 | 6.5 | 0.99 | 9.49 | 10.4
2018-04-23 22:00 | 10503.5291 | -0.048233 | 11.32 | 31.31 | 18.05 | 22.04 | 6.5 | 0.01 | 52.7062 | 17.03
2018-04-23 23:00 | 9248.2042 | -0.048233 | 11.52 | 19.76 | 17.89 | 19.87 | 6.07 | 0.01 | 30 | 17
2018-04-24 | 10132.1691 | -0.048233 | 9.36 | 17.63 | 16.53 | 19.12 | 20.75 | 0.01 | 25 | 3.59
2018-04-24 01:00 | 9961.2591 | -0.048233 | 0 | 12.2 | 16.78 | 15.71 | 20.75 | 0.01 | 11.3 | 2.61
2018-04-24 02:00 | 9922.2241 | -0.048233 | -0.69 | 7.62 | 15.25 | 13.31 | 20.75 | 1.57 | 8.61 | 2.42
2018-04-24 03:00 | 9934.8841 | -0.048233 | -0.78 | 6.77 | 15.25 | 12.32 | 20.75 | 1.58 | 3 | 2.11
2018-04-24 04:00 | 9466.7042 | -0.048233 | -0.99 | 11.17 | 16.82 | 14.88 | 20.75 | 1.95 | 8 | 3.45
2018-04-24 05:00 | 11393.9491 | -0.048233 | -1.16 | 11.97 | 16.92 | 18.83 | 30 | 2 | 53.9862 | 25.59
2018-04-24 06:00 | 13635.5753 | 72.7159 | -0.75 | 16.3 | 17.13 | 23.07 | 30 | 11 | 25 | 29.8
2018-04-24 07:00 | 13523.3716 | 309.128 | -0.53 | 19.27 | 16.27 | 25.63 | 4.72 | 9 | 2.94 | 3.53
2018-04-24 08:00 | 15808.503 | 631.363 | 12.02 | 19.24 | 18.52 | 24.35 | 18.11 | 9 | 3.5 | 10.8
2018-04-24 09:00 | 17305.4003 | 908.223 | 11.7 | 19.5 | 18.61 | 24.42 | 6 | 7.65 | 3.01 | 5.28
2018-04-24 10:00 | 17339.6107 | 1099.65 | 12.26 | 19.35 | 18.51 | 25.66 | 20 | 1.22 | 2 | 5.87
2018-04-24 11:00 | 15054.3175 | 1158.65 | 12.89 | 19.63 | 18.59 | 25.79 | 6.88 | 1.25 | 1.29 | 4
2018-04-24 12:00 | 18560.2458 | 1158.65 | 13.76 | 20.42 | 18.28 | 31.28 | 7.47 | 1.25 | 2 | 5.18
2018-04-24 13:00 | 16433.3657 | 1158.65 | 15.29 | 21.11 | 18.27 | 33.78 | 10 | 1.25 | 2.11 | 5.59
2018-04-24 14:00 | 13892.344 | 1063.52 | 15.65 | 24.71 | 18.36 | 36.31 | 20 | 10.71 | 1.62 | 15.21
2018-04-24 15:00 | 14509.5595 | 850.137 | 15.29 | 22.41 | 17.55 | 40.18 | 17.78 | 12.18 | 2 | 17.78
2018-04-24 16:00 | 12494.5805 | 577.19 | 14.92 | 36.28 | 18.6 | 42.2 | 21.94 | 7.08 | 2 | 15
2018-04-24 17:00 | 11982.3842 | 246.036 | 14.4 | 26.13 | 19.65 | 34.35 | 16.42 | 1.75 | 1 | 11.42
2018-04-24 18:00 | 12863.0711 | 26.4845 | 13.75 | 24.56 | 20.31 | 29.9 | 16.4 | 1.46 | 12.03 | 6.4
2018-04-24 19:00 | 11495.9042 | -0.048233 | 13.64 | 22.22 | 22 | 28.79 | 6.62 | 1.53 | 2 | 5
2018-04-24 20:00 | 11669.7542 | -0.048233 | 17.3 | 27.24 | 22.86 | 31.64 | 17.69 | 1.5 | 20 | 17.49
2018-04-24 21:00 | 11710.6042 | -0.048233 | 15.29 | 22.24 | 20.95 | 24.46 | 8 | 1 | 20 | 12.62
2018-04-24 22:00 | 11067.4542 | -0.048233 | 15.02 | 21.05 | 16.25 | 19.31 | 28.58 | 0.01 | 102.7434 | 28.91
2018-04-24 23:00 | 10620.0042 | -0.048233 | 13.21 | 14.79 | 16.16 | 16.63 | 20.3 | 0.01 | 24.87 | 16.8
2018-04-25 | 11733.6591 | -0.048233 | 0.04 | 14.32 | 16.04 | 14.05 | 23.01 | 0.01 | 25 | 15.41
2018-04-25 01:00 | 11736.8241 | -0.048233 | 0 | 12.27 | 15.34 | 12.41 | 30 | 0.01 | 12.38 | 2.61
2018-04-25 02:00 | 11714.6691 | -0.048233 | -0.01 | 10.73 | 15.17 | 10.91 | 30 | 1.95 | 11.4 | 2.01
2018-04-25 03:00 | 10505.0542 | -0.048233 | 0 | 11.25 | 14.88 | 11.52 | 25.75 | 1.95 | 11 | 2.11
2018-04-25 04:00 | 11288.8042 | -0.048233 | 0.33 | 13.63 | 16.29 | 13.34 | 25.75 | 2 | 11 | 3.5
2018-04-25 05:00 | 13770.8641 | -0.048233 | 6.2 | 12.85 | 18.27 | 18.09 | 25 | 1.45 | 20 | 87.1162
2018-04-25 06:00 | 16030.5862 | 64.8684 | 4.91 | 17.42 | 19.19 | 20.22 | 22 | 11 | 20 | 29
2018-04-25 07:00 | 15614.3672 | 296.176 | 12.54 | 18.53 | 21 | 20.73 | 3.5 | 6 | 3.46 | 3.5
2018-04-25 08:00 | 16150.5966 | 577.628 | 90.81 | 18.77 | 21.04 | 22.07 | 4 | 7.5 | 3.5 | 4
2018-04-25 09:00 | 17169.2835 | 870.93 | 14.48 | 20.65 | 21.27 | 25.14 | 4.1 | 11 | 11.3 | 4.1
2018-04-25 10:00 | 19833.462 | 1052.49 | 16.16 | 22.65 | 21.55 | 27.67 | 5.61 | 1.42 | 2 | 4.49
2018-04-25 11:00 | 16741.2914 | 653.412 | 18.78 | 23.88 | 21.14 | 31.21 | 6.6 | 1.35 | 2 | 5.3
2018-04-25 12:00 | 19221.6063 | 506.532 | 19.16 | 28.01 | 20.15 | 35.05 | 5.31 | 1.52 | 1 | 4.41
2018-04-25 13:00 | 19314.1245 | 461.227 | 20.51 | 29.83 | 19.16 | 38.98 | 15.18 | 10.9 | 1 | 14.4
2018-04-25 14:00 | 18905.7097 | 408.104 | 22.31 | 26.93 | 18.81 | 45.3 | 31.22 | 8.99 | 1.09 | 16.54
2018-04-25 15:00 | 18455.6172 | 337.476 | 44.83 | 30.68 | 18.79 | 53.03 | 34.45 | 8.99 | 1 | 23.43
2018-04-25 16:00 | 14411.3575 | 250.85 | 37.85 | 31.6 | 18.87 | 59.24 | 44.14 | 23 | 1 | 34.73
2018-04-25 17:00 | 13995.5843 | 130.194 | 33.11 | 33.11 | 19.54 | 51.19 | 30.25 | 14.79 | 1.1 | 19.29
2018-04-25 18:00 | 13539.5025 | 17.1079 | 19.8 | 28.01 | 20.1 | 39.33 | 16.58 | 11.82 | 1.18 | 15.32
2018-04-25 19:00 | 13411.1042 | -0.048233 | 18.56 | 28.25 | 20.71 | 33.31 | 7.53 | 1.5 | 2.86 | 3
2018-04-25 20:00 | 14976.7291 | -0.048233 | 19.3 | 31.33 | 21.86 | 37.09 | 13.03 | 6 | 2.28 | 10
2018-04-25 21:00 | 14679.2191 | -0.048233 | 61.95 | 61.95 | 19.64 | 34.7 | 6.51 | 1.42 | 8.61 | 5.98
2018-04-25 22:00 | 12798.3542 | -0.048233 | 12.18 | 30.36 | 18.18 | 26.53 | 6.24 | 0.3 | 22 | 6.24
2018-04-25 23:00 | 12427.8542 | -0.048233 | 10.32 | 26.56 | 17.83 | 21.46 | 6 | 0.25 | 22 | 5
2018-04-26 | 12259.7042 | -0.048233 | 9.55 | 21.89 | 17.61 | 23.43 | 3.11 | 0.12 | 17.57 | 3.11
2018-04-26 01:00 | 13317.2141 | -0.048233 | 10.83 | 20.73 | 16.11 | 21.15 | 3.11 | 0.01 | 8.11 | 2.21
2018-04-26 02:00 | 11742.9042 | -0.048233 | 9.94 | 20.71 | 15.52 | 20.55 | 2.95 | 1.95 | 2.66 | 2
2018-04-26 03:00 | 11742.9042 | -0.048233 | 8.06 | 19.79 | 15.62 | 20.33 | 2.95 | 1.95 | 2.11 | 2
2018-04-26 04:00 | 13910.1241 | -0.048233 | 8.47 | 18.26 | 15.63 | 21.25 | 3 | 1.53 | 3.5 | 2.61
2018-04-26 05:00 | 13421.5542 | -0.048233 | 10.09 | 21.1 | 18.32 | 25.28 | 25 | 1.41 | 11 | 4
2018-04-26 06:00 | 15171.6115 | 34.1174 | 11.13 | 23.41 | 20 | 26.74 | 4 | 16.8 | 20 | 18
2018-04-26 07:00 | 16613.9182 | 145.335 | 13.19 | 22.3 | 19.48 | 26.85 | 3.5 | 7.79 | 3.46 | 3.01
2018-04-26 08:00 | 18559.3775 | 192.827 | 16.48 | 21.38 | 20.38 | 26.15 | 3.5 | 11.43 | 3.98 | 3.5
2018-04-26 09:00 | 17606.273 | 149.919 | 14.51 | 21.07 | 21.36 | 31.13 | 3.5 | 10.95 | 8.45 | 3.15
2018-04-26 10:00 | 17914.5385 | 811.409 | 14.86 | 21.82 | 20.67 | 32.23 | 4.14 | 1.33 | 2 | 3.02
2018-04-26 11:00 | 17490.5298 | 893.084 | 17.54 | 20.91 | 21.2 | 39.39 | 6.64 | 9.04 | 1 | 4
2018-04-26 12:00 | 18260.2872 | 919.355 | 34.98 | 20.88 | 20.81 | 45.8 | 7.11 | 1 | 1 | 5.23
2018-04-26 13:00 | 18464.541 | 889.359 | 22.28 | 24.05 | 20.36 | 58.08 | 9.16 | 2.48 | 1 | 2.48
2018-04-26 14:00 | 19456.6592 | 789.331 | 61.82 | 61.82 | 19.68 | 77.5 | 18.89 | 8 | 1 | 15.19
2018-04-26 15:00 | 17008.2841 | 715.457 | 31.87 | 31.87 | 19.99 | 91.77 | 34.36 | 9.22 | 1 | 19.11
2018-04-26 16:00 | 18044.6061 | 461.892 | 92.24 | 92.24 | 19.65 | 100.66 | 39.66 | 12 | 1 | 24.03
2018-04-26 17:00 | 15878.94 | 224.128 | 36.99 | 36.99 | 20.49 | 72.18 | 25.24 | 12 | 1 | 22.51
2018-04-26 18:00 | 15233.1438 | 25.9989 | 37 | 37 | 20.31 | 56.02 | 18.52 | 12.28 | 2.11 | 15.28
2018-04-26 19:00 | 14965.1241 | -0.048233 | 41.25 | 41.25 | 21.84 | 45.55 | 17.16 | 11.98 | 2.92 | 14.27
2018-04-26 20:00 | 13390.2042 | -0.048233 | 42.66 | 42.66 | 22.57 | 54.05 | 23.7 | 19.46 | 2.31 | 20.08
2018-04-26 21:00 | 13231.5542 | -0.048233 | 18.81 | 31.3 | 19.98 | 34.63 | 7.2 | 1.44 | 2.22 | 7.08
2018-04-26 22:00 | 13596.7891 | -0.048233 | 48.51 | 48.51 | 18.68 | 28.63 | 7.92 | 0.3 | 20 | 9.84
2018-04-26 23:00 | 11684.9542 | -0.048233 | 13.95 | 23.46 | 18.35 | 22.87 | 5.33 | 0.12 | 20 | 3.75
2018-04-27 | 11179.5542 | -0.048233 | 12.25 | 20.86 | 18.35 | 20.23 | 3.45 | 0.01 | 11 | 3.45
2018-04-27 01:00 | 10799.5542 | -0.048233 | 13.36 | 20.34 | 17.54 | 18.34 | 3.39 | 0.01 | 4.36 | 2.11
2018-04-27 02:00 | 11595.4541 | -0.048233 | 11.52 | 18.43 | 17.58 | 16.63 | 3.07 | 1.57 | 3 | 1.68
2018-04-27 03:00 | 10369.2042 | -0.048233 | 4.98 | 16.06 | 17.54 | 13.91 | 3 | 1.5 | 2.88 | 1.76
2018-04-27 04:00 | 11211.8542 | -0.048233 | 2.31 | 2.31 | 17.26 | 14.65 | 3.15 | 1.57 | 2.61 | 2.61
2018-04-27 05:00 | 13379.4591 | -0.048233 | 4.84 | 4.84 | 18.49 | 18.69 | 25 | 2.25 | 112.7434 | 5.35
2018-04-27 06:00 | 13528.1723 | 33.1814 | 11.65 | 16.62 | 20.2 | 22.6 | 25.75 | 10 | 112.7434 | 25.04
2018-04-27 07:00 | 14520.2066 | 135.428 | 12.59 | 18.06 | 20.52 | 20.83 | 4.54 | 7.5 | 3.5 | 3.01
2018-04-27 08:00 | 16420.5929 | 134.543 | 13.16 | 18.24 | 20.52 | 20.89 | 5.19 | 13.53 | 2.88 | 15.13
2018-04-27 09:00 | 15202.906 | 150.059 | 14.26 | 18.07 | 20.93 | 21.99 | 5.97 | 10 | 8.61 | 4.65
2018-04-27 10:00 | 17119.3099 | 189.834 | 15.43 | 17.52 | 21.12 | 23.7 | 8.57 | 0.99 | 2 | 4
2018-04-27 11:00 | 16581.5088 | 280.07 | 16.96 | 16.96 | 21.38 | 26.23 | 19.45 | 1 | 1.19 | 4
2018-04-27 12:00 | 15913.2771 | 288.818 | 17.78 | 17.78 | 21.44 | 30 | 12.75 | 1.27 | 1 | 3.1
2018-04-27 13:00 | 15725.8659 | 367.543 | 21.49 | 22.71 | 21.44 | 33.77 | 19.5 | 3.16 | 1 | 12.51
2018-04-27 14:00 | 15972.217 | 900.86 | 19.59 | 19.59 | 21.35 | 39.88 | 37.04 | 6 | 1 | 14.46
2018-04-27 15:00 | 14230.5411 | 590.517 | 21.48 | 21.48 | 21.22 | 54.87 | 82.9541 | 23.39 | 1 | 31.62
2018-04-27 16:00 | 14917.6652 | 408.967 | 79.04 | 21.07 | 21.34 | 57.15 | 117.1641 | 59.3073 | 1 | 91.5962
2018-04-27 17:00 | 12685.9113 | 44.5908 | 56.05 | 21.73 | 21.05 | 48.12 | 114.8741 | 59.3073 | 1 | 93.0862
2018-04-27 18:00 | 12422.009 | 24.7989 | 28.71 | 22.06 | 21.14 | 37.37 | 27.3 | 10.34 | 10.03 | 11.09
2018-04-27 19:00 | 12604.5542 | -0.048233 | 29.84 | 21.37 | 21.38 | 32.27 | 7 | 2.61 | 2.38 | 5.27
2018-04-27 20:00 | 14249.8341 | -0.048233 | 21.75 | 21.79 | 22.21 | 35.74 | 15.52 | 2.03 | 1.35 | 12.7
2018-04-27 21:00 | 12653.9542 | -0.048233 | 19.21 | 22.46 | 20.39 | 28.87 | 6 | 1.25 | 8.61 | 4.17
2018-04-27 22:00 | 12335.7042 | -0.048233 | 15.78 | 20.05 | 19.44 | 24.61 | 6 | 0.01 | 30 | 6.9
2018-04-27 23:00 | 11855.0042 | -0.048233 | 12.95 | 19.63 | 18.8 | 22.44 | 17.88 | 0.01 | 20 | 4.57
2018-04-28 | 13104.1041 | -0.048233 | 12.02 | 18.92 | 18.43 | 19.56 | 8 | 0.01 | 20 | 15
2018-04-28 01:00 | 11741.9542 | -0.048233 | 10.67 | 18.92 | 17.94 | 18.41 | 7.11 | 0.01 | 11 | 2.5
2018-04-28 02:00 | 12933.1941 | -0.048233 | 10.42 | 18.37 | 17.58 | 17.32 | 5 | 2 | 11 | 2.01
2018-04-28 03:00 | 11653.6042 | -0.048233 | 10 | 18.26 | 17.19 | 17.37 | 5 | 2 | 3.5 | 2.11
2018-04-28 04:00 | 12406.0042 | -0.048233 | 9.33 | 19.31 | 17.85 | 18.64 | 6.29 | 2 | 13.7 | 2.61
2018-04-28 05:00 | 14972.5091 | -0.048233 | 9.64 | 21.24 | 18.68 | 21.25 | 25 | 1.25 | 11 | 24.8
2018-04-28 06:00 | 16565.8369 | 65.2151 | 77.39 | 77.39 | 21.17 | 23.08 | 18.75 | 8.92 | 17 | 110.1262
2018-04-28 07:00 | 15596.1129 | 310.961 | 12.49 | 23.12 | 21.54 | 20.6 | 4.34 | 1 | 0.25 | 4
2018-04-28 08:00 | 16130.0719 | 590.023 | 12.95 | 22.59 | 21.55 | 22.65 | 5.45 | 7.01 | 2.74 | 5.45
2018-04-28 09:00 | 17103.1749 | 823.342 | 13.62 | 28.66 | 21.67 | 27.89 | 5.45 | 6 | 2.03 | 4
2018-04-28 10:00 | 17144.1655 | 967.49 | 14.74 | 34.46 | 21.67 | 34.47 | 6 | 0.97 | 0.25 | 5.36
2018-04-28 11:00 | 16778.5238 | 588.604 | 13.61 | 33.28 | 21.65 | 38.02 | 7.26 | 0.99 | 0 | 4.83
2018-04-28 12:00 | 16988.7189 | 318.862 | 14.37 | 34.17 | 21.59 | 44.58 | 7.47 | 1.38 | 0.25 | 5.63
2018-04-28 13:00 | 16714.8225 | 400.55 | 48.64 | 48.64 | 20.73 | 50 | 9.72 | 2.5 | 0.61 | 6.3
2018-04-28 14:00 | 17032.4665 | 224.518 | 345.8357 | 301.51 | 20.49 | 68.67 | 16.87 | 2.5 | 0 | 13.45
2018-04-28 15:00 | 14261.4076 | 389.008 | 355.0357 | 310.71 | 19.99 | 86.88 | 34.58 | 5 | 0 | 22.14
2018-04-28 16:00 | 13936.3784 | 365.872 | 359.9757 | 315.65 | 19.92 | 90.62 | 42.88 | 6 | 0 | 31.7
2018-04-28 17:00 | 15123.2321 | 84.8172 | 67.22 | 67.22 | 19.26 | 64.64 | 25.1 | 6 | 0 | 16.51
2018-04-28 18:00 | 13501.2968 | 28.8914 | 14.51 | 34.26 | 19.42 | 50.28 | 22.63 | 2.2 | 33.17 | 21.63
2018-04-28 19:00 | 15066.4041 | -0.048233 | 13.67 | 32.4 | 21.39 | 42.34 | 20.02 | 1 | 22.48 | 4.17
2018-04-28 20:00 | 14966.1791 | -0.048233 | 14.55 | 32.98 | 22.15 | 42.9 | 29.73 | 2.05 | 13.38 | 28.73
2018-04-28 21:00 | 14698.2091 | -0.048233 | 14.38 | 30.27 | 21.1 | 36.99 | 8.68 | 1.32 | 53.5762 | 10
2018-04-28 22:00 | 14169.6541 | -0.048233 | 15.2 | 29.4 | 19.22 | 33.73 | 18.89 | 0.12 | 20.89 | 18.89
2018-04-28 23:00 | 12329.0542 | -0.048233 | 15.56 | 28.88 | 18.41 | 26.76 | 15.2 | 0.12 | 9.11 | 15
2018-04-29 | 13595.7341 | -0.048233 | 12.43 | 27.25 | 16.81 | 25.68 | 5 | 0.01 | 35.29 | 14.75
2018-04-29 01:00 | 13399.5041 | -0.048233 | 10.52 | 24.74 | 16.19 | 23.16 | 5 | 0.01 | 4.89 | 4
2018-04-29 02:00 | 13301.3891 | -0.048233 | 0.64 | 23.16 | 16.51 | 20.69 | 4.59 | 2 | 4.02 | 3.68
2018-04-29 03:00 | 11836.0042 | -0.048233 | 3.21 | 21.84 | 16.11 | 20.5 | 4.59 | 2 | 3.5 | 2.73
2018-04-29 04:00 | 13414.2741 | -0.048233 | 8.11 | 22.75 | 16.4 | 20.66 | 5 | 2 | 3.5 | 5
2018-04-29 05:00 | 14161.2141 | -0.048233 | 10.63 | 23.34 | 16.73 | 22.21 | 18.75 | 2 | 12 | 18.75
2018-04-29 06:00 | 14641.5325 | 63.2299 | 12.75 | 24.5 | 18.03 | 23.43 | 18.75 | 10 | 25 | 26
2018-04-29 07:00 | 13547.8901 | 308.937 | 14.22 | 23.16 | 19.02 | 23.17 | 4.2 | 1.29 | 3.01 | 4
2018-04-29 08:00 | 15529.4607 | 530.868 | 12.96 | 25.33 | 20.25 | 27.74 | 6.84 | 6.91 | 10 | 6.84
2018-04-29 09:00 | 14531.1126 | 863.908 | 12.27 | 25.39 | 19.3 | 33.09 | 6.21 | 6 | 14.11 | 5.42
2018-04-29 10:00 | 16023.627 | 700.272 | 12.39 | 24.08 | 20.38 | 37.8 | 19.24 | 1.43 | 1.11 | 5.12
2018-04-29 11:00 | 16477.5702 | 1157.55 | 13.35 | 34.19 | 20.08 | 42.3 | 6.59 | 1 | 0 | 5.59
2018-04-29 12:00 | 14653.4175 | 1158.65 | 35.16 | 35.16 | 20.02 | 43.78 | 6.73 | 1 | 0.25 | 5.21
2018-04-29 13:00 | 16051.4557 | 1158.65 | 141.07 | 141.07 | 19.89 | 55.88 | 14.65 | 1.88 | 0.25 | 7.25
2018-04-29 14:00 | 14244.585 | 1020.3 | 111.62 | 111.62 | 18.73 | 63.54 | 19.63 | 1.47 | 0 | 13.96
2018-04-29 15:00 | 15487.0118 | 834.632 | 94.44 | 94.44 | 18.7 | 69.94 | 23.5 | 2.5 | 0 | 18.49
2018-04-29 16:00 | 15166.43 | 558.763 | 71.24 | 71.24 | 18.76 | 62.91 | 24.58 | 2.1 | 0 | 21.18
2018-04-29 17:00 | 14779.15 | 245.673 | 38.22 | 36.26 | 19.1 | 46.48 | 16 | 1 | 0 | 11.33
2018-04-29 18:00 | 12930.4354 | 25.9846 | 36.17 | 36.17 | 18.75 | 42.07 | 9.09 | 1.53 | 2 | 5.31
2018-04-29 19:00 | 12904.7542 | -0.048233 | 15.19 | 33.66 | 20.59 | 38.78 | 7.23 | 0.99 | 3.5 | 5
2018-04-29 20:00 | 14217.1291 | -0.048233 | 17.5 | 26.82 | 21.36 | 34.92 | 25.63 | 1 | 3.5 | 24.63
2018-04-29 21:00 | 12638.7542 | -0.048233 | 15.89 | 30.45 | 18.71 | 31.79 | 5.59 | 1 | 32 | 11.34
2018-04-29 22:00 | 12414.5542 | -0.048233 | 20.22 | 29.07 | 17.79 | 27.81 | 34.74 | 0.25 | 62.7562 | 34.74
2018-04-29 23:00 | 13449.0891 | -0.048233 | 17.55 | 22.11 | 17.53 | 25.47 | 32.81 | 0.01 | 10.57 | 32.81
2018-04-30 | 11754.3042 | -0.048233 | 14.94 | 14.94 | 16 | 26.25 | 27.5 | 0.49 | 31.33 | 27.5
2018-04-30 01:00 | 10313.1542 | -0.048233 | 15.67 | 18.4 | 14.93 | 24.26 | 4 | 0.49 | 10 | 4
2018-04-30 02:00 | 9937.9042 | -0.048233 | 3.1 | 3.1 | 14.93 | 19.11 | 3 | 0.99 | 10 | 3
2018-04-30 03:00 | 9763.1042 | -0.048233 | 0.11 | 0.11 | 14.91 | 14.28 | 3 | 0.99 | 2.61 | 2.75
2018-04-30 04:00 | 9630.1042 | -0.048233 | 2.42 | 2.42 | 14.93 | 12.04 | 3.5 | 1 | 10 | 3.5
2018-04-30 05:00 | 9506.6042 | -0.048233 | 5.05 | 5.05 | 16.04 | 14.75 | 24 | 1.25 | 25 | 50.5
2018-04-30 06:00 | 10682.4501 | 75.5451 | 7.96 | 7.96 | 17.26 | 16.72 | 24.44 | 8.38 | 111.3634 | 91.0562
2018-04-30 07:00 | 9548.2524 | 310.792 | -0.58 | -0.58 | 17.27 | 18.01 | 4 | 1.75 | 1 | 4
2018-04-30 08:00 | 9681.9658 | 601.543 | 8.42 | 8.42 | 18.63 | 20 | 5.13 | 2.61 | 10.03 | 17.05
2018-04-30 09:00 | 10876.8738 | 839.833 | 15.97 | 15.97 | 18.86 | 22.75 | 5.45 | 1 | 12.74 | 5.45
2018-04-30 10:00 | 11099.3786 | 984.738 | 20.71 | 21.25 | 18.88 | 24.1 | 20 | 1 | 1 | 6.07
2018-04-30 11:00 | 11129.8913 | 1074.66 | 18.52 | 18.52 | 18.62 | 25.39 | 21.3 | 1.61 | 0.01 | 12.44
2018-04-30 12:00 | 10985.1812 | 742.494 | 18.09 | 18.09 | 17.74 | 27.57 | 7.6 | 1 | 1 | 7.6
2018-04-30 13:00 | 11461.2351 | 1142.73 | 18.78 | 18.78 | 17.44 | 28.53 | 12.96 | 1 | 1 | 9.69
2018-04-30 14:00 | 11462.2585 | 1044.7 | 18.31 | 18.31 | 16.57 | 31.89 | 14.98 | 0.95 | 2 | 10.72
2018-04-30 15:00 | 10304.9255 | 842.29 | 34.62 | 16.51 | 16.42 | 30.81 | 21.87 | 0.99 | 1.27 | 17.12
2018-04-30 16:00 | 10258.8419 | 566.781 | 346.2957 | 13.11 | 17.01 | 32.61 | 31.34 | 0.99 | 1.8 | 24.82
2018-04-30 17:00 | 9987.2388 | 250.883 | 1775.3811 | 16.31 | 18.08 | 30.13 | 18.36 | 0.99 | 0.71 | 17.3
2018-04-30 18:00 | 11076.415 | 28.9716 | 55.99 | 13.47 | 18.59 | 26.98 | 8 | 0.99 | 2.11 | 5
2018-04-30 19:00 | 10044.3042 | -0.048233 | 19.18 | 19.18 | 19.3 | 34.76 | 15.14 | 0.95 | 3.5 | 10.81
2018-04-30 20:00 | 11291.6141 | -0.048233 | 21.64 | 21.64 | 19.68 | 47.27 | 28.74 | 0.95 | 8.61 | 21.86
2018-04-30 21:00 | 10099.4042 | -0.048233 | 18.39 | 26.31 | 18.67 | 36.77 | 17.28 | 0.95 | 15 | 17.08
2018-04-30 22:00 | 11078.5041 | -0.048233 | 15.39 | 23.47 | 17.93 | 24.52 | 5.39 | 0.5 | 38.6 | 15
2018-04-30 23:00 | 10929.7491 | -0.048233 | 13.73 | 20.53 | 17.58 | 23.98 | 19.11 | 0.5 | 30 | 19.11
2018-05-01 | 10786.2691 | -0.048233 | 14.35 | 22.56 | 17.13 | 21.1 | 16.11 | 0.01 | 62.6962 | 16.11
2018-05-01 01:00 | 10672.3291 | -0.048233 | 13.2 | 19.06 | 14.98 | 20.88 | 5 | 0.01 | 20 | 2.5
2018-05-01 02:00 | 9687.1042 | -0.048233 | 10.57 | 17.72 | 13.94 | 19.29 | 5.59 | 1.22 | 10 | 2.11
2018-05-01 03:00 | 9561.7042 | -0.048233 | 11.34 | 17.26 | 13.48 | 18.29 | 5.59 | 1.62 | 10 | 2.11
2018-05-01 04:00 | 11427.7091 | -0.048233 | 7.63 | 17.17 | 13.96 | 19.81 | 5.59 | 1.22 | 8.68 | 2.61
2018-05-01 05:00 | 12355.0541 | -0.048233 | -0.41 | 16.68 | 14.64 | 20.97 | 7.85 | 1.54 | 117.9034 | 22.5
2018-05-01 06:00 | 14192.5859 | 57.6881 | -0.57 | 18.85 | 14.96 | 22.98 | 8.25 | 1.32 | 23.9 | 22.5
2018-05-01 07:00 | 14527.9472 | 288.576 | -0.39 | 18.5 | 16.02 | 21.97 | 4 | 1.89 | 1.66 | 4
2018-05-01 08:00 | 16688.6177 | 241.595 | 3.14 | 19.27 | 18 | 22.71 | 4.45 | 2.25 | 1.25 | 4.45
2018-05-01 09:00 | 15989.2344 | 127.773 | 8.22 | 19.87 | 18.13 | 23.01 | 5.25 | 2.25 | 0.25 | 3.93
2018-05-01 10:00 | 17480.5398 | 160.232 | 13 | 20.06 | 18.73 | 23.35 | 4.27 | 1 | 2.11 | 4.07
2018-05-01 11:00 | 14667.7064 | 171.691 | 13.8 | 20.26 | 19.09 | 26.61 | 5.35 | 1 | 0.61 | 5.15
2018-05-01 12:00 | 16411.5399 | 182.962 | 14.28 | 20.82 | 18.65 | 28.67 | 6.34 | 1.81 | 2 | 6.51
2018-05-01 13:00 | 14412.1033 | 172.635 | 15.84 | 23.2 | 18.62 | 37.49 | 7.64 | 1 | 1.5 | 6.97
2018-05-01 14:00 | 13609.6202 | 155.916 | 16.18 | 23.35 | 18.46 | 42.14 | 15.41 | 2.01 | 2 | 13.57
2018-05-01 15:00 | 14395.5151 | 126.038 | 52.23 | 25.23 | 17.89 | 57.55 | 23.95 | 9.18 | 2 | 22.15
2018-05-01 16:00 | 13901.179 | 135.473 | 58.48 | 35.58 | 18.22 | 57.15 | 25.33 | 10.85 | 2.5 | 24.32
2018-05-01 17:00 | 12324.1253 | 69.7635 | 52.02 | 52.02 | 18.52 | 48.93 | 19.46 | 2.01 | 2.99 | 17.37
2018-05-01 18:00 | 12045.3569 | 13.3231 | 15.64 | 29.2 | 18.56 | 31.72 | 8.25 | 2.25 | 22.56 | 5.25
2018-05-01 19:00 | 12096.3042 | -0.048233 | 14.94 | 29.37 | 19.46 | 29.71 | 6.93 | 1.58 | 2 | 5
2018-05-01 20:00 | 13443.8141 | -0.048233 | 17.53 | 25.26 | 21.31 | 28.62 | 8.25 | 1 | 1.7 | 7.66
2018-05-01 21:00 | 13223.3191 | -0.048233 | 16.2 | 23.02 | 19.18 | 27.56 | 6.97 | 1.52 | 10.03 | 6.97
2018-05-01 22:00 | 12780.2191 | -0.048233 | 18.75 | 20.22 | 17.49 | 24.31 | 16.89 | 0.01 | 17.87 | 16.89
2018-05-01 23:00 | 11088.3542 | -0.048233 | 14.04 | 19.19 | 16 | 20.8 | 19.79 | 0.01 | 25 | 32.3
2018-05-02 | 12239.0041 | -0.048233 | 13.87 | 18.09 | 15.69 | 17.52 | 7.25 | 0.01 | 62.6962 | 7.05
2018-05-02 01:00 | 10819.5042 | -0.048233 | 13.83 | 17.62 | 15.62 | 16.72 | 3.59 | 0.01 | 12.65 | 2.5
2018-05-02 02:00 | 11919.3391 | -0.048233 | 13.33 | 17.11 | 15.61 | 15.29 | 3.59 | 1 | 10 | 2.11
2018-05-02 03:00 | 11857.0941 | -0.048233 | 13.65 | 16.78 | 15.15 | 14.64 | 3.59 | 0.99 | 10 | 2.11
2018-05-02 04:00 | 12402.5291 | -0.048233 | 13.8 | 17.3 | 15.98 | 16.62 | 3.59 | 1.57 | 11.9 | 2.11
2018-05-02 05:00 | 12228.3542 | -0.048233 | 1.87 | 17.35 | 17.45 | 18.43 | 4.45 | 1.49 | 102.4034 | 20
2018-05-02 06:00 | 14365.3879 | 71.461 | 12.17 | 18.5 | 16.94 | 22.2 | 4 | 1.22 | 25 | 6
2018-05-02 07:00 | 15021.799 | 303.42 | 15.43 | 18.68 | 16.01 | 22.62 | 3.5 | 1.22 | 8.57 | 3.49
2018-05-02 08:00 | 17443.8173 | 617.424 | 15.57 | 19.34 | 17.58 | 22.19 | 3.5 | 1.88 | 10.84 | 3.5
2018-05-02 09:00 | 16568.9091 | 873.957 | 15.96 | 20.11 | 18.95 | 23.34 | 3.5 | 1.31 | 1.94 | 3.5
2018-05-02 10:00 | 18474.0945 | 1040.99 | 15.48 | 21.6 | 19.53 | 25.31 | 3.75 | 1 | 3.5 | 3.75
2018-05-02 11:00 | 18225.0723 | 1138.95 | 15.19 | 21.23 | 19.17 | 30.12 | 5.39 | 9.79 | 1 | 5.39
2018-05-02 12:00 | 19198.4247 | 899.559 | 13.55 | 21.94 | 18.22 | 35 | 6 | 1.81 | 0.51 | 3.61
2018-05-02 13:00 | 18215.813 | 1107.54 | 13.06 | 24.14 | 18.08 | 40.02 | 6.01 | 12 | 0.51 | 6.01
2018-05-02 14:00 | 15708.326 | 1028.08 | 13.15 | 24.53 | 17.56 | 49.02 | 8.69 | 2.01 | 0.71 | 4.33
2018-05-02 15:00 | 16220.9162 | 809.276 | 13.76 | 28.65 | 17.53 | 54.02 | 19.08 | 8.8 | 1.12 | 17
2018-05-02 16:00 | 15503.3832 | 546.15 | 14.17 | 27.89 | 17.53 | 56.46 | 28.6 | 12.75 | 1.47 | 28.6
2018-05-02 17:00 | 14959.1024 | 239.244 | 67.08 | 28.38 | 17.6 | 37.62 | 23.07 | 6.25 | 9.06 | 22.1
2018-05-02 18:00 | 14590.933 | 28.2682 | 15.89 | 27.76 | 17.56 | 37.5 | 8.58 | 2 | 16.04 | 5.69
2018-05-02 19:00 | 13166.0042 | -0.048233 | 102.84 | 102.84 | 18 | 29.16 | 6.36 | 1.64 | 8.11 | 4.48
2018-05-02 20:00 | 13319.9042 | -0.048233 | 135.51 | 135.51 | 20.6 | 34.41 | 7.61 | 1.56 | 2 | 6.76
2018-05-02 21:00 | 14725.6391 | -0.048233 | 132.05 | 132.05 | 18.38 | 27.02 | 6 | 1.55 | 25 | 5
2018-05-02 22:00 | 12972.2042 | -0.048233 | 19.03 | 31.44 | 17 | 23.2 | 15 | 0.01 | 52.6962 | 15
2018-05-02 23:00 | 14050.4391 | -0.048233 | 15.44 | 22.39 | 17.17 | 19.63 | 6.01 | 0.01 | 49.7062 | 15
2018-05-03 | 13796.1841 | -0.048233 | 13.06 | 17.35 | 15.86 | 18.46 | 7.11 | 0.01 | 62.6962 | 3.5
2018-05-03 01:00 | 12329.0542 | -0.048233 | 12.23 | 14.66 | 13.59 | 16.8 | 3.49 | 0.01 | 14.12 | 1.61
2018-05-03 02:00 | 13438.5391 | -0.048233 | 5.06 | 12.76 | 11.95 | 15.99 | 3.49 | 1.62 | 12 | 1.58
2018-05-03 03:00 | 13378.4041 | -0.048233 | 4.48 | 13.33 | 11.07 | 15.44 | 3.75 | 1.62 | 16.08 | 1.58
2018-05-03 04:00 | 12903.8042 | -0.048233 | 1.21 | 17.16 | 11.44 | 17.81 | 3.49 | 1.61 | 20.07 | 1.58
2018-05-03 05:00 | 13799.6542 | -0.048233 | 6.37 | 19.38 | 12.25 | 20.86 | 5 | 1.33 | 118.8034 | 4
2018-05-03 06:00 | 17337.4396 | 78.592 | 10.04 | 20.08 | 11.96 | 23.81 | 6.19 | 2 | 13.82 | 10.56
2018-05-03 07:00 | 18302.7983 | 300.624 | 14.94 | 21.76 | 13.34 | 23.69 | 4.45 | 1.45 | 3.01 | 3.96
2018-05-03 08:00 | 16840.137 | 567.46 | 15.36 | 22.45 | 15.81 | 23.61 | 4.45 | 2.25 | 10.79 | 4.45
2018-05-03 09:00 | 19908.1971 | 830.329 | 15.38 | 20.98 | 17.18 | 24.93 | 3.75 | 7 | 3.5 | 3.75
2018-05-03 10:00 | 19908.1982 | 1001.33 | 16.44 | 21.39 | 17.56 | 28.45 | 4 | 1 | 3.5 | 4
2018-05-03 11:00 | 17959.4175 | 1158.65 | 17.62 | 24.98 | 17.55 | 33.27 | 5.55 | 9.79 | 0.71 | 5.55
2018-05-03 12:00 | 18246.3175 | 1158.65 | 18.05 | 24.52 | 17.55 | 36.77 | 6 | 9.52 | 0.25 | 5
2018-05-03 13:00 | 17953.822 | 1151.76 | 18.49 | 22.1 | 17.54 | 40.24 | 6.25 | 11.38 | 0.25 | 5.25
2018-05-03 14:00 | 18781.282 | 999.163 | 18.55 | 26.86 | 17.57 | 48.7 | 8.11 | 1.89 | 0.51 | 12.85
2018-05-03 15:00 | 15770.3278 | 784.345 | 18.29 | 28.02 | 17.57 | 55.85 | 17.1 | 2.45 | 1 | 16.22
2018-05-03 16:00 | 15003.5476 | 536.208 | 320.1757 | 275.85 | 17.61 | 51.95 | 17.61 | 2.13 | 1.09 | 16.72
2018-05-03 17:00 | 16235.6282 | 245.221 | 46.18 | 46.18 | 17.65 | 38.9 | 17 | 6.25 | 18.52 | 15.33
2018-05-03 18:00 | 14193.4232 | 27.4455 | 37.52 | 37.52 | 17.6 | 29.76 | 8 | 1.57 | 52.6962 | 5
2018-05-03 19:00 | 14033.3542 | -0.048233 | 39.82 | 39.82 | 19.39 | 26.05 | 8 | 1.62 | 12.46 | 5
2018-05-03 20:00 | 13913.6542 | -0.048233 | 36.73 | 36.73 | 20.57 | 33.45 | 9.09 | 1.58 | 1 | 6.95
2018-05-03 21:00 | 15208.8291 | -0.048233 | 347.2957 | 302.97 | 18.3 | 30.38 | 6.09 | 1.49 | 17.98 | 6.09
2018-05-03 22:00 | 14635.9641 | -0.048233 | 138.15 | 138.15 | 18.39 | 25.56 | 30 | 0.01 | 102.7534 | 30
2018-05-03 23:00 | 13875.3091 | -0.048233 | 14.98 | 21.11 | 17.43 | 22 | 25 | 0.01 | 30 | 25
2018-05-04 | 12528.0741 | -0.048233 | 14.35 | 19.24 | 15 | 16.88 | 3 | 0.01 | 30 | 2.11
2018-05-04 01:00 | 11884.5241 | -0.048233 | 13.19 | 17.84 | 11.97 | 16.13 | 3 | 0.01 | 11.07 | 1
2018-05-04 02:00 | 10450.9042 | -0.048233 | 0 | 0 | 9.63 | 13.87 | 3 | 0.99 | 9.75 | 0.5
2018-05-04 03:00 | 11448.8091 | -0.048233 | -0.74 | -0.74 | 11.05 | 11.35 | 3 | 0.99 | 9.43 | 0.5
2018-05-04 04:00 | 10771.0542 | -0.048233 | 6.39 | 6.39 | 12.09 | 13.85 | 3 | 0.99 | 11.07 | 1
2018-05-04 05:00 | 11280.2542 | -0.048233 | 11.56 | 13 | 17.5 | 17.25 | 3 | 0.99 | 102.7534 | 2.5
2018-05-04 06:00 | 14095.0408 | 78.2282 | 13.22 | 17.41 | 19.25 | 23.15 | 31.88 | 3.05 | 10.15 | 31.88
2018-05-04 07:00 | 15808.7097 | 309.559 | 13.09 | 17.41 | 20.68 | 23.55 | 4.49 | 2.25 | 2.11 | 2.25
2018-05-04 08:00 | 16410.9175 | 602.372 | 13.03 | 18.62 | 20.11 | 22.88 | 5.2 | 2.5 | 12 | 3.4
2018-05-04 09:00 | 17460.4621 | 872.201 | 15.2 | 18.96 | 20.62 | 23.23 | 4.3 | 2.59 | 0.61 | 3.5
2018-05-04 10:00 | 16437.9656 | 1053.01 | 15.65 | 18.79 | 21.25 | 22.98 | 4.82 | 6 | 3.5 | 3.81
2018-05-04 11:00 | 16225.5307 | 1158.65 | 15.52 | 19.47 | 21.48 | 23.64 | 4.95 | 7 | 1 | 3.98
2018-05-04 12:00 | 15947.3175 | 1158.65 | 15.78 | 19.59 | 21.27 | 25.49 | 6.01 | 6 | 0.25 | 5.18
2018-05-04 13:00 | 16187.5507 | 1158.65 | 16.62 | 20.44 | 21.35 | 25.35 | 7.61 | 2.25 | 0.51 | 3.11
2018-05-04 14:00 | 15152.332 | 1043.4 | 18.83 | 20.41 | 21.23 | 30.51 | 19.45 | 11.25 | 1.62 | 15.25
2018-05-04 15:00 | 13074.8186 | 835.193 | 20.59 | 21.55 | 21.18 | 32.39 | 32 | 23 | 2.31 | 28
2018-05-04 16:00 | 12551.6125 | 564.263 | 22.13 | 22.13 | 21.49 | 36.67 | 38.35 | 26.75 | 15 | 32.75
2018-05-04 17:00 | 11452.9359 | 239.722 | 29.92 | 23.35 | 21.66 | 35.32 | 24.15 | 15.82 | 2.26 | 19.21
2018-05-04 18:00 | 12124.2063 | 30.1387 | 42.93 | 23.2 | 21.64 | 29.82 | 13.27 | 1 | 20.07 | 5
2018-05-04 19:00 | 10980.0542 | -0.048233 | 32.89 | 24.37 | 21.74 | 35.25 | 20.1 | 0.99 | 2 | 15.02
2018-05-04 20:00 | 10963.9042 | -0.048233 | 104.23 | 104.23 | 22.25 | 52.04 | 38.49 | 0.99 | 2 | 25
2018-05-04 21:00 | 10755.8542 | -0.048233 | 34.03 | 34.03 | 20.49 | 34.87 | 6.12 | 0.99 | 15 | 15.07
2018-05-04 22:00 | 11480.4591 | -0.048233 | 18.62 | 27.55 | 19.11 | 25.78 | 4.57 | 0.01 | 29.82 | 15
2018-05-04 23:00 | 10990.9391 | -0.048233 | 16.14 | 21.11 | 18.65 | 23.09 | 6.01 | 0.01 | 12.42 | 15
2018-05-05 | 9667.1542 | -0.048233 | 15.03 | 21.1 | 17.68 | 20.63 | 3 | 0.01 | 8.69 | 2.5
2018-05-05 01:00 | 10564.7191 | -0.048233 | 13.27 | 20.63 | 17 | 19.91 | 3 | 0.01 | 4.89 | 1
2018-05-05 02:00 | 9397.3542 | -0.048233 | 11.74 | 20.46 | 15.69 | 19.31 | 3 | 1 | 4.11 | 0.69
2018-05-05 03:00 | 10388.5341 | -0.048233 | 11.28 | 20.77 | 15.13 | 19.06 | 3 | 0.99 | 2.71 | 0.61
2018-05-05 04:00 | 9987.3042 | -0.048233 | 11.22 | 44.25 | 15.67 | 19.42 | 3 | 1 | 2.11 | 0.82
2018-05-05 05:00 | 10795.7542 | -0.048233 | 12.15 | 23.08 | 17.54 | 20.39 | 3.25 | 1 | 62.6962 | 2.75
2018-05-05 06:00 | 12573.9701 | 77.758 | 14.9 | 20.94 | 18.5 | 24 | 3.25 | 2.25 | 6.74 | 25
2018-05-05 07:00 | 13117.4689 | 309.862 | 15.66 | 31.93 | 20.5 | 23.25 | 3.16 | 2 | 2.11 | 2.61
2018-05-05 08:00 | 15092.3468 | 598.542 | 17.69 | 20.93 | 21.11 | 23.82 | 3.45 | 2.25 | 2.79 | 3.25
2018-05-05 09:00 | 15924.4854 | 876.299 | 17.42 | 21.37 | 22.75 | 25.41 | 3.38 | 2 | 0.61 | 3.38
2018-05-05 10:00 | 14397.2785 | 1055.03 | 18.97 | 23.59 | 22.68 | 29.74 | 3.7 | 1 | 2 | 3.7
2018-05-05 11:00 | 15810.9157 | 1158.65 | 18.85 | 22.53 | 22.49 | 29.55 | 5 | 1 | 1 | 5
2018-05-05 12:00 | 16562.0757 | 1158.65 | 19.64 | 21.91 | 21.87 | 29.27 | 5 | 2 | 0.71 | 3.79
2018-05-05 13:00 | 15938.9716 | 1158.03 | 22.2 | 22.2 | 21.05 | 35.87 | 5.65 | 10.26 | 0.71 | 5.05
2018-05-05 14:00 | 14759.8192 | 1032.35 | 21.76 | 23.54 | 20.97 | 39.48 | 8 | 1.84 | 1 | 6.67
2018-05-05 15:00 | 13777.0171 | 816.784 | 23.25 | 24.92 | 20.93 | 51.11 | 19.58 | 8.47 | 2 | 15.67
2018-05-05 16:00 | 11797.4068 | 555.323 | 30.67 | 29.69 | 21.04 | 60.81 | 34.96 | 10.91 | 2.11 | 26.08
2018-05-05 17:00 | 11386.6781 | 238.977 | 29.76 | 29.76 | 21.23 | 56.88 | 27.53 | 12 | 2 | 21.5
2018-05-05 18:00 | 10919.4087 | 29.1144 | 30.89 | 30.89 | 19.9 | 35.34 | 6.55 | 1.74 | 10 | 5
2018-05-05 19:00 | 12034.3341 | -0.048233 | 20.57 | 28.04 | 20.42 | 31 | 6 | 1.11 | 9.66 | 5
2018-05-05 20:00 | 10711.2042 | -0.048233 | 20.36 | 23.91 | 21.37 | 31.84 | 6.61 | 0.99 | 2.65 | 4
2018-05-05 21:00 | 10632.3542 | -0.048233 | 18.72 | 21.6 | 19.45 | 27.03 | 3.84 | 1.31 | 25 | 3.83
2018-05-05 22:00 | 10260.9042 | -0.048233 | 39.89 | 39.89 | 17.66 | 25.93 | 6 | 0.01 | 25 | 15
2018-05-05 23:00 | 9870.4542 | -0.048233 | 15.59 | 19.66 | 17.57 | 22.49 | 6 | 0.01 | 22 | 15
2018-05-06 | 10957.1791 | -0.048233 | 15.26 | 19.01 | 14.36 | 19.54 | 30 | 0.01 | 112.7534 | 30
2018-05-06 01:00 | 9730.8042 | -0.048233 | 14.56 | 17 | 12.83 | 17.31 | 5 | 0.01 | 30 | 2.61
2018-05-06 02:00 | 9421.1042 | -0.048233 | 7.59 | 7.59 | 11.35 | 15.57 | 4 | 0.99 | 25 | 2.11
2018-05-06 03:00 | 10184.9191 | -0.048233 | 7.08 | 7.08 | 11.35 | 10.88 | 4 | 0.99 | 17.03 | 2.61
2018-05-06 04:00 | 10335.7841 | -0.048233 | 1.67 | 1.67 | 12.86 | 14.31 | 4 | 1.13 | 9.5 | 2.61
2018-05-06 05:00 | 9647.2042 | -0.048233 | 12.77 | 15.71 | 15.31 | 16.76 | 5 | 1.22 | 112.1534 | 15.94
2018-05-06 06:00 | 10051.867 | 83.9126 | 12.42 | 16.77 | 17.8 | 21.36 | 41.68 | 2.5 | 52.6962 | 87.1162
2018-05-06 07:00 | 10290.8788 | 288.504 | 13.81 | 17.37 | 18.28 | 21.19 | 4.1 | 2.25 | 3 | 3.9
2018-05-06 08:00 | 11963.6916 | 583.992 | 13.94 | 19.55 | 18.83 | 23.53 | 4.1 | 2.25 | 25 | 4.1
2018-05-06 09:00 | 12703.14 | 765.891 | 15.41 | 20.1 | 19.3 | 23.86 | 3.63 | 2.25 | 25 | 3.63
2018-05-06 10:00 | 11409.367 | 659.86 | 15.36 | 19.79 | 20.06 | 24.34 | 4.1 | 1 | 2.92 | 4.1
2018-05-06 11:00 | 11398.8125 | 929.75 | 15.86 | 20.46 | 20.92 | 26.02 | 4.95 | 9.55 | 1 | 4.95
2018-05-06 12:00 | 12793.8035 | 777.828 | 15.68 | 21.42 | 18.77 | 32.07 | 5.04 | 10.26 | 0.71 | 5.04
2018-05-06 13:00 | 11435.5718 | 683.444 | 16.82 | 22.75 | 18.92 | 34.46 | 6.79 | 8.7 | 0.95 | 6.79
2018-05-06 14:00 | 12134.4686 | 496.866 | 29.86 | 27.93 | 18.94 | 37.1 | 16.74 | 9.25 | 1 | 15.74
2018-05-06 15:00 | 10878.7473 | 583.313 | 32.81 | 29.2 | 18.71 | 50.48 | 29.32 | 21.12 | 2.11 | 29.32
2018-05-06 16:00 | 11990.4801 | 503.384 | 107.63 | 107.63 | 18.93 | 62.9 | 36.43 | 25.43 | 2.31 | 35.43
2018-05-06 17:00 | 11852.4228 | 220.524 | 36.79 | 36.79 | 19.53 | 44.76 | 24.65 | 19.08 | 2.11 | 23.08
2018-05-06 18:00 | 10494.5481 | 31.8927 | 15.21 | 28.27 | 18.74 | 34.34 | 8.11 | 1.55 | 20.07 | 9.93
2018-05-06 19:00 | 10613.3542 | -0.048233 | 14.09 | 30.43 | 19.03 | 30.43 | 7.2 | 1.3 | 7.9 | 7
2018-05-06 20:00 | 11769.5291 | -0.048233 | 15.12 | 23.47 | 20.67 | 29.3 | 7.11 | 1.22 | 2.11 | 6.31
2018-05-06 21:00 | 10490.8042 | -0.048233 | 15.32 | 21.06 | 19.13 | 26.39 | 4.04 | 1.22 | 25 | 4.04
2018-05-06 22:00 | 11306.3841 | -0.048233 | 14.42 | 20.19 | 17.69 | 24.03 | 15 | 0.01 | 57.7062 | 15
2018-05-06 23:00 | 11054.2391 | -0.048233 | 11.15 | 18.68 | 17.21 | 20.6 | 13.89 | 0.01 | 30 | 22
2018-05-07 | 10900.2091 | -0.048233 | 10.11 | 16.42 | 15.57 | 17.85 | 5 | 0.01 | 57.7062 | 15
2018-05-07 01:00 | 9658.6042 | -0.048233 | 9.91 | 14.76 | 15.18 | 14.28 | 3 | 0.01 | 30.53 | 2.61
2018-05-07 02:00 | 9496.1542 | -0.048233 | -0.14 | -0.14 | 15.03 | 8.56 | 2.89 | 1.4 | 25 | 2.61
2018-05-07 03:00 | 9498.0542 | -0.048233 | -0.35 | -0.35 | 11.51 | 6.11 | 3 | 1.39 | 20.89 | 2.61
2018-05-07 04:00 | 9480.0042 | -0.048233 | -0.52 | -0.48 | 7.01 | 6.19 | 3 | 1.4 | 19.66 | 2.61
2018-05-07 05:00 | 10507.7491 | -0.048233 | -0.46 | -0.46 | 7.73 | 7.28 | 5.25 | 1.42 | 95.5934 | 25
2018-05-07 06:00 | 9572.6861 | 89.5117 | -0.48 | -0.48 | 10.95 | 17.4 | 6.33 | 10.22 | 53.0162 | 87.1162
2018-05-07 07:00 | 10581.3685 | 76.7332 | -0.48 | -0.48 | 17.52 | 19.71 | 5.25 | 2.25 | 15.47 | 3.77
2018-05-07 08:00 | 10776.8155 | 258.991 | 7.06 | 17.42 | 18 | 20.81 | 3.5 | 2.25 | 25 | 3.5
2018-05-07 09:00 | 10967.8275 | 299.045 | 9.14 | 18.28 | 18.77 | 22.36 | 3.4 | 2.5 | 25 | 3.4
2018-05-07 10:00 | 9951.023 | 377.761 | 10.87 | 18.01 | 19.19 | 23.96 | 3.5 | 9.55 | 15 | 3.5
2018-05-07 11:00 | 10952.1481 | 174.183 | 11.92 | 18.74 | 19.66 | 24.39 | 4.54 | 12 | 12.88 | 12.62
2018-05-07 12:00 | 10385.8 | 624.421 | 12.09 | 19.55 | 18.09 | 30.37 | 4.12 | 14.14 | 2.11 | 4.12
2018-05-07 13:00 | 10340.4441 | 539.678 | 11.77 | 20.09 | 17.64 | 30.23 | 5.93 | 10.09 | 2.11 | 5.93
2018-05-07 14:00 | 10103.9444 | 152.731 | 13.91 | 21.72 | 17.27 | 39.13 | 15.78 | 8.78 | 2.11 | 14.78
2018-05-07 15:00 | 11328.533 | 122.946 | 13.39 | 23.08 | 17.37 | 50.94 | 26.66 | 21.66 | 2.5 | 26.66
2018-05-07 16:00 | 11525.0754 | 87.2421 | 14.95 | 26.3 | 18.03 | 56.84 | 33.64 | 23.04 | 11.09 | 32.64
2018-05-07 17:00 | 10367.8718 | 61.5493 | 14.87 | 22.6 | 18.15 | 40.4 | 22 | 15 | 7.5 | 20.04
2018-05-07 18:00 | 11513.9242 | 31.6722 | 12.11 | 20.68 | 17.68 | 31.21 | 6.85 | 1.28 | 33.66 | 6.53
2018-05-07 19:00 | 10178.2542 | -0.048233 | 10.39 | 18.75 | 18.06 | 28.09 | 5.74 | 1.43 | 25 | 5.74
2018-05-07 20:00 | 11594.3991 | -0.048233 | 11.49 | 20.59 | 21.19 | 31.65 | 6.43 | 1.32 | 25 | 6.43
2018-05-07 21:00 | 11542.7041 | -0.048233 | 12.09 | 20.57 | 19.02 | 26.83 | 5.32 | 1.33 | 25 | 5.32
2018-05-07 22:00 | 11301.1091 | -0.048233 | 14.8 | 19.87 | 17.5 | 21.98 | 8.5 | 0.01 | 112.7534 | 15
2018-05-07 23:00 | 11158.6841 | -0.048233 | 13.1 | 18.41 | 17.03 | 20.14 | 8.69 | 0.01 | 52.6962 | 22
2018-05-08 | 9920.8042 | -0.048233 | 10.46 | 17.68 | 16.72 | 15.73 | 3.12 | 0.01 | 40 | 3.12
2018-05-08 01:00 | 9841.9542 | -0.048233 | 9.26 | 16.06 | 15.9 | 13.59 | 3 | 0.01 | 20 | 2.61
2018-05-08 02:00 | 10999.3791 | -0.048233 | 6.58 | 7.42 | 14.75 | 9.75 | 3 | 1.75 | 26.72 | 2.3
2018-05-08 03:00 | 9813.4542 | -0.048233 | -0.18 | 9.1 | 13.71 | 8.65 | 3 | 1.75 | 16.98 | 2.61
2018-05-08 04:00 | 11761.0891 | -0.048233 | 3.99 | 11.28 | 14.01 | 12.28 | 3 | 1.75 | 10.91 | 2.61
2018-05-08 05:00 | 12783.3841 | -0.048233 | 0.59 | 17.27 | 14.98 | 18.2 | 3.5 | 1 | 112.7534 | 3.5
2018-05-08 06:00 | 13443.799 | 89.3674 | 1.31 | 16.45 | 16.43 | 21.62 | 3.67 | 9.9 | 20 | 12
2018-05-08 07:00 | 14216.891 | 51.1484 | 11.31 | 18.75 | 16.32 | 21.62 | 3.2 | 2.25 | 1 | 3.2
2018-05-08 08:00 | 16418.3046 | 100.374 | 11.16 | 20.54 | 16.41 | 22.45 | 3.5 | 2.25 | 9.28 | 3.5
2018-05-08 09:00 | 17715.9841 | 156.402 | 12.94 | 20.01 | 17.32 | 28.66 | 3.12 | 2.55 | 0.61 | 3.12
2018-05-08 10:00 | 16758.8079 | 157.126 | 13.73 | 20.17 | 17.61 | 29.37 | 3.31 | 2.14 | 1 | 3.31
2018-05-08 11:00 | 16975.0238 | 175.07 | 14.17 | 21.81 | 17.64 | 40.82 | 4.46 | 2.25 | 1 | 4.46
2018-05-08 12:00 | 16219.1543 | 351.794 | 14.91 | 22.11 | 17.53 | 42.88 | 4.96 | 7.44 | 1 | 4.92
2018-05-08 13:00 | 17003.5902 | 331.516 | 13.26 | 22.74 | 16.74 | 46.7 | 17.73 | 7.83 | 0.47 | 15.73
2018-05-08 14:00 | 15842.4666 | 325.556 | 10.78 | 20.06 | 16.37 | 52.53 | 25.83 | 17.63 | 1.31 | 23.83
2018-05-08 15:00 | 14828.9123 | 161.841 | 11.34 | 23.16 | 16.35 | 56.15 | 42 | 53.5573 | 1 | 41
2018-05-08 16:00 | 14478.6871 | 291.874 | 10.16 | 24.29 | 17.57 | 61.61 | 42.53 | 53.5573 | 2.07 | 40.22
2018-05-08 17:00 | 12628.8253 | 49.5003 | 10.03 | 19.4 | 17.65 | 45.85 | 29.38 | 17.27 | 2.55 | 22.38
2018-05-08 18:00 | 12460.4816 | 28.2964 | 11.32 | 17.07 | 17.73 | 44.04 | 20.24 | 17.04 | 20 | 17.04
2018-05-08 19:00 | 13753.9841 | -0.048233 | 9.93 | 14.27 | 19.41 | 43.48 | 5.4 | 1.5 | 8.11 | 5
2018-05-08 20:00 | 13642.1541 | -0.048233 | 13.37 | 18.64 | 21.6 | 54.32 | 6 | 7.26 | 2.11 | 11.08
2018-05-08 21:00 | 13346.7541 | -0.048233 | 13.68 | 21.57 | 18.06 | 44.84 | 3.3 | 1.25 | 7.5 | 3.3
2018-05-08 22:00 | 11469.3042 | -0.048233 | 14.18 | 20.54 | 16.43 | 38.95 | 3.3 | 0.01 | 27.52 | 3.3
2018-05-08 23:00 | 10927.8042 | -0.048233 | 11.91 | 19.41 | 15.9 | 25.26 | 3.3 | 0.01 | 22 | 15
2018-05-09 | 10766.3042 | -0.048233 | 10.4 | 19.4 | 15.81 | 20.17 | 4.2 | 0.01 | 32.04 | 4
2018-05-09 01:00 | 10784.3542 | -0.048233 | 11.31 | 20.02 | 15.14 | 19.38 | 3.12 | 0.01 | 20 | 2.61
2018-05-09 02:00 | 12007.9591 | -0.048233 | 12.27 | 20.28 | 14.49 | 18.62 | 3 | 0.99 | 20 | 2.3
2018-05-09 03:00 | 12043.8291 | -0.048233 | 13.8 | 20.67 | 13.41 | 18.33 | 3.01 | 0.99 | 11.3 | 2.61
2018-05-09 04:00 | 13131.5341 | -0.048233 | 14.01 | 21.14 | 13.42 | 19.02 | 3.01 | 0.99 | 3.5 | 2.61
2018-05-09 05:00 | 14209.7441 | -0.048233 | 15.92 | 21.88 | 14.35 | 21.02 | 4 | 0.99 | 62.6962 | 20
2018-05-09 06:00 | 16143.6873 | 79.0733 | 11.8 | 23.85 | 15.18 | 22.19 | 6 | 2.25 | 25.55 | 25
2018-05-09 07:00 | 15806.6415 | 311.57 | 13.18 | 28.33 | 16.65 | 21.55 | 4 | 2.25 | 2.61 | 4
2018-05-09 08:00 | 16422.5493 | 603.894 | 10.46 | 24.17 | 17.7 | 22.15 | 3.35 | 2.25 | 2.39 | 3.5
2018-05-09 09:00 | 18457.3157 | 799.086 | 13.13 | 26.48 | 18.16 | 23.48 | 4 | 1.43 | 0.61 | 3.57
2018-05-09 10:00 | 17007.603 | 1035.74 | 10.83 | 24.18 | 18.55 | 26.96 | 4.24 | 1.35 | 2 | 4.55
2018-05-09 11:00 | 16782.0255 | 1088.29 | 12.17 | 22.63 | 18.83 | 28.39 | 5.46 | 1.81 | 1 | 5.09
2018-05-09 12:00 | 17126.2675 | 1158.65 | 12.68 | 24.86 | 19.29 | 32.1 | 4.74 | 2.22 | 0.36 | 4.54
2018-05-09 13:00 | 18469.0821 | 651.239 | 18.49 | 22.93 | 19.29 | 34.79 | 5.57 | 7.55 | 0.47 | 5.57
2018-05-09 14:00 | 17391.3268 | 972.67 | 14.58 | 21.45 | 18.79 | 38.96 | 8.25 | 1.22 | 1 | 12.4
2018-05-09 15:00 | 15746.9142 | 353.985 | 15.32 | 23.27 | 18.8 | 40.27 | 30.12 | 13.25 | 1.45 | 29.12
2018-05-09 16:00 | 13608.7224 | 347.971 | 16.1 | 22.9 | 18.83 | 41 | 33.18 | 18.28 | 2.21 | 31.89
2018-05-09 17:00 | 14762.7427 | 212.121 | 15.99 | 21.47 | 18.83 | 33.03 | 23.82 | 10.39 | 2.11 | 21.82
2018-05-09 18:00 | 14249.7846 | 40.9048 | 17.46 | 19.45 | 18.83 | 28.92 | 8 | 0.97 | 20 | 5
2018-05-09 19:00 | 12777.4542 | -0.048233 | 17.53 | 19.09 | 19.07 | 25.92 | 7.21 | 0.97 | 10 | 4.77
2018-05-09 20:00 | 12813.5542 | -0.048233 | 16.69 | 20.35 | 21.78 | 28.52 | 7.01 | 0.97 | 3.5 | 4.95
2018-05-09 21:00 | 12622.6042 | -0.048233 | 17.48 | 22.07 | 18.24 | 27.09 | 4.57 | 0.97 | 9.11 | 4.57
2018-05-09 22:00 | 13591.5141 | -0.048233 | 16.16 | 23.64 | 16.82 | 24.06 | 4.69 | 0.01 | 28.03 | 23.4
2018-05-09 23:00 | 11737.2042 | -0.048233 | 13.76 | 20.7 | 15.97 | 20.89 | 4.94 | 0.01 | 25 | 80.1162
2018-05-10 | 12940.5791 | -0.048233 | 15.26 | 19.58 | 13.05 | 18.89 | 3 | 0.01 | 25 | 19.66
2018-05-10 01:00 | 11392.3542 | -0.048233 | 14.38 | 19.36 | 12 | 16.45 | 3 | 0.01 | 20 | 2.11
2018-05-10 02:00 | 11220.4042 | -0.048233 | 14.18 | 17.15 | 8.56 | 14.7 | 3 | 1.22 | 20 | 1.98
2018-05-10 03:00 | 11223.2542 | -0.048233 | 14.81 | 17 | 6.54 | 16.34 | 3 | 1.22 | 12.68 | 2.11
2018-05-10 04:00 | 13464.9141 | -0.048233 | 14.73 | 15.86 | 6.38 | 18.67 | 3 | 1.22 | 2.24 | 2.11
2018-05-10 05:00 | 12978.8542 | -0.048233 | 14.83 | 17.03 | 9.75 | 20.61 | 3.14 | 1 | 23.56 | 18.52
2018-05-10 06:00 | 14889.7087 | 74.3776 | 14.23 | 19.11 | 9.8 | 23.72 | 3.21 | 6 | 14.18 | 5.11
2018-05-10 07:00 | 17836.2383 | 137.387 | 14.95 | 20.18 | 12.76 | 23.59 | 3 | 2 | 2.11 | 3
2018-05-10 08:00 | 16676.7437 | 327.467 | 16.33 | 20.31 | 17.32 | 24.02 | 3.8 | 2 | 2 | 3.8
2018-05-10 09:00 | 19987.8591 | 611.838 | 16.54 | 21.09 | 18.46 | 26.15 | 3.8 | 2 | 0.61 | 3.8
2018-05-10 10:00 | 18587.68 | 540.654 | 17.38 | 20.48 | 18.63 | 27.27 | 4 | 6.19 | 2 | 4
2018-05-10 11:00 | 18982.8714 | 944.243 | 19.37 | 20.73 | 19.42 | 26.8 | 7.79 | 7.34 | 1 | 6.79
2018-05-10 12:00 | 20623.1432 | 702.003 | 18.47 | 23.28 | 19.24 | 29.54 | 7.51 | 10 | 1 | 10.9
2018-05-10 13:00 | 18800.2287 | 869.122 | 18.99 | 24.41 | 19.32 | 34.47 | 14.24 | 13.62 | 1 | 13.34
2018-05-10 14:00 | 15957.6022 | 773.476 | 22.03 | 24.56 | 17.37 | 41.67 | 17.12 | 8.87 | 1 | 16.48
2018-05-10 15:00 | 14782.4855 | 504.511 | 41.47 | 41.47 | 18.73 | 45.07 | 30.22 | 17.07 | 1.28 | 24.81
2018-05-10 16:00 | 14076.6468 | 302.523 | 35.71 | 32.88 | 17.52 | 45.82 | 83.2841 | 19.75 | 2.11 | 49.5
2018-05-10 17:00 | 13530.0833 | 129.193 | 32.3 | 26.58 | 17.52 | 34.1 | 33.37 | 18.77 | 1 | 26.48
2018-05-10 18:00 | 14710.3821 | 42.4901 | 20.47 | 23.17 | 16.84 | 28.88 | 13.62 | 8.25 | 10 | 6.97
2018-05-10 19:00 | 13242.9542 | -0.048233 | 18.7 | 21.85 | 17.65 | 26.41 | 14.32 | 1.88 | 8.11 | 13.71
2018-05-10 20:00 | 14778.3891 | -0.048233 | 16.72 | 25.95 | 21.87 | 31.51 | 14.85 | 11.29 | 3.09 | 13.79
2018-05-10 21:00 | 12999.7542 | -0.048233 | 17.17 | 27.08 | 17.01 | 26.32 | 6.39 | 8.83 | 11.75 | 6.39
2018-05-10 22:00 | 13922.7841 | -0.048233 | 16.4 | 24.52 | 16.19 | 27.43 | 4.93 | 0.01 | 30.01 | 4.93
2018-05-10 23:00 | 12114.3542 | -0.048233 | 12.46 | 22.55 | 15.61 | 22.14 | 3.58 | 0.01 | 20 | 3.58
2018-05-11 | 11893.9542 | -0.048233 | 12.2 | 20.67 | 7.61 | 20.45 | 3 | 0.01 | 12.01 | 2.8
2018-05-11 01:00 | 11769.5042 | -0.048233 | 12.65 | 19.36 | 4.28 | 19.86 | 3 | 0.01 | 1.55 | 2.12
2018-05-11 02:00 | 13052.4091 | -0.048233 | 1.09 | 19.68 | 3.72 | 18.48 | 3 | 0.99 | 3 | 2.01
2018-05-11 03:00 | 11732.4542 | -0.048233 | 0 | 20.21 | 3.68 | 18.66 | 3 | 0.99 | 3 | 2.11
2018-05-11 04:00 | 14267.7691 | -0.048233 | 5.18 | 19.98 | 4.26 | 19.21 | 3 | 0.99 | 1.55 | 2.11
2018-05-11 05:00 | 15078.0091 | -0.048233 | 10.7 | 20.95 | 12.37 | 22.01 | 3 | 0.99 | 15.01 | 3
2018-05-11 06:00 | 15377.0415 | 73.3595 | 8.51 | 24.44 | 16.96 | 24.18 | 3.01 | 6 | 8.11 | 3.01
2018-05-11 07:00 | 17921.6711 | 263.366 | 11.58 | 26.19 | 17.12 | 23.16 | 4.2 | 2.25 | 1 | 3.4
2018-05-11 08:00 | 18553.8957 | 513.631 | 11.72 | 28.68 | 16.88 | 23.94 | 4.44 | 1.65 | 1 | 4
2018-05-11 09:00 | 17521.553 | 809.74 | 11.81 | 24 | 16.95 | 25.71 | 4.75 | 2.25 | 0.51 | 4
2018-05-11 10:00 | 19516.8142 | 1023.35 | 76.39 | 76.39 | 18.15 | 28.26 | 5.51 | 1 | 1.3 | 5
2018-05-11 11:00 | 19183.7085 | 1110.61 | 18.87 | 30.87 | 18.46 | 32.14 | 7.31 | 7.21 | 1 | 7.11
2018-05-11 12:00 | 18398.7925 | 1040.15 | 30.87 | 30.51 | 18.16 | 36.19 | 7.29 | 8.1 | 0.45 | 6.44
2018-05-11 13:00 | 20160.7862 | 864.75 | 19.53 | 26.48 | 18.53 | 45.38 | 18 | 13.25 | 0.53 | 13.4
2018-05-11 14:00 | 16437.394 | 888.52 | 27.77 | 26.58 | 18.53 | 55.08 | 28.67 | 18.47 | 1 | 22.47
2018-05-11 15:00 | 17128.7479 | 756.78 | 1137.9111 | 870.3 | 18.05 | 59.72 | 45 | 56.1073 | 1 | 43
2018-05-11 16:00 | 14386.4893 | 476.673 | 190.35 | 190.35 | 18.53 | 62.72 | 45 | 53.7073 | 2.04 | 38.67
2018-05-11 17:00 | 15137.8785 | 148.7 | 130.99 | 130.99 | 18.44 | 45.59 | 31.29 | 16.89 | 1.02 | 24.81
2018-05-11 18:00 | 14447.1129 | 39.9459 | 23.16 | 26.38 | 16.58 | 35.18 | 20 | 8.25 | 12.68 | 10.25
2018-05-11 19:00 | 14316.2991 | -0.048233 | 21.61 | 25.97 | 17.42 | 35.8 | 8 | 0.99 | 3.5 | 7.8
2018-05-11 20:00 | 12995.0042 | -0.048233 | 23.62 | 25.95 | 22.33 | 33.45 | 6.97 | 0.99 | 3.46 | 6.54
2018-05-11 21:00 | 12944.6542 | -0.048233 | 21.15 | 26.75 | 17.08 | 28.98 | 5.16 | 0.99 | 7.5 | 5.16
2018-05-11 22:00 | 13856.3191 | -0.048233 | 49.8 | 25.94 | 14.73 | 26.33 | 3.69 | 0.01 | 22 | 3.69
2018-05-11 23:00 | 13261.2991 | -0.048233 | 17.47 | 25.03 | 14.58 | 22.7 | 3.01 | 0.01 | 20 | 15
2018-05-12 | 12961.6791 | -0.048233 | 15.24 | 20.88 | 14.8 | 22.33 | 3.8 | 0.01 | 9.59 | 3.8
2018-05-12 01:00 | 11633.6542 | -0.048233 | 13.98 | 19.71 | 10.95 | 21.2 | 3 | 0.01 | 9.52 | 3
2018-05-12 02:00 | 11542.4542 | -0.048233 | 13.71 | 19.6 | 5.01 | 20.22 | 2.9 | 0.99 | 7 | 2.61
2018-05-12 03:00 | 12702.1491 | -0.048233 | 13.2 | 19.31 | 5 | 20.23 | 3 | 0.99 | 4.11 | 2.5
2018-05-12 04:00 | 13667.4741 | -0.048233 | 13.32 | 18.92 | 10.97 | 20.84 | 3 | 0.99 | 3.29 | 2.61
2018-05-12 05:00 | 12932.3042 | -0.048233 | 11.52 | 19.13 | 15 | 22.34 | 5 | 0.99 | 25 | 5
2018-05-12 06:00 | 16205.248 | 84.4246 | 13.09 | 19.51 | 17.66 | 24.82 | 7.11 | 6 | 11.83 | 12
2018-05-12 07:00 | 16121.9636 | 300.488 | 14.71 | 20.31 | 18.05 | 24.57 | 4.45 | 2 | 2.39 | 3.4
2018-05-12 08:00 | 17058.5468 | 571.365 | 15.16 | 20.53 | 17.35 | 24.5 | 4.45 | 2.01 | 2.5 | 4.01
2018-05-12 09:00 | 17854.6572 | 491.376 | 15.15 | 20.59 | 17.53 | 28.51 | 4.45 | 2.11 | 2.16 | 4.11
2018-05-12 10:00 | 16894.0495 | 359.21 | 16.02 | 22 | 18.05 | 34.39 | 5 | 2 | 2.5 | 4
2018-05-12 11:00 | 16672.063 | 576.54 | 17.12 | 22.71 | 18.05 | 38.85 | 6.54 | 6.82 | 2.11 | 6.54
2018-05-12 12:00 | 17084.306 | 1082.48 | 18.57 | 24.22 | 18.06 | 42.85 | 7.2 | 7.24 | 0.71 | 5.2
2018-05-12 13:00 | 18233.1979 | 769.652 | 20.06 | 25.49 | 19.09 | 51.2 | 8 | 12.31 | 0.71 | 13.21
2018-05-12 14:00 | 15294.9848 | 844.984 | 22.36 | 29.89 | 18.17 | 62.02 | 14.73 | 8.97 | 1 | 14.39
2018-05-12 15:00 | 16159.2957 | 677.868 | 32.45 | 32.45 | 19.36 | 78.89 | 23.65 | 13.51 | 1 | 20.11
2018-05-12 16:00 | 15478.769 | 469.819 | 88.96 | 36.58 | 19.95 | 87.52 | 28.67 | 13.25 | 2.33 | 18.51
2018-05-12 17:00 | 14752.5619 | 218.471 | 78.36 | 31.99 | 18.43 | 65.56 | 18.25 | 7.73 | 2.11 | 14.28
2018-05-12 18:00 | 12890.553 | 40.0032 | 31.39 | 31.39 | 18.41 | 47.02 | 8 | 3 | 8.35 | 4.85
2018-05-12 19:00 | 14037.7791 | -0.048233 | 32.27 | 32.27 | 18.21 | 40.82 | 6.68 | 0.99 | 3 | 6.12
2018-05-12 20:00 | 13932.2791 | -0.048233 | 31.16 | 31.16 | 20.38 | 39.4 | 8.27 | 9.68 | 2.39 | 12.18
2018-05-12 21:00 | 13781.4141 | -0.048233 | 19.7 | 30.33 | 18.08 | 34.18 | 7.29 | 0.99 | 8.7 | 6.67
2018-05-12 22:00 | 12859.3441 | -0.048233 | 16.66 | 26.08 | 15.53 | 30.4 | 5.71 | 0.01 | 15.87 | 5.7
2018-05-12 23:00 | 11975.2541 | -0.048233 | 15.39 | 23.81 | 15.05 | 23.32 | 4.87 | 0.01 | 12.29 | 4.87
2018-05-13 | 10641.8542 | -0.048233 | 14.13 | 21.68 | 17.1 | 22.86 | 3.69 | 0.01 | 20 | 3.43
2018-05-13 01:00 | 11613.3891 | -0.048233 | 13.68 | 20.99 | 15.3 | 21.51 | 3 | 0.01 | 4 | 2.5
2018-05-13 02:00 | 11487.8441 | -0.048233 | 12.52 | 19.41 | 14.85 | 20.49 | 2.75 | 0.99 | 4 | 2.17
2018-05-13 03:00 | 10135.5042 | -0.048233 | 11.7 | 18.85 | 14.41 | 20.11 | 2.75 | 0.99 | 3.5 | 2.06
2018-05-13 04:00 | 10242.8542 | -0.048233 | 11.68 | 18.59 | 14.79 | 19.52 | 2.75 | 0.97 | 3.5 | 2.01
2018-05-13 05:00 | 10823.3042 | -0.048233 | 12.06 | 18.38 | 16.09 | 20.23 | 3 | 0.99 | 20.01 | 2.8
2018-05-13 06:00 | 11824.8364 | 93.1962 | 13.25 | 18.29 | 18.02 | 21.57 | 3.5 | 2.5 | 20 | 25.5
2018-05-13 07:00 | 11585.4124 | 144.171 | 13.52 | 18.3 | 19.31 | 21.68 | 3.4 | 2.38 | 13.39 | 3.4
2018-05-13 08:00 | 13381.4818 | 309.869 | 13.73 | 20.57 | 19.73 | 22.8 | 3.12 | 2.59 | 13.42 | 3.12
2018-05-13 09:00 | 13351.7435 | 329.681 | 14.55 | 20.42 | 19.99 | 24.22 | 3.19 | 2.25 | 2.61 | 3.15
2018-05-13 10:00 | 12731.6691 | 921.757 | 15.35 | 20.27 | 19.98 | 27.35 | 4.42 | 2.25 | 2.45 | 4.25
2018-05-13 11:00 | 14123.5751 | 836.275 | 16.33 | 21.96 | 19.52 | 29.64 | 6.36 | 6 | 2.02 | 6.36
2018-05-13 12:00 | 12533.711 | 966.38 | 18.24 | 28.02 | 19.52 | 33.56 | 7.01 | 6.12 | 0.51 | 6.65
2018-05-13 13:00 | 13379.0068 | 558.523 | 20.05 | 29.64 | 19.49 | 39.54 | 9.63 | 9.92 | 0.51 | 9.92
2018-05-13 14:00 | 11467.4861 | 231.038 | 18.67 | 30.39 | 19.49 | 45.46 | 9.83 | 1.54 | 0.61 | 10
2018-05-13 15:00 | 13000.3187 | 510.577 | 42.1 | 33.08 | 19.63 | 60.4 | 22.08 | 9.61 | 1 | 19.41
2018-05-13 16:00 | 11385.6037 | 204.846 | 54.24 | 47.61 | 18.81 | 75 | 33.1 | 11.24 | 1.34 | 31.35
2018-05-13 17:00 | 11116.0158 | 44.0693 | 38.97 | 38.97 | 18.44 | 51.74 | 24.62 | 2 | 1.31 | 19.3
2018-05-13 18:00 | 11075.8906 | 9.8322 | 20.06 | 33.69 | 18.02 | 32.18 | 7.94 | 0.99 | 3.56 | 5.94
2018-05-13 19:00 | 12298.0841 | -0.048233 | 17.84 | 29.58 | 18.55 | 28.68 | 7.01 | 0.97 | 2.45 | 6.75
2018-05-13 20:00 | 12472.1591 | -0.048233 | 15.94 | 23.32 | 20.77 | 27.3 | 6.65 | 0.97 | 2 | 5.27
2018-05-13 21:00 | 11298.3042 | -0.048233 | 15.77 | 22.21 | 17.52 | 25.86 | 4.78 | 0.97 | 20 | 4.78
2018-05-13 22:00 | 10982.9042 | -0.048233 | 14.71 | 24.03 | 16.43 | 22.31 | 3.85 | 0.01 | 35.01 | 3.33
2018-05-13 23:00 | 12011.1241 | -0.048233 | 14.17 | 19.81 | 15.45 | 21.65 | 3 | 0.01 | 40 | 40.17
2018-05-14 | 10631.4042 | -0.048233 | 13.34 | 18.34 | 15.36 | 18.86 | 3.01 | 0.01 | 20 | 3.01
2018-05-14 01:00 | 11634.4891 | -0.048233 | 12.14 | 17.68 | 14.7 | 17.37 | 3 | 0.01 | 11.39 | 2
2018-05-14 02:00 | 10382.5042 | -0.048233 | 7.55 | 8.67 | 13.74 | 8.66 | 2.9 | 0.97 | 14.88 | 1.6
2018-05-14 03:00 | 10162.1042 | -0.048233 | 5.2 | 5.2 | 13.72 | 6.54 | 3 | 0.97 | 12.42 | 1.6
2018-05-14 04:00 | 11275.7891 | -0.048233 | 0.02 | 0.02 | 14.76 | 6.88 | 3 | 0.97 | 8.61 | 1.6
2018-05-14 05:00 | 11358.0791 | -0.048233 | -0.39 | -0.39 | 15.32 | 8.83 | 4 | 0.97 | 40 | 2.61
2018-05-14 06:00 | 10112.8654 | 61.1215 | -0.2 | -0.2 | 16.71 | 15.81 | 6.87 | 2.01 | 20 | 25.46
2018-05-14 07:00 | 10294.5562 | 313.375 | 5.03 | 5.03 | 16.68 | 18.05 | 4.1 | 2.31 | 3.11 | 2.61
2018-05-14 08:00 | 10487.5259 | 363.501 | 12.05 | 20.16 | 15.49 | 20.96 | 4 | 2.5 | 3.11 | 2.75
2018-05-14 09:00 | 11940.3718 | 512.888 | 12.64 | 19.02 | 16.63 | 23.17 | 4.34 | 2.25 | 0.94 | 4.25
2018-05-14 10:00 | 11118.4893 | 744.673 | 13.7 | 19.43 | 16.96 | 24.71 | 5.77 | 2.25 | 2.5 | 5.77
2018-05-14 11:00 | 11414.1293 | 908.873 | 14.22 | 21.12 | 17.05 | 25.27 | 6.46 | 6.4 | 1.44 | 6.45
2018-05-14 12:00 | 12968.4609 | 1040.38 | 15.04 | 23.09 | 16.54 | 30.32 | 5.82 | 6.07 | 0.51 | 5.62
2018-05-14 13:00 | 12922.2403 | 909.569 | 160.68 | 31.2 | 16.48 | 34.04 | 8.44 | 8.4 | 0.51 | 10.69
2018-05-14 14:00 | 13045.3598 | 957.27 | 89.19 | 32.39 | 16.48 | 40.95 | 14.78 | 10.78 | 0.61 | 14.78
2018-05-14 15:00 | 12981.2602 | 728.512 | 37.93 | 37.93 | 16.41 | 53.41 | 26.52 | 16.54 | 1 | 21.54
2018-05-14 16:00 | 12493.022 | 257.727 | 40.65 | 38.23 | 16.47 | 55.82 | 28.97 | 18.92 | 1 | 21.92
2018-05-14 17:00 | 11093.5937 | 90.4671 | 36.03 | 36.03 | 16.51 | 39.25 | 19.38 | 10.56 | 1 | 13.25
2018-05-14 18:00 | 11137.0401 | 26.2001 | 33.39 | 30.48 | 16.58 | 31.36 | 8 | 1.29 | 10.03 | 6
2018-05-14 19:00 | 12262.2141 | -0.048233 | 15.65 | 28.22 | 16.61 | 28.41 | 7.81 | 0.99 | 8.17 | 6.81
2018-05-14 20:00 | 12461.6091 | -0.048233 | 15.85 | 22.05 | 17.58 | 31.09 | 8.57 | 0.99 | 4.42 | 5.73
2018-05-14 21:00 | 11122.5542 | -0.048233 | 15.68 | 21.97 | 16.13 | 26.66 | 6.34 | 0.99 | 14.57 | 6
2018-05-14 22:00 | 12228.4541 | -0.048233 | 15.85 | 22.07 | 16.11 | 24.29 | 5.32 | 0.01 | 27.01 | 4.59
2018-05-14 23:00 | 10883.1542 | -0.048233 | 14.64 | 21.59 | 16.67 | 20.36 | 5.75 | 0.01 | 20 | 15
2018-05-15 | 11969.9791 | -0.048233 | 14.66 | 19.92 | 15.21 | 17.6 | 3.11 | 0.01 | 30 | 22.5
2018-05-15 01:00 | 10756.8042 | -0.048233 | 13.83 | 18.99 | 8.73 | 16.07 | 3 | 0.01 | 20 | 1.11
2018-05-15 02:00 | 11765.3091 | -0.048233 | 13.36 | 17.79 | 8.83 | 11.87 | 3 | 1 | 24.06 | 1.11
2018-05-15 03:00 | 10567.7542 | -0.048233 | 13.44 | 17.43 | 7.29 | 9.33 | 3 | 1 | 15.62 | 1.11
2018-05-15 04:00 | 12533.3491 | -0.048233 | 13.21 | 16.26 | 7.28 | 13.05 | 3 | 1 | 10 | 1.11
2018-05-15 05:00 | 12371.8042 | -0.048233 | 12.88 | 17.63 | 7.51 | 17.85 | 3.61 | 1 | 40 | 36.27
2018-05-15 06:00 | 14185.1995 | 94.789 | 13.3 | 19.56 | 7.57 | 20.22 | 3.21 | 2.08 | 20 | 89.1062
2018-05-15 07:00 | 17088.4226 | 217.557 | 13.27 | 19.56 | 13.33 | 21.68 | 3.1 | 2 | 2.11 | 1.9
2018-05-15 08:00 | 15946.4026 | 259.687 | 13.09 | 20.77 | 14.32 | 22.29 | 3.61 | 2 | 12 | 2.61
2018-05-15 09:00 | 17583.5148 | 357.963 | 14.24 | 20.61 | 15.57 | 24.59 | 3.85 | 2.01 | 2.11 | 2.75
2018-05-15 10:00 | 18494.8083 | 525.624 | 15.79 | 19.23 | 16.65 | 28 | 4.91 | 2.25 | 2.25 | 3.33
2018-05-15 11:00 | 17560.2465 | 1137.47 | 15.46 | 21.48 | 16.67 | 29.13 | 5.28 | 6 | 1.48 | 4.28
2018-05-15 12:00 | 20744.0958 | 1158.65 | 15.9 | 24.01 | 16.58 | 35.03 | 6.31 | 7.5 | 0.71 | 5.84
2018-05-15 13:00 | 18978.1946 | 1109.81 | 16.26 | 24.49 | 16.41 | 39.39 | 8 | 11.27 | 0.71 | 11.28
2018-05-15 14:00 | 16147.814 | 967.699 | 16.54 | 24.02 | 15.34 | 47.92 | 14.28 | 1.56 | 1 | 13.61
2018-05-15 15:00 | 15046.2111 | 770.117 | 16.23 | 27.45 | 15.53 | 61.03 | 20 | 10 | 1 | 16.25
2018-05-15 16:00 | 15604.2845 | 534.791 | 16.13 | 28.45 | 16.57 | 62.68 | 20.03 | 10.78 | 2.11 | 19.19
2018-05-15 17:00 | 13683.7677 | 242.966 | 16.02 | 26.78 | 16.61 | 41.02 | 17.63 | 1.62 | 2.11 | 13.63
2018-05-15 18:00 | 13313.9812 | 34.7171 | 15.7 | 22.02 | 15.88 | 32.59 | 7 | 1.82 | 9.18 | 5
2018-05-15 19:00 | 14816.3691 | -0.048233 | 15.39 | 20.56 | 16.7 | 30 | 4.11 | 1.42 | 7.5 | 4.11
2018-05-15 20:00 | 13263.8542 | -0.048233 | 15.55 | 21.05 | 19.35 | 30.6 | 4.72 | 1.12 | 3.01 | 4.72
2018-05-15 21:00 | 14490.3741 | -0.048233 | 15.83 | 23.03 | 16.74 | 26.24 | 6.57 | 1.2 | 11.5 | 5.35
2018-05-15 22:00 | 13876.3641 | -0.048233 | 48.77 | 19.21 | 16.48 | 25.39 | 5.39 | 0.01 | 49.8262 | 4.39
2018-05-15 23:00 | 12005.1042 | -0.048233 | 14.83 | 15.24 | 11.15 | 21.11 | 3.61 | 0.01 | 105.5334 | 15
2018-05-16 | 13057.6841 | -0.048233 | 13 | 14.39 | 17.37 | 18.69 | 6.29 | 0.01 | 30 | 30
2018-05-16 01:00 | 11608.0042 | -0.048233 | 11.28 | 13.23 | 15.99 | 16.09 | 4.25 | 0.01 | 15.25 | 1.11
2018-05-16 02:00 | 12726.4141 | -0.048233 | 10.58 | 10.58 | 14.5 | 11.23 | 4.25 | 0.99 | 15 | 1.11
2018-05-16 03:00 | 12702.1491 | -0.048233 | 11.17 | 11.17 | 13.82 | 11.85 | 4.25 | 0.99 | 15 | 1.11
2018-05-16 04:00 | 13235.9791 | -0.048233 | 10.63 | 10.63 | 14.14 | 10.8 | 4 | 0.99 | 12 | 1.11
2018-05-16 05:00 | 14226.6241 | -0.048233 | 13.5 | 17.87 | 15.37 | 17.9 | 5.61 | 0.99 | 277.7434 | 38
2018-05-16 06:00 | 14559.8588 | 88.1672 | 17.52 | 22.35 | 16.44 | 21.85 | 4.58 | 2.5 | 40.97 | 87.1162
2018-05-16 07:00 | 16424.0598 | 305.484 | 15.5 | 20.89 | 16.14 | 22.46 | 4 | 2.5 | 11 | 2.76
2018-05-16 08:00 | 18885.6215 | 467.063 | 17.24 | 21.25 | 18.09 | 22.82 | 4 | 2.5 | 20 | 3.24
2018-05-16 09:00 | 18940.6334 | 378.207 | 15.07 | 21.26 | 18.2 | 23.83 | 4.79 | 2.5 | 19.42 | 20.26
2018-05-16 10:00 | 18586.2645 | 541.489 | 15.59 | 21.91 | 18.59 | 27.46 | 5 | 10 | 11.45 | 5
2018-05-16 11:00 | 17299.0535 | 1047.53 | 15.24 | 20.18 | 19.23 | 28.84 | 5.61 | 10.48 | 2.5 | 5.61
2018-05-16 12:00 | 19235.4848 | 835.687 | 15.59 | 19.8 | 19.62 | 28.68 | 7.39 | 9.33 | 1 | 6.39
2018-05-16 13:00 | 17521.0457 | 846.206 | 17.28 | 21.17 | 19.26 | 32.72 | 8 | 12 | 1 | 12.01
2018-05-16 14:00 | 16460.8628 | 905.224 | 20.14 | 20.14 | 20.17 | 42.14 | 17.55 | 1.82 | 2.04 | 12.8
2018-05-16 15:00 | 15222.2404 | 459.411 | 276.9057 | 21.67 | 20.16 | 52.36 | 27.55 | 9.25 | 2.5 | 24
2018-05-16 16:00 | 14594.4928 | 524.624 | 904.4311 | 22.33 | 21 | 54.88 | 27.87 | 16.16 | 15 | 24
2018-05-16 17:00 | 13948.5935 | 243.73 | 17.44 | 22.11 | 21.17 | 37.69 | 26.32 | 10.25 | 20 | 14.25
2018-05-16 18:00 | 14890.9201 | 34.6162 | 16.38 | 21.35 | 21.49 | 33.17 | 14.69 | 0.99 | 22.02 | 11.44
2018-05-16 19:00 | 14857.5141 | -0.048233 | 14.85 | 19.28 | 21.48 | 28.98 | 6.21 | 0.99 | 9.11 | 5.21
2018-05-16 20:00 | 13310.4042 | -0.048233 | 15.4 | 20.11 | 21.79 | 29.19 | 7.87 | 0.99 | 3.5 | 11.35
2018-05-16 21:00 | 14793.1591 | -0.048233 | 51.63 | 20.93 | 20.3 | 28.22 | 4.47 | 0.99 | 20 | 4.27
2018-05-16 22:00 | 14215.0191 | -0.048233 | 12.63 | 16.35 | 17.48 | 26.21 | 4.51 | 0.01 | 40 | 19.42
2018-05-16 23:00 | 12405.0542 | -0.048233 | 12.08 | 20.4 | 15.61 | 21.11 | 6.29 | 0.01 | 105.5334 | 29.81
2018-05-17 | 12249.2542 | -0.048233 | 8.11 | 17.97 | 15.35 | 19.18 | 3.95 | 0.01 | 40 | 38.05
2018-05-17 01:00 | 11624.1542 | -0.048233 | 7.71 | 15.65 | 13.97 | 18.16 | 3 | 0.01 | 20 | 2.45
2018-05-17 02:00 | 12696.8741 | -0.048233 | 6.01 | 16.22 | 12.66 | 16.9 | 3 | 0.99 | 20 | 2.11
2018-05-17 03:00 | 11442.7042 | -0.048233 | 8.53 | 11.59 | 11.6 | 16.65 | 3 | 0.99 | 15 | 2.25
2018-05-17 04:00 | 12520.9542 | -0.048233 | 12.52 | 17.22 | 11.48 | 20 | 3 | 1.22 | 11.85 | 2.51
2018-05-17 05:00 | 15082.2291 | -0.048233 | 13.64 | 16.01 | 11.42 | 21.71 | 4.5 | 1 | 57.6962 | 30
2018-05-17 06:00 | 17029.8159 | 86.0056 | 12.28 | 20.99 | 11.55 | 22.83 | 3.89 | 2.04 | 20 | 87.1162
2018-05-17 07:00 | 16531.7879 | 308.882 | 12.86 | 19.6 | 14.66 | 23.53 | 3.01 | 2.4 | 10 | 2.11
2018-05-17 08:00 | 19189.8993 | 564.478 | 12.14 | 19.66 | 17.62 | 23.98 | 3.85 | 2.5 | 14.45 | 2.75
2018-05-17 09:00 | 19738.6248 | 683.597 | 12.73 | 23.76 | 18.18 | 26.79 | 3.85 | 2.5 | 13.48 | 3.01
2018-05-17 10:00 | 18348.9679 | 790.703 | 61.38 | 61.38 | 18.9 | 30.77 | 4.35 | 2.71 | 14.32 | 4.15
2018-05-17 11:00 | 17680.9915 | 1115.57 | 60.64 | 60.64 | 18.92 | 33.76 | 5.82 | 7.5 | 2.11 | 5.62
2018-05-17 12:00 | 20093.8992 | 1112.35 | 14.7 | 26.2 | 18.28 | 43.71 | 8.38 | 7.5 | 1 | 7.38
2018-05-17 13:00 | 19681.1727 | 1108.14 | 16.87 | 28.63 | 18.93 | 50.89 | 19.75 | 10.83 | 1 | 19.55
2018-05-17 14:00 | 16263.9392 | 871.936 | 124.85 | 32.24 | 18.62 | 63.99 | 20.02 | 12.27 | 1 | 19.82
2018-05-17 15:00 | 15732.1862 | 726.196 | 21.84 | 29.4 | 29.88 | 71 | 30.45 | 23.08 | 2.11 | 31.28
2018-05-17 16:00 | 16685.4812 | 425.622 | 16.15 | 35.34 | 32.68 | 72.6 | 27.5 | 17.9 | 2.5 | 27.5
2018-05-17 17:00 | 16027.694 | 238.127 | 16.9 | 32.45 | 34.18 | 54.26 | 21.94 | 16.82 | 2.61 | 20.32
2018-05-17 18:00 | 13694.5271 | 38.2917 | 17.1 | 28.34 | 31.66 | 45.26 | 15.68 | 11.62 | 12.46 | 14.12
2018-05-17 19:00 | 15143.4191 | -0.048233 | 15.42 | 29.15 | 30.11 | 35.51 | 5.87 | 7.96 | 3.65 | 4.87
2018-05-17 20:00 | 15064.2941 | -0.048233 | 32.58 | 32.58 | 33.87 | 37.92 | 6.91 | 1.49 | 3.46 | 11
2018-05-17 21:00 | 15080.1191 | -0.048233 | 32.04 | 32.04 | 16.93 | 30.05 | 5.2 | 1.42 | 14.38 | 4.45
2018-05-17 22:00 | 13084.3042 | -0.048233 | 15.34 | 23.45 | 15.64 | 31.07 | 3.62 | 0.01 | 52.7862 | 3.01
2018-05-17 23:00 | 12573.2042 | -0.048233 | 12.29 | 21.47 | 16.04 | 22.8 | 5.75 | 0.01 | 40 | 20.5
2018-05-18 | 13800.4041 | -0.048233 | 11.66 | 14.88 | 15.84 | 21.41 | 4.5 | 0.01 | 20 | 2.61
2018-05-18 01:00 | 12301.5042 | -0.048233 | 12.75 | 15.66 | 15.27 | 19.26 | 3 | 0.01 | 19.14 | 1.61
2018-05-18 02:00 | 12250.2042 | -0.048233 | 5.15 | 5.15 | 15.27 | 18 | 3 | 0.99 | 15 | 1.11
2018-05-18 03:00 | 12254.0042 | -0.048233 | 9.14 | 9.14 | 15.28 | 17.81 | 3 | 0.97 | 15 | 1.32
2018-05-18 04:00 | 13038.7042 | -0.048233 | 11.75 | 11.75 | 15.34 | 18.34 | 3 | 0.97 | 12 | 1.61
2018-05-18 05:00 | 14015.3042 | -0.048233 | 12.75 | 13.88 | 16.25 | 20.95 | 5.5 | 0.97 | 277.7434 | 3.01
2018-05-18 06:00 | 15639.7118 | 85.8545 | 14.65 | 21.56 | 17.8 | 21.92 | 5 | 2.42 | 20 | 25.5
2018-05-18 07:00 | 16567.372 | 316.339 | 14.97 | 21.48 | 16.95 | 21.67 | 4.38 | 2.01 | 2.61 | 2.43
2018-05-18 08:00 | 18861.7342 | 511.421 | 14.98 | 21.08 | 17.15 | 22 | 4.56 | 2.1 | 10.92 | 2.95
2018-05-18 09:00 | 17623.9668 | 776.544 | 14.38 | 19.42 | 17.48 | 22.72 | 3.31 | 2.41 | 2.11 | 2.54
2018-05-18 10:00 | 17970.2332 | 948.035 | 15.29 | 17.18 | 31.67 | 26.35 | 5.01 | 2.25 | 2.5 | 3.42
2018-05-18 11:00 | 20258.2049 | 1091.09 | 56.27 | 20.54 | 33.78 | 27.71 | 5.01 | 7.1 | 1 | 3.8
2018-05-18 12:00 | 20773.2591 | 820.293 | 46.72 | 22.26 | 35.93 | 38.88 | 5.59 | 8.1 | 0.54 | 16.06
2018-05-18 13:00 | 21901.9899 | 1062.18 | 116.26 | 31.17 | 39.36 | 44.4 | 25.22 | 15 | 0.71 | 24.22
2018-05-18 14:00 | 19119.8146 | 806.047 | 105.45 | 33.27 | 46.42 | 56.67 | 26.72 | 19.72 | 1 | 25.92
2018-05-18 15:00 | 16110.8163 | 762.754 | 957.7511 | 34.92 | 51.23 | 70.63 | 39.72 | 54.8273 | 1 | 39.72
2018-05-18 16:00 | 16705.5526 | 507.647 | 111.98 | 40.07 | 51.21 | 67.1 | 37.34 | 26.74 | 2.11 | 36.34
2018-05-18 17:00 | 16318.1102 | 243.403 | 45.21 | 45.21 | 51.2 | 49.58 | 21.35 | 17 | 2.11 | 19.76
2018-05-18 18:00 | 15746.3502 | 37.4504 | 30.12 | 30.12 | 43.4 | 34.71 | 16.13 | 12.72 | 10.03 | 15
2018-05-18 19:00 | 14091.3042 | -0.048233 | 29.09 | 29.08 | 37.6 | 35.15 | 6.01 | 0.97 | 3.5 | 4.01
2018-05-18 20:00 | 13951.6542 | -0.048233 | 44.67 | 44.67 | 36.92 | 34.52 | 8.34 | 0.97 | 2.33 | 11.47
2018-05-18 21:00 | 13919.3542 | -0.048233 | 33.45 | 33.45 | 16.74 | 28.15 | 6.84 | 0.97 | 10 | 4.59
2018-05-18 22:00 | 13510.8542 | -0.048233 | 38.95 | 29 | 15.53 | 26.05 | 5.01 | 0.01 | 40.48 | 15
2018-05-18 23:00 | 14251.9441 | -0.048233 | 15.74 | 23.97 | 15.19 | 22.22 | 5.01 | 0.01 | 22 | 21.53
2018-05-19 | 13855.2641 | -0.048233 | 13.43 | 19.97 | 14.67 | 22.51 | 3.44 | 0.01 | 12 | 2.51
2018-05-19 01:00 | 13716.0041 | -0.048233 | 13.16 | 19.35 | 11.13 | 19.97 | 3 | 0.01 | 10 | 1
2018-05-19 02:00 | 12278.7042 | -0.048233 | 12.78 | 19.86 | 10.6 | 18.75 | 3 | 0.97 | 3.5 | 1
2018-05-19 03:00 | 12274.9042 | -0.048233 | 12.67 | 18.28 | 8.94 | 18.41 | 3 | 0.97 | 3.11 | 1
2018-05-19 04:00 | 14572.6641 | -0.048233 | 12.79 | 19.53 | 10.58 | 19.46 | 3 | 0.97 | 2.61 | 1
2018-05-19 05:00 | 15722.6141 | -0.048233 | 14.2 | 19.6 | 15.08 | 22.34 | 4.75 | 0.99 | 57.6962 | 2.75
2018-05-19 06:00 | 15728.7831 | 88.6138 | 11.36 | 19.98 | 16.6 | 23.17 | 4.76 | 1 | 12.16 | 25.5
2018-05-19 07:00 | 16444.233 | 300.719 | 16.78 | 24.22 | 17.53 | 22 | 4 | 1 | 2.11 | 2.11
2018-05-19 08:00 | 18449.1964 | 599.39 | 17.07 | 20.64 | 18.18 | 22.78 | 4 | 1 | 3.5 | 2.36
2018-05-19 09:00 | 19260.4746 | 828.374 | 18.28 | 29.21 | 19.22 | 23.71 | 4.76 | 2.5 | 2.11 | 2.5
2018-05-19 10:00 | 19779.5641 | 960.402 | 38.67 | 30.42 | 19.12 | 28.19 | 5 | 2.25 | 2.5 | 3.06
2018-05-19 11:00 | 18167.116 | 1146.28 | 17.13 | 29.63 | 25.28 | 29.73 | 5.59 | 2.59 | 2 | 2.96
2018-05-19 12:00 | 19336.9175 | 1158.65 | 17.97 | 28.36 | 31.16 | 35.14 | 5.91 | 7.5 | 1 | 3.34
2018-05-19 13:00 | 20405.4091 | 1156.62 | 17.09 | 33.89 | 32.94 | 40.28 | 7.75 | 10 | 1 | 9.81
2018-05-19 14:00 | 19158.8422 | 1005.04 | 320.5457 | 276.22 | 30.74 | 53.83 | 16.41 | 13 | 1 | 16.41
2018-05-19 15:00 | 17584.51 | 797.782 | 389.0257 | 344.7 | 19.22 | 61.64 | 25.63 | 20 | 2 | 28.1
2018-05-19 16:00 | 14980.3723 | 513.813 | 346.0957 | 301.77 | 17.49 | 62.23 | 28.19 | 18.03 | 2.5 | 24.03
2018-05-19 17:00 | 14527.4161 | 239.017 | 686.9211 | 419.31 | 16.5 | 40.53 | 18.88 | 14.5 | 3.5 | 16.91
2018-05-19 18:00 | 14113.9267 | 44.765 | 15.9 | 30.87 | 15.03 | 37.03 | 8.18 | 1.45 | 11.55 | 4.72
2018-05-19 19:00 | 13919.3542 | -0.048233 | 15.96 | 29.33 | 15.47 | 31.86 | 6.48 | 0.97 | 8.83 | 4
2018-05-19 20:00 | 13717.0042 | -0.048233 | 16.51 | 28.44 | 18.8 | 34.13 | 8 | 0.97 | 3.5 | 6.4
2018-05-19 21:00 | 14939.8041 | -0.048233 | 36.88 | 36.88 | 14.63 | 28.16 | 4.76 | 0.97 | 17.44 | 3.53
2018-05-19 22:00 | 14472.4391 | -0.048233 | 19.5 | 28.87 | 14.1 | 27.91 | 8.01 | 0.01 | 24.64 | 15.45
2018-05-19 23:00 | 12563.7042 | -0.048233 | 13.58 | 26.18 | 13.95 | 24.44 | 6.68 | 0.01 | 16.47 | 2.75
2018-05-20 | 12380.3542 | -0.048233 | 12.72 | 21.29 | 15.4 | 25.18 | 3.39 | 0.01 | 10.28 | 2.26
2018-05-20 01:00 | 12249.2542 | -0.048233 | 12.22 | 19.65 | 15.01 | 21.45 | 3 | 0.01 | 10.76 | 1
2018-05-20 02:00 | 13556.6991 | -0.048233 | 11.9 | 18.16 | 13.63 | 20.42 | 2.89 | 1 | 3.86 | 1
2018-05-20 03:00 | 12137.1542 | -0.048233 | 11.68 | 17.11 | 13.48 | 19.38 | 3 | 1 | 2.61 | 1
2018-05-20 04:00 | 12159.0042 | -0.048233 | 11.87 | 16.53 | 13.67 | 18.99 | 3 | 1 | 2.11 | 1
2018-05-20 05:00 | 14437.6241 | -0.048233 | 12.27 | 16.97 | 15.41 | 20.2 | 5 | 1 | 112.7434 | 2.76
2018-05-20 06:00 | 13513.6972 | 86.9444 | 13.21 | 17.98 | 15.45 | 22.65 | 3.55 | 2.5 | 12.07 | 28
2018-05-20 07:00 | 15268.5244 | 325.535 | 13.64 | 18.14 | 15.91 | 22.68 | 3.31 | 2 | 1 | 2.85
2018-05-20 08:00 | 15461.6285 | 300.572 | 13.68 | 18.49 | 15.66 | 23.86 | 4 | 2.25 | 1 | 3.4
2018-05-20 09:00 | 15857.6069 | 604.907 | 13.98 | 19.59 | 16.26 | 27.15 | 4.93 | 2.5 | 2.61 | 4.24
2018-05-20 10:00 | 16396.0399 | 1018.27 | 14.36 | 22.25 | 16.49 | 33.73 | 5 | 2.07 | 2.5 | 4.07
2018-05-20 11:00 | 16484.8044 | 966.407 | 14.66 | 23.7 | 18.69 | 35.18 | 5.89 | 8.1 | 2 | 5.58
2018-05-20 12:00 | 16679.4023 | 1123.86 | 15.95 | 30.17 | 19.03 | 35.79 | 8.27 | 7.5 | 1 | 6.34
2018-05-20 13:00 | 16398.2237 | 1110.34 | 43.7 | 43.7 | 17.95 | 38.83 | 12.24 | 9.91 | 0.9 | 10.97
2018-05-20 14:00 | 14213.7765 | 1007.87 | 29.44 | 28.85 | 18 | 47.57 | 25 | 16.8 | 1.82 | 22.8
2018-05-20 15:00 | 13905.529 | 797.399 | 28.95 | 28.95 | 18.97 | 52.79 | 32.05 | 23 | 2.11 | 31.2
2018-05-20 16:00 | 13695.6845 | 538.51 | 29.57 | 27.27 | 19.42 | 56.49 | 34.51 | 23 | 2.11 | 32.6
2018-05-20 17:00 | 13392.5214 | 243.391 | 28.1 | 28.1 | 19.87 | 43.15 | 16.56 | 13.01 | 2.31 | 15.21
2018-05-20 18:00 | 13089.6996 | 39.6312 | 18.07 | 30.93 | 16.95 | 33.47 | 7.33 | 1.22 | 8.31 | 5.52
2018-05-20 19:00 | 12960.8042 | -0.048233 | 17.4 | 32.02 | 17.25 | 32.96 | 7.57 | 0.97 | 3.5 | 7.04
2018-05-20 20:00 | 12961.7542 | -0.048233 | 15.52 | 25.78 | 18.46 | 32.83 | 7.87 | 0.97 | 3.11 | 6.01
2018-05-20 21:00 | 12886.7042 | -0.048233 | 14.2 | 34.38 | 14.08 | 31.05 | 5.2 | 0.97 | 11.85 | 5.2
2018-05-20 22:00 | 13923.8391 | -0.048233 | 310.8757 | 266.55 | 13.27 | 28.16 | 8.24 | 0.01 | 29.46 | 3.24
2018-05-20 23:00 | 13663.2541 | -0.048233 | 65.65 | 65.65 | 13.48 | 22.92 | 6.01 | 0.01 | 18.75 | 2.76
2018-05-21 | 13514.4991 | -0.048233 | 10.7 | 40.43 | 12.19 | 21.39 | 3.45 | 0.01 | 13 | 3.45
2018-05-21 01:00 | 13491.2891 | -0.048233 | 10.62 | 29.57 | 10.37 | 20.14 | 3 | 0.01 | 10.61 | 2.11
2018-05-21 02:00 | 13262.3541 | -0.048233 | 7.52 | 18.66 | 10.14 | 19.12 | 3 | 0.99 | 3.23 | 2
2018-05-21 03:00 | 13212.7691 | -0.048233 | 0.65 | 21.92 | 7.15 | 18.81 | 3 | 0.99 | 2.83 | 2
2018-05-21 04:00 | 13260.2441 | -0.048233 | 6 | 27.14 | 9.7 | 18.66 | 2.9 | 0.99 | 2.61 | 2
2018-05-21 05:00 | 12274.9042 | -0.048233 | 58.83 | 58.83 | 9.02 | 19.22 | 4.35 | 0.99 | 20 | 4
2018-05-21 06:00 | 12610.8243 | 85.5519 | 87.77 | 87.77 | 11.64 | 21.94 | 5 | 2.5 | 10 | 28
2018-05-21 07:00 | 14131.0023 | 313.315 | 57.96 | 57.96 | 12.28 | 21.05 | 3.61 | 2.1 | 1.14 | 2.49
2018-05-21 08:00 | 14469.0064 | 584.698 | 11.96 | 22.64 | 12.7 | 21.81 | 3.56 | 2.1 | 2.11 | 2.61
2018-05-21 09:00 | 14846.2512 | 847.276 | 13.58 | 19.43 | 13.09 | 23.03 | 4.65 | 2.5 | 0.71 | 3.01
2018-05-21 10:00 | 13604.817 | 1034.86 | 13.62 | 18.94 | 13.77 | 26.1 | 5 | 1.5 | 2.5 | 4
2018-05-21 11:00 | 13693.4995 | 1053.21 | 14 | 19.82 | 13.42 | 26.5 | 5.88 | 2.13 | 1 | 5.88
2018-05-21 12:00 | 13843.3335 | 1057.93 | 19.96 | 21.6 | 12.15 | 36.06 | 7.1 | 2.5 | 1 | 5.1
2018-05-21 13:00 | 13841.4715 | 1110.97 | 15.71 | 22.15 | 12.08 | 34.6 | 14.36 | 8.71 | 1 | 8
2018-05-21 14:00 | 15121.1568 | 1020.85 | 17.28 | 21.87 | 11.84 | 38.85 | 20.47 | 17.06 | 1 | 19.47
2018-05-21 15:00 | 13441.7115 | 808.17 | 17.77 | 21.12 | 11.94 | 47.83 | 29.17 | 20 | 2 | 27.9
2018-05-21 16:00 | 14696.0508 | 548.906 | 17.87 | 21.51 | 12.06 | 48.7 | 35.69 | 12.18 | 2 | 26.87
2018-05-21 17:00 | 12799.2122 | 246.855 | 17.69 | 20.84 | 12.09 | 40.18 | 15.38 | 3 | 1.23 | 11.36
2018-05-21 18:00 | 12542.8437 | 35.9934 | 16.39 | 19.98 | 12.14 | 31.85 | 5 | 1.57 | 8.11 | 5
2018-05-21 19:00 | 13948.1041 | -0.048233 | 15.38 | 20.64 | 13.65 | 31.45 | 5 | 0.99 | 3.78 | 5
2018-05-21 20:00 | 12638.7542 | -0.048233 | 14.94 | 20.96 | 15.66 | 31.49 | 7.92 | 0.99 | 2.61 | 5.92
2018-05-21 21:00 | 13915.3991 | -0.048233 | 15.2 | 20.86 | 12.17 | 28.38 | 5.04 | 0.99 | 11.56 | 4.04
2018-05-21 22:00 | 12378.4542 | -0.048233 | 15.08 | 23.3 | 12.16 | 24.57 | 8.81 | 0.01 | 26.57 | 10
2018-05-21 23:00 | 12243.5542 | -0.048233 | 13.99 | 19.71 | 10.11 | 21.92 | 8 | 0.01 | 17.31 | 7.11
2018-05-22 | 12199.8542 | -0.048233 | 58.66 | 58.66 | 11.66 | 21.43 | 3.25 | 0.01 | 10 | 3.11
2018-05-22 01:00 | 12083.0042 | -0.048233 | 61.6 | 61.6 | 10.55 | 20.25 | 3 | 0.01 | 10.29 | 2.25
2018-05-22 02:00 | 13355.1941 | -0.048233 | 10.5 | 20.34 | 7.72 | 19.79 | 3 | 1 | 3.27 | 2
2018-05-22 03:00 | 11936.7042 | -0.048233 | 7.95 | 23.36 | 7.11 | 19.7 | 3 | 1 | 3.5 | 2.01
2018-05-22 04:00 | 14323.6841 | -0.048233 | 10.92 | 21.61 | 7.07 | 19.81 | 3 | 1 | 3.5 | 2.11
2018-05-22 05:00 | 13792.0542 | -0.048233 | 11.39 | 40.01 | 8.61 | 21.73 | 5 | 1.22 | 20 | 4.76
2018-05-22 06:00 | 16429.355 | 45.8483 | 11.77 | 22.65 | 9.69 | 25.86 | 5 | 1.99 | 10.2 | 15
2018-05-22 07:00 | 15977.7602 | 325.695 | 12.19 | 22.12 | 10.31 | 24.8 | 3.01 | 1.99 | 2.61 | 2.11
2018-05-22 08:00 | 16019.83 | 579.979 | 12.95 | 21.37 | 10.92 | 24.26 | 3.01 | 1.99 | 3.5 | 2.49
2018-05-22 09:00 | 18782.4519 | 809.002 | 14.59 | 21.61 | 11.91 | 26.52 | 3.61 | 2 | 1 | 2.61
2018-05-22 10:00 | 17146.7542 | 727.215 | 14.85 | 22.37 | 11.9 | 35.01 | 4.72 | 1 | 2.4 | 3.66
2018-05-22 11:00 | 18998.0359 | 955.617 | 14.44 | 22.18 | 12.1 | 35.06 | 6.53 | 1.72 | 1 | 5.79
2018-05-22 12:00 | 17342.1341 | 960.878 | 17.48 | 23.38 | 12.83 | 41.47 | 5.73 | 2.25 | 0.61 | 5.22
2018-05-22 13:00 | 17381.068 | 870.861 | 17.37 | 26.65 | 12.01 | 42.33 | 6.45 | 7.66 | 0.61 | 5.13
2018-05-22 14:00 | 16444.0829 | 909.561 | 30.07 | 30.07 | 11.81 | 47.25 | 13.62 | 0.99 | 1 | 12.62
2018-05-22 15:00 | 16997.5871 | 745.457 | 36.41 | 36.41 | 11.89 | 57.69 | 19.35 | 12.75 | 1.31 | 18.74
2018-05-22 16:00 | 14400.1123 | 525.013 | 20.68 | 29.59 | 12.52 | 57.29 | 18.76 | 1.71 | 1.71 | 13.13
2018-05-22 17:00 | 13680.3562 | 230.375 | 17.33 | 31.62 | 12.89 | 44.62 | 7.72 | 1 | 2.11 | 5.62
2018-05-22 18:00 | 14758.4421 | 37.0446 | 16.94 | 28.16 | 14.35 | 37.25 | 6.17 | 0.99 | 19.85 | 4.89
2018-05-22 19:00 | 14743.5741 | -0.048233 | 16.94 | 29.87 | 14.99 | 33.47 | 5.01 | 0.99 | 3.11 | 4
2018-05-22 20:00 | 14616.9741 | -0.048233 | 14.9 | 28.91 | 15.37 | 37.13 | 4.58 | 0.99 | 2.61 | 3.36
2018-05-22 21:00 | 14496.7041 | -0.048233 | 151.57 | 25.91 | 12.98 | 33.35 | 5.13 | 0.99 | 10.03 | 4.13
2018-05-22 22:00 | 13956.5441 | -0.048233 | 15.64 | 26.52 | 13.05 | 29.5 | 6.68 | 0.01 | 35 | 15
2018-05-22 23:00 | 12180.8542 | -0.048233 | 19.43 | 21.89 | 11.71 | 24.62 | 7.61 | 0.01 | 20 | 13
2018-05-23 | 12175.1542 | -0.048233 | 13.71 | 22.02 | 11.81 | 27.26 | 3.59 | 0.01 | 10.72 | 3.59
2018-05-23 01:00 | 12122.9042 | -0.048233 | 12.19 | 21.65 | 9.81 | 25.37 | 3 | 0.01 | 12.87 | 2.11
2018-05-23 02:00 | 12052.6042 | -0.048233 | 3.4 | 19.77 | 9.94 | 24.38 | 3 | 1 | 8.45 | 2.01
2018-05-23 03:00 | 13357.3041 | -0.048233 | 5.12 | 18.75 | 8.66 | 23.44 | 3 | 1 | 2.62 | 2.11
2018-05-23 04:00 | 14318.4091 | -0.048233 | 3.74 | 18.34 | 9.75 | 23.59 | 3 | 1 | 2.55 | 2.01
2018-05-23 05:00 | 13377.8542 | -0.048233 | 7.2 | 19.54 | 12.19 | 24.31 | 4.59 | 1 | 15.8 | 4.59
2018-05-23 06:00 | 14969.2889 | 86.1462 | 11.9 | 22.21 | 15.37 | 30.09 | 5 | 1 | 3.5 | 15
2018-05-23 07:00 | 17659.1091 | 313.492 | 12.62 | 19.15 | 14.28 | 25.23 | 5 | 1.22 | 2.61 | 2.76
2018-05-23 08:00 | 18366.3758 | 568.887 | 13.54 | 19.4 | 14.47 | 23.89 | 5.5 | 1.5 | 9.29 | 3.01
2018-05-23 09:00 | 17228.4153 | 718.174 | 8.59 | 18.71 | 14.97 | 27.02 | 4 | 1.75 | 2.31 | 3.01
2018-05-23 10:00 | 19858.112 | 787.855 | 157.82 | 20.81 | 14.92 | 30.09 | 4 | 1.5 | 1.84 | 4
2018-05-23 11:00 | 19485.0693 | 1089.26 | 16.97 | 23.38 | 15.41 | 29.99 | 5.78 | 1.5 | 0.71 | 5.64
2018-05-23 12:00 | 20957.9864 | 1073.39 | 17.05 | 26 | 15.54 | 37.82 | 5.35 | 1.5 | 0.47 | 5.35
2018-05-23 13:00 | 17874.9245 | 1076.71 | 41.05 | 41.05 | 16.73 | 39.59 | 5.68 | 8.46 | 0.51 | 5.01
2018-05-23 14:00 | 18692.5755 | 984.081 | 1340.9011 | 1073.29 | 16.22 | 48.42 | 6.2 | 1.25 | 0.61 | 10.44
2018-05-23 15:00 | 15591.419 | 797.02 | 142.26 | 142.26 | 16.47 | 56.82 | 19.84 | 9.28 | 1 | 18.74
2018-05-23 16:00 | 14907.1483 | 543.735 | 180.66 | 180.66 | 16.92 | 57.9 | 23.43 | 9.75 | 1 | 21.57
2018-05-23 17:00 | 14136.8284 | 247.872 | 646.4711 | 378.86 | 16.99 | 44.02 | 5.76 | 2.14 | 0.71 | 5.76
2018-05-23 18:00 | 15132.7403 | 41.8297 | 15.63 | 41.62 | 16.98 | 37.44 | 5.23 | 1.08 | 10.95 | 5.22
2018-05-23 19:00 | 13653.3542 | -0.048233 | 15.58 | 33.14 | 17 | 33.36 | 5.84 | 0.97 | 2.61 | 4.64
2018-05-23 20:00 | 14798.4341 | -0.048233 | 15.47 | 28.73 | 16.98 | 40.56 | 5 | 0.97 | 2 | 3.5
2018-05-23 21:00 | 12629.2542 | -0.048233 | 16.75 | 36.48 | 14.74 | 34.72 | 4.88 | 0.97 | 7 | 3.88
2018-05-23 22:00 | 13289.7841 | -0.048233 | 17.51 | 23.84 | 11.97 | 31.07 | 4.57 | 0.01 | 20.93 | 3.58
2018-05-23 23:00 | 11145.3542 | -0.048233 | 13.56 | 16.15 | 12.01 | 25.88 | 7.11 | 0.01 | 11.77 | 11.64
2018-05-24 | 10825.2042 | -0.048233 | 8.61 | 8.61 | 12.64 | 22.62 | 3.59 | 0.01 | 9.69 | 2.61
2018-05-24 01:00 | 11783.2441 | -0.048233 | 11.12 | 11.12 | 11.76 | 20.67 | 2.99 | 0.01 | 11.74 | 1.68
2018-05-24 02:00 | 11488.8991 | -0.048233 | 12.01 | 14.75 | 10.56 | 19.82 | 2.22 | 1 | 4.11 | 2
2018-05-24 03:00 | 11321.1541 | -0.048233 | 5.25 | 9.31 | 8.82 | 19.73 | 2.59 | 1 | 3.5 | 1.68
2018-05-24 04:00 | 10777.7042 | -0.048233 | 10.35 | 16.81 | 8.8 | 20.02 | 2.61 | 1 | 2.61 | 1.68
2018-05-24 05:00 | 11533.9042 | -0.048233 | 12.83 | 20.5 | 8.84 | 21.7 | 4 | 1 | 16.72 | 2.96
2018-05-24 06:00 | 14403.8297 | 85.9191 | 16.63 | 20.62 | 10.56 | 26 | 4.3 | 1.22 | 3.98 | 4.3
2018-05-24 07:00 | 15435.6596 | 315.957 | 14.31 | 20.1 | 11.52 | 24.3 | 3.51 | 1.22 | 2 | 2.34
2018-05-24 08:00 | 15908.2342 | 583.895 | 16.68 | 19.37 | 14.27 | 24.3 | 6 | 1.75 | 9.01 | 3.85
2018-05-24 09:00 | 14999.4274 | 794.871 | 14.64 | 20.16 | 17.08 | 24.24 | 3.75 | 1.75 | 1.32 | 3.75
2018-05-24 10:00 | 15414.9736 | 959.288 | 15.86 | 20.01 | 16.1 | 27.79 | 4 | 10.22 | 2.5 | 4
2018-05-24 11:00 | 14654.5575 | 1009.85 | 17.75 | 19.16 | 17.01 | 28.71 | 5.17 | 8.29 | 1 | 5.17
2018-05-24 12:00 | 18661.1459 | 1105.29 | 17.53 | 20.31 | 17.62 | 30.06 | 4.86 | 7.5 | 0.51 | 4.86
2018-05-24 13:00 | 15404.174 | 1085.92 | 19.36 | 21.29 | 17.65 | 33.49 | 5.44 | 8.23 | 0.51 | 5.44
2018-05-24 14:00 | 14815.9758 | 990.764 | 19.83 | 23.12 | 17.6 | 39.54 | 6.71 | 1.59 | 0.71 | 6.05
2018-05-24 15:00 | 13743.2918 | 796.623 | 69.76 | 26.39 | 17.69 | 45.53 | 24.47 | 10.75 | 1 | 20.5
2018-05-24 16:00 | 12989.407 | 548.06 | 173.06 | 33.52 | 17.9 | 48.56 | 27.73 | 9 | 1 | 25.14
2018-05-24 17:00 | 12432.6329 | 248.982 | 122.76 | 31.05 | 17.88 | 43.43 | 17.94 | 2.5 | 1 | 12.06
2018-05-24 18:00 | 13303.6472 | 40.0921 | 19.08 | 31.86 | 16.63 | 36.15 | 5.39 | 0.99 | 10 | 4.82
2018-05-24 19:00 | 12039.3042 | -0.048233 | 17.39 | 31.84 | 16.78 | 33.53 | 5.88 | 1.35 | 2.61 | 4.29
2018-05-24 20:00 | 13354.1391 | -0.048233 | 17.86 | 28.14 | 17.45 | 31.23 | 5.31 | 1.27 | 2.11 | 4.44
2018-05-24 21:00 | 11870.2042 | -0.048233 | 17.73 | 22.17 | 16.02 | 28.26 | 3.94 | 1 | 10 | 3.52
2018-05-24 22:00 | 11425.6042 | -0.048233 | 18.02 | 19.79 | 15.64 | 25.16 | 4.79 | 0.01 | 20 | 4.29
2018-05-24 23:00 | 12042.7741 | -0.048233 | 14.76 | 19.08 | 14.33 | 22.35 | 6.75 | 0.01 | 35 | 50
2018-05-25 | 11868.6991 | -0.048233 | 3.17 | 3.17 | 14.15 | 18.77 | 3.61 | 0.01 | 20 | 3.37
2018-05-25 01:00 | 11822.2791 | -0.048233 | 0.01 | 0.94 | 9.87 | 7.2 | 3 | 0.01 | 17.46 | 1.68
2018-05-25 02:00 | 11752.6491 | -0.048233 | -0.61 | -0.49 | 5.12 | 5.34 | 3 | 0.99 | 15 | 1.61
2018-05-25 03:00 | 11749.4841 | -0.048233 | -0.71 | -0.71 | 4.2 | 6.32 | 3 | 0.99 | 15 | 1.68
2018-05-25 04:00 | 12778.1091 | -0.048233 | -0.51 | -0.51 | 4.15 | 7.09 | 3 | 0.99 | 12.59 | 1.68
2018-05-25 05:00 | 12707.1542 | -0.048233 | -0.15 | -0.15 | 6.14 | 16.89 | 3.61 | 0.99 | 39.95 | 35.91
2018-05-25 06:00 | 15816.1841 | 86.6437 | 13.64 | 17.62 | 6.66 | 23.91 | 20 | 2.88 | 20 | 90.6262
2018-05-25 07:00 | 15375.4394 | 318.673 | 12.49 | 17.42 | 14.81 | 21.76 | 3.61 | 2.5 | 2.61 | 2.61
2018-05-25 08:00 | 16038.8994 | 480.052 | 10.42 | 17.92 | 17.05 | 21.43 | 6 | 3.11 | 10.12 | 4.01
2018-05-25 09:00 | 19297.3553 | 751.332 | 17.39 | 17.39 | 17.35 | 22.16 | 4 | 3 | 1.01 | 4
2018-05-25 10:00 | 17397.407 | 1011.06 | 18.07 | 18.07 | 17.79 | 24.23 | 4 | 6 | 2.5 | 4
2018-05-25 11:00 | 17337.025 | 1124.5 | 19.03 | 19.03 | 18.81 | 27.06 | 6.59 | 6 | 1 | 6.51
2018-05-25 12:00 | 21063.7608 | 1158.65 | 18.5 | 18.5 | 19.41 | 30.52 | 6.59 | 7.5 | 0.51 | 5.59
2018-05-25 13:00 | 19622.6729 | 1124.69 | 21.07 | 21.07 | 19.57 | 37.06 | 5.81 | 10 | 0.6 | 5.45
2018-05-25 14:00 | 16967.1805 | 999.19 | 73.73 | 23.25 | 20.16 | 48.48 | 15.7 | 11.58 | 0.71 | 14.42
2018-05-25 15:00 | 17197.1235 | 800.591 | 40.32 | 25.5 | 20.34 | 59.37 | 25.87 | 13.84 | 1 | 23.79
2018-05-25 16:00 | 16306.004 | 538.928 | 67.94 | 41.44 | 20.57 | 66.36 | 31.29 | 15.72 | 1 | 29.44
2018-05-25 17:00 | 14317.297 | 253.839 | 32.39 | 32.39 | 20.75 | 57.52 | 23.29 | 12.3 | 0.71 | 18.91
2018-05-25 18:00 | 15238.6721 | 42.239 | 18.99 | 25.44 | 20.35 | 37.28 | 8.17 | 1.53 | 3.5 | 4.4
2018-05-25 19:00 | 13407.3042 | -0.048233 | 18.81 | 26.13 | 18.81 | 32.34 | 6.3 | 0.97 | 2.11 | 3.16
2018-05-25 20:00 | 13547.9042 | -0.048233 | 20.2 | 22.51 | 20.66 | 31.65 | 6.27 | 0.97 | 2 | 4
2018-05-25 21:00 | 13451.9542 | -0.048233 | 19.18 | 21.82 | 18.11 | 30.2 | 3.34 | 0.97 | 11.01 | 3.14
2018-05-25 22:00 | 14549.4541 | -0.048233 | 18.43 | 21.31 | 17.68 | 25.17 | 5.08 | 12.34 | 20 | 4.88
2018-05-25 23:00 | 14600.0941 | -0.048233 | 15.61 | 20.02 | 17.08 | 23.73 | 3.62 | 16.18 | 16 | 17.68
2018-05-26 | 12850.6042 | -0.048233 | 14.04 | 19.18 | 14.84 | 20.41 | 3 | 0.01 | 20 | 2.87
2018-05-26 01:00 | 14023.0091 | -0.048233 | -0.48 | 16.35 | 13.52 | 17.83 | 2.61 | 0.01 | 15.43 | 2
2018-05-26 02:00 | 14031.4491 | -0.048233 | -1.03 | 14.76 | 4.16 | 17.06 | 2.59 | 0.99 | 10.07 | 1.61
2018-05-26 03:00 | 13993.4691 | -0.048233 | -1.03 | 15.84 | 3.86 | 17.24 | 2.61 | 0.99 | 3.97 | 1.89
2018-05-26 04:00 | 14807.9291 | -0.048233 | -1.1 | 16.86 | 3.88 | 17.64 | 3 | 0.99 | 3.5 | 2
2018-05-26 05:00 | 14462.7542 | -0.048233 | -0.63 | 19.34 | 8.49 | 20.84 | 3 | 1 | 30 | 3
2018-05-26 06:00 | 16251.1512 | 88.475 | 11.17 | 20.24 | 16.25 | 24 | 2.83 | 1.75 | 15.76 | 25.5
2018-05-26 07:00 | 16862.6235 | 312.13 | 17.6 | 19.7 | 17.15 | 22.14 | 2.96 | 1.65 | 3.5 | 2.76
2018-05-26 08:00 | 19405.3672 | 495.713 | 17.6 | 20.43 | 17.5 | 23.09 | 3.75 | 1.75 | 8.61 | 3.19
2018-05-26 09:00 | 19342.4882 | 459.112 | 17.61 | 20.92 | 20.01 | 25 | 3.48 | 2 | 0.93 | 3.28
2018-05-26 10:00 | 19766.3471 | 913.874 | 17.48 | 22.1 | 19.55 | 28.73 | 4.58 | 1 | 2 | 4.42
2018-05-26 11:00 | 17895.738 | 920.619 | 17.55 | 25 | 21.27 | 36.29 | 6.22 | 6 | 1 | 5.72
2018-05-26 12:00 | 18140.8675 | 1158.65 | 18.56 | 29.71 | 21.04 | 41.6 | 7.11 | 10.36 | 0.61 | 7.04
2018-05-26 13:00 | 20156.197 | 1093.4 | 18.24 | 34 | 28.11 | 50.24 | 7.88 | 12.81 | 0.61 | 10.81
2018-05-26 14:00 | 18998.5033 | 892.06 | 198.31 | 198.31 | 23.87 | 70 | 21.06 | 13.75 | 0.71 | 16.26
2018-05-26 15:00 | 17719.1744 | 743.426 | 62.85 | 62.85 | 23.63 | 94.72 | 42.97 | 24.06 | 1 | 34.1
2018-05-26 16:00 | 17039.4643 | 525.151 | 139.8 | 48.97 | 28.29 | 89.95 | 40 | 23 | 1 | 32.49
2018-05-26 17:00 | 14827.3292 | 261.715 | 138.59 | 34.16 | 23.82 | 59.18 | 20.78 | 18.58 | 1 | 20.78
2018-05-26 18:00 | 15838.8957 | 51.1713 | 36.73 | 36.73 | 22.48 | 43.75 | 6.38 | 1 | 2.31 | 3.48
2018-05-26 19:00 | 15742.6591 | -0.048233 | 16.48 | 29.99 | 20.58 | 38.52 | 5.58 | 1 | 2.11 | 4
2018-05-26 20:00 | 14064.7042 | -0.048233 | 16.08 | 29.16 | 20.25 | 35.93 | 4.5 | 1 | 2 | 3.46
2018-05-26 21:00 | 15460.9741 | -0.048233 | 16.43 | 26.71 | 18.04 | 33.55 | 4.73 | 1 | 15 | 3.06
2018-05-26 22:00 | 14821.6441 | -0.048233 | 16.34 | 26.08 | 16.46 | 30.93 | 3.82 | 0.01 | 15.93 | 3.78
2018-05-26 23:00 | 14298.3641 | -0.048233 | 14.87 | 24.43 | 15.65 | 25.55 | 3.6 | 0.01 | 16.07 | 3.6
2018-05-27 | 12763.2042 | -0.048233 | 13.32 | 22.05 | 14.76 | 22.27 | 2.87 | 0.01 | 2.11 | 2.61
2018-05-27 01:00 | 14064.1541 | -0.048233 | 10.85 | 19.01 | 13.59 | 20.98 | 2.53 | 0.01 | 3.5 | 2
2018-05-27 02:00 | 12417.4042 | -0.048233 | 8.38 | 18.69 | 8.92 | 19.36 | 2.53 | 0.99 | 3.5 | 1.51
2018-05-27 03:00 | 13725.4991 | -0.048233 | 7.96 | 18.87 | 7.09 | 18.82 | 2.53 | 0.99 | 2.61 | 1.51
2018-05-27 04:00 | 13855.2641 | -0.048233 | 11.58 | 17.89 | 8.5 | 18.99 | 2.53 | 0.99 | 2.11 | 1.6
2018-05-27 05:00 | 12656.8042 | -0.048233 | 14.16 | 19.17 | 13.62 | 20.44 | 3 | 1 | 10.42 | 2.92
2018-05-27 06:00 | 12708.1487 | 87.9986 | 14.51 | 20.48 | 14.88 | 21.88 | 2.49 | 1.5 | 36.77 | 42.75
2018-05-27 07:00 | 14409.17 | 292.981 | 15.1 | 20.53 | 16.86 | 21.44 | 3 | 2 | 0.47 | 2.15
2018-05-27 08:00 | 13111.4478 | 531.524 | 16.06 | 21.66 | 17.16 | 23.6 | 3 | 2 | 0.01 | 3.11
2018-05-27 09:00 | 14722.8046 | 653.265 | 17.67 | 21.88 | 19.2 | 25.38 | 3.58 | 2 | 0.25 | 3.28
2018-05-27 10:00 | 14762.2668 | 695.67 | 163.4 | 23.29 | 19 | 31.38 | 4 | 1 | 0.57 | 4
2018-05-27 11:00 | 15168.2308 | 1015.47 | 167.99 | 23.21 | 19.08 | 30.73 | 6 | 6 | 0.51 | 6
2018-05-27 12:00 | 13834.679 | 1116.82 | 21.42 | 26.87 | 18.96 | 37.29 | 6.74 | 8 | 1 | 6.74
2018-05-27 13:00 | 13810.0455 | 1102.89 | 163.84 | 32.14 | 18.94 | 45 | 14.82 | 13.93 | 1 | 11.93
2018-05-27 14:00 | 13698.2941 | 970.257 | 188.68 | 44.84 | 30.54 | 58.39 | 19.85 | 13.75 | 1.48 | 17.75
2018-05-27 15:00 | 13276.2728 | 625.024 | 36.64 | 36.64 | 33.5 | 76.42 | 35.54 | 24 | 2.5 | 32.2
2018-05-27 16:00 | 13063.8214 | 524.391 | 32.06 | 32.06 | 33.69 | 70.89 | 30.1 | 15.25 | 2.31 | 25.01
2018-05-27 17:00 | 12838.9052 | 248.637 | 17.33 | 30.87 | 30.1 | 48.05 | 16.46 | 13.17 | 3 | 15.37
2018-05-27 18:00 | 14026.5869 | 42.343 | 17.47 | 29.25 | 18.39 | 35.93 | 7.63 | 1.94 | 8.31 | 4
2018-05-27 19:00 | 13881.6391 | -0.048233 | 17.15 | 28.89 | 18.95 | 34.05 | 5.69 | 0.99 | 3.5 | 4
2018-05-27 20:00 | 12458.2542 | -0.048233 | 15.77 | 28.79 | 20.1 | 32.55 | 6.78 | 0.99 | 3.02 | 4.78
2018-05-27 21:00 | 12514.3042 | -0.048233 | 15.37 | 26.75 | 18.98 | 29.63 | 4.58 | 0.99 | 10 | 4.52
2018-05-27 22:00 | 12387.9542 | -0.048233 | 358.5257 | 314.2 | 16.19 | 29.12 | 3.56 | 0.01 | 10.03 | 3.56
2018-05-27 23:00 | 12218.8542 | -0.048233 | 12.94 | 22.67 | 16.74 | 25.03 | 3.11 | 0.01 | 10 | 3
2018-05-28 | 13422.7141 | -0.048233 | 12.33 | 22.73 | 12.63 | 22.74 | 3 | 0.01 | 8.11 | 2.92
2018-05-28 01:00 | 13368.9091 | -0.048233 | 11.11 | 21.94 | 9.22 | 21.43 | 2.5 | 0.01 | 3.19 | 1.51
2018-05-28 02:00 | 12026.0042 | -0.048233 | 10.43 | 22.64 | 5.38 | 20.92 | 2.3 | 1.26 | 3.05 | 1.11
2018-05-28 03:00 | 13211.7141 | -0.048233 | 0.68 | 19.97 | 2.92 | 18.36 | 2.23 | 1.23 | 3.11 | 1.4
2018-05-28 04:00 | 11887.3042 | -0.048233 | -0.23 | 18.14 | 3 | 18.3 | 2.3 | 1.17 | 2.11 | 1.11
2018-05-28 05:00 | 13226.4841 | -0.048233 | -0.16 | 5.29 | 4.3 | 18.01 | 2.53 | 1 | 20 | 2.33
2018-05-28 06:00 | 11981.6815 | 89.2963 | 9.94 | 18.01 | 8.89 | 20.44 | 2.42 | 1.43 | 18.87 | 3.84
2018-05-28 07:00 | 11967.5851 | 267.458 | 9.75 | 17.56 | 8.18 | 19.94 | 2.39 | 2.1 | 0.27 | 2.11
2018-05-28 08:00 | 13727.9944 | 584.317 | 12.48 | 19.13 | 12.78 | 21.47 | 3.5 | 2.5 | 0.53 | 3.42
2018-05-28 09:00 | 14152.768 | 823.946 | 13.04 | 20.09 | 13.76 | 23.51 | 3.61 | 2.5 | 0.13 | 3.51
2018-05-28 10:00 | 13027.483 | 1016.14 | 13.07 | 22.06 | 15.01 | 25.51 | 3.85 | 1 | 0.29 | 3.85
2018-05-28 11:00 | 12860.5879 | 589.461 | 14.46 | 21.93 | 15 | 27.01 | 4 | 1.5 | 0.25 | 4
2018-05-28 12:00 | 13433.0769 | 994.081 | 17.08 | 23.05 | 15.02 | 31.49 | 4 | 6.77 | 0 | 4
2018-05-28 13:00 | 14938.0298 | 1073.27 | 18.26 | 23.77 | 15.02 | 38.01 | 15.52 | 10 | 0.62 | 6.61
2018-05-28 14:00 | 13440.8175 | 950.229 | 148.83 | 25.49 | 15.66 | 48.23 | 22.11 | 10.75 | 1 | 17.49
2018-05-28 15:00 | 14755.1593 | 793.933 | 32.38 | 25.17 | 22.92 | 57.62 | 32.7 | 25.76 | 1 | 29.26
2018-05-28 16:00 | 13092.0355 | 543.09 | 30.12 | 24.68 | 23.03 | 58.77 | 32.26 | 22.25 | 1 | 26.78
2018-05-28 17:00 | 12833.758 | 248.219 | 22.01 | 25.54 | 17.36 | 40.52 | 15.2 | 2.25 | 1 | 4.76
2018-05-28 18:00 | 14060.8709 | 43.8397 | 20.08 | 24.41 | 17.8 | 34.62 | 8.38 | 1.5 | 12.76 | 4
2018-05-28 19:00 | 12486.7542 | -0.048233 | 18.5 | 21.21 | 17.59 | 31.01 | 4.67 | 1 | 0.25 | 4.07
2018-05-28 20:00 | 12563.7042 | -0.048233 | 18.81 | 21.99 | 19.19 | 30.22 | 4.78 | 1.3 | 0.25 | 4
2018-05-28 21:00 | 12535.2042 | -0.048233 | 18.57 | 23.75 | 18.57 | 27.67 | 3.69 | 1.22 | 2 | 3.17
2018-05-28 22:00 | 13726.5541 | -0.048233 | 16.78 | 24.29 | 12.96 | 26.81 | 3.87 | 0.01 | 10 | 4
2018-05-28 23:00 | 12203.6542 | -0.048233 | 15.48 | 21.89 | 12.67 | 24.81 | 3.98 | 0.01 | 10 | 3.38
2018-05-29 | 13527.1591 | -0.048233 | 15.33 | 20.9 | 11.06 | 22.53 | 3 | 0.01 | 9 | 3
2018-05-29 01:00 | 12125.7542 | -0.048233 | 15.46 | 20.29 | 9.42 | 21.03 | 2.39 | 0.01 | 3.5 | 2
2018-05-29 02:00 | 11841.2691 | -0.048233 | 14.79 | 19.81 | 8.97 | 20.29 | 2.3 | 1.18 | 2.66 | 1.47
2018-05-29 03:00 | 9383.1042 | -0.048233 | 12.34 | 19.31 | 6.92 | 19.55 | 2.39 | 1 | 2.11 | 1.5
2018-05-29 04:00 | 10426.5141 | -0.048233 | 8.51 | 19.23 | 8.09 | 19.18 | 2.31 | 1 | 2.11 | 1.6
2018-05-29 05:00 | 10325.2341 | -0.048233 | 9.87 | 19.83 | 8.92 | 19.79 | 2.5 | 1 | 20 | 2.5
2018-05-29 06:00 | 9460.2501 | 89.158 | 11.45 | 20.84 | 9.16 | 20.14 | 3 | 2 | 3.2 | 3.26
2018-05-29 07:00 | 11316.0112 | 300.077 | 10.69 | 19.37 | 14.03 | 20.07 | 2.61 | 2 | 0.98 | 2.15
2018-05-29 08:00 | 11583.535 | 319.654 | 10.93 | 21.01 | 14.87 | 20.53 | 2.61 | 2.43 | 0.71 | 2.61
2018-05-29 09:00 | 10187.249 | 369.42 | 12.95 | 37.12 | 15.9 | 22.25 | 3 | 2.5 | 0.35 | 2.81
2018-05-29 10:00 | 11434.9762 | 927.84 | 14.26 | 22.55 | 17.17 | 24.29 | 3 | 1.5 | 0.71 | 3
2018-05-29 11:00 | 9716.3046 | 432.689 | 14.99 | 23.08 | 17.35 | 25.11 | 3.11 | 1 | 0.4 | 3.11
2018-05-29 12:00 | 10165.0703 | 978.074 | 15.85 | 24.11 | 16.24 | 26.71 | 4.36 | 1.5 | 0.01 | 4.06
2018-05-29 13:00 | 10431.874 | 1061.92 | 17.55 | 30.52 | 16.22 | 30.88 | 7.5 | 7 | 1 | 5.58
2018-05-29 14:00 | 11437.2117 | 929.959 | 33.87 | 33.87 | 15.03 | 38.29 | 15.28 | 12.2 | 1 | 13.4
2018-05-29 15:00 | 10254.2658 | 705.964 | 88.01 | 88.01 | 15.21 | 36.4 | 22.85 | 17.82 | 2.21 | 22.22
2018-05-29 16:00 | 11403.6532 | 486.15 | 103.02 | 103.02 | 16.21 | 41.48 | 24.86 | 12.85 | 2.11 | 19.86
2018-05-29 17:00 | 10520.8871 | 190.618 | 81.96 | 77.96 | 17.09 | 30.83 | 8.36 | 1.22 | 9.11 | 4
2018-05-29 18:00 | 11890.1649 | 56.2985 | 36.37 | 36.37 | 17.17 | 26.44 | 6.52 | 0.99 | 10.89 | 4.02
2018-05-29 19:00 | 11637.6541 | -0.048233 | 17.67 | 30.88 | 17.73 | 25.66 | 4 | 1 | 1 | 3.92
2018-05-29 20:00 | 11623.9391 | -0.048233 | 17.09 | 29.82 | 20.27 | 26.57 | 3.85 | 1 | 1 | 3.85
2018-05-29 21:00 | 11591.2341 | -0.048233 | 45.49 | 45.49 | 17.11 | 25.54 | 3.68 | 1 | 10 | 3.68
2018-05-29 22:00 | 11317.9891 | -0.048233 | 14.75 | 25.83 | 14.14 | 23.49 | 4.26 | 0.01 | 20 | 4
2018-05-29 23:00 | 10063.3042 | -0.048233 | 53.99 | 53.99 | 12.78 | 21.84 | 3.88 | 0.01 | 10.53 | 3.88
2018-05-30 | 9855.2542 | -0.048233 | 10.63 | 25.49 | 14.79 | 21.09 | 3 | 0.01 | 1.46 | 3
2018-05-30 01:00 | 10868.5591 | -0.048233 | 11.61 | 21.19 | 12.79 | 20.62 | 3 | 0.01 | 2 | 2
2018-05-30 02:00 | 10678.6591 | -0.048233 | 11.14 | 21.06 | 9.74 | 19.87 | 3 | 1 | 3.02 | 1.5
2018-05-30 03:00 | 10632.2391 | -0.048233 | 3.09 | 21.19 | 8.95 | 19.73 | 3 | 0.99 | 2.61 | 1.53
2018-05-30 04:00 | 11571.1891 | -0.048233 | 14.3 | 25.23 | 10.64 | 19.85 | 3 | 1.26 | 2.11 | 1.58
2018-05-30 05:00 | 12887.8291 | -0.048233 | 45.84 | 45.84 | 14.2 | 21.5 | 3 | 0.99 | 13.57 | 3
2018-05-30 06:00 | 15076.1429 | 88.1828 | 14.94 | 21.28 | 11.12 | 25.15 | 3 | 2.25 | 3.28 | 3.5
2018-05-30 07:00 | 14936.6144 | 227.752 | 13.64 | 22.61 | 14.15 | 23.95 | 2.67 | 2.15 | 1.82 | 2.15
2018-05-30 08:00 | 17644.6935 | 257.828 | 59.26 | 59.26 | 14.79 | 24.6 | 3.19 | 2 | 3.46 | 2.5
2018-05-30 09:00 | 16771.9887 | 676.725 | 16.09 | 25.03 | 17.09 | 26.17 | 4.16 | 2 | 2 | 2.89
2018-05-30 10:00 | 16984.8685 | 943.809 | 15.98 | 29.78 | 17.03 | 27.92 | 5 | 0.97 | 1 | 3
2018-05-30 11:00 | 18746.8647 | 1104.54 | 317.7457 | 40.07 | 17.1 | 33.6 | 5.26 | 6 | 1 | 3.99
2018-05-30 12:00 | 19045.1765 | 1125.3 | 780.8811 | 55.01 | 18.03 | 36.37 | 6 | 7.5 | 1 | 4
2018-05-30 13:00 | 19146.4565 | 1064.3 | 148.67 | 148.67 | 17.24 | 40.73 | 6.93 | 10 | 1 | 4.93
2018-05-30 14:00 | 17930.8043 | 953.023 | 1717.6711 | 960.11 | 17.7 | 48.3 | 16 | 1.51 | 1 | 12.34
2018-05-30 15:00 | 16358.9176 | 384.083 | 1181.9111 | 914.3 | 17.02 | 54.45 | 20.75 | 12.96 | 2.39 | 16.34
2018-05-30 16:00 | 14221.3851 | 284.879 | 668.5111 | 400.9 | 18.32 | 50.98 | 22.41 | 1.39 | 2 | 18.76
2018-05-30 17:00 | 13889.7201 | 179.758 | 61.47 | 61.47 | 17.08 | 36.93 | 9.68 | 2.18 | 2 | 4.94
2018-05-30 18:00 | 14877.8654 | 16.2421 | 35.27 | 35.27 | 17.87 | 30.09 | 6.51 | 0.99 | 3.5 | 2.24
2018-05-30 19:00 | 14702.4291 | -0.048233 | 18.1 | 28.67 | 17.3 | 30 | 6.58 | 0.99 | 3.5 | 4.58
2018-05-30 20:00 | 14711.9241 | -0.048233 | 17.5 | 24.15 | 19.2 | 31.28 | 6.33 | 0.99 | 3.01 | 4.73
2018-05-30 21:00 | 14556.8391 | -0.048233 | 16.97 | 25.13 | 16.61 | 27.43 | 4.74 | 0.99 | 10 | 4
2018-05-30 22:00 | 14144.3341 | -0.048233 | 15.59 | 26.6 | 14.51 | 24.56 | 4.53 | 0.01 | 12.11 | 4.33
2018-05-30 23:00 | 13808.8441 | -0.048233 | 13.46 | 24.08 | 13.91 | 22.12 | 4.18 | 0.01 | 10.03 | 3.14
2018-05-31 | 12301.5042 | -0.048233 | 12.71 | 21.6 | 16.52 | 22.24 | 3 | 0.01 | 2.2 | 2.61
2018-05-31 01:00 | 12167.5542 | -0.048233 | 11.86 | 19.46 | 15.83 | 20.92 | 2.61 | 0.01 | 1.84 | 1.6
2018-05-31 02:00 | 13300.3341 | -0.048233 | 11.07 | 19.85 | 13.53 | 19.98 | 2.32 | 1 | 2.7 | 1.54
2018-05-31 03:00 | 13327.7641 | -0.048233 | 11.58 | 19.08 | 12.45 | 19.96 | 2.32 | 0.99 | 2.61 | 1.51
2018-05-31 04:00 | 12672.0042 | -0.048233 | 11.81 | 19.1 | 12.48 | 20.8 | 2.5 | 1.52 | 1.84 | 1.58
2018-05-31 05:00 | 14969.3441 | -0.048233 | 12.69 | 20.23 | 13.03 | 22.26 | 3 | 0.99 | 9.11 | 3
2018-05-31 06:00 | 15019.051 | 89.5274 | 12.93 | 22.2 | 12.52 | 24.9 | 3.57 | 2 | 2.11 | 4
2018-05-31 07:00 | 18015.4701 | 290.275 | 14.96 | 22.57 | 14.17 | 24.75 | 2.61 | 1.5 | 1 | 2.61
2018-05-31 08:00 | 18766.8485 | 531.482 | 101.35 | 101.35 | 15.51 | 24.91 | 3.75 | 2 | 2.11 | 3
2018-05-31 09:00 | 19759.747 | 721.618 | 17.75 | 22.55 | 17.72 | 26.24 | 3.75 | 1.52 | 1.31 | 3
2018-05-31 10:00 | 19961.079 | 930.454 | 18.33 | 24.49 | 17.66 | 29.51 | 3.75 | 1 | 1 | 3
2018-05-31 11:00 | 19636.9576 | 1033.23 | 19.44 | 28.12 | 17.72 | 34.85 | 5.69 | 7.5 | 1 | 3.99
2018-05-31 12:00 | 18109.622 | 1057.76 | 33.62 | 27.69 | 18.29 | 35.78 | 5.45 | 8.11 | 1 | 3.79
2018-05-31 13:00 | 18207.6715 | 1081.97 | 49.17 | 49.17 | 18.21 | 42.04 | 6 | 9.51 | 0.85 | 4.25
2018-05-31 14:00 | 18608.2672 | 976.168 | 21.14 | 29.45 | 17.68 | 50.44 | 15.21 | 6 | 1 | 11.21
2018-05-31 15:00 | 15374.9976 | 788.208 | 31.7 | 31.7 | 17.64 | 54.36 | 19.91 | 9.87 | 2 | 14.38
2018-05-31 16:00 | 14453.3 | 534 | 37.17 | 37.17 | 17.7 | 51.15 | 20.66 | 8.25 | 1.94 | 16.26
2018-05-31 17:00 | 14089.3759 | 240.922 | 17.4 | 30.23 | 18.19 | 39.79 | 11.37 | 7.79 | 1.01 | 4.14
2018-05-31 18:00 | 15357.7 | 55.0616 | 15.19 | 22.16 | 17.64 | 34.04 | 8.33 | 2.5 | 8.11 | 4.5
2018-05-31 19:00 | 13505.1542 | -0.048233 | 15.56 | 20.74 | 17.7 | 33 | 5.77 | 1.74 | 2.61 | 3.77
2018-05-31 20:00 | 14853.2941 | -0.048233 | 15.38 | 23.39 | 19.36 | 31.38 | 7.01 | 1.32 | 1.38 | 4
2018-05-31 21:00 | 14620.1391 | -0.048233 | 14.98 | 23.12 | 18 | 28.09 | 4.26 | 1.34 | 15.11 | 3.56
2018-05-31 22:00 | 12774.6042 | -0.048233 | 15.2 | 23.58 | 16.24 | 26.23 | 4.27 | 0.01 | 3.95 | 4
2018-05-31 23:00 | 12477.2542 | -0.048233 | 14.28 | 22.67 | 14.8 | 24.16 | 3.76 | 0.01 | 8.11 | 3.87
2018-06-01 | 12230.2542 | -0.048233 | 12.28 | 20.6 | 14.5 | 23.63 | 3 | 0.3 | 8.76 | 3.11
2018-06-01 01:00 | 12242.6042 | -0.048233 | 0.58 | 20.61 | 9.21 | 22.51 | 2.61 | 0.3 | 3.5 | 2
2018-06-01 02:00 | 13463.8591 | -0.048233 | 0.03 | 20.07 | 8.88 | 21.86 | 2.61 | 0.99 | 2.61 | 1
2018-06-01 03:00 | 12309.1042 | -0.048233 | 3.09 | 20.16 | 8.36 | 21.5 | 2.61 | 0.99 | 1.33 | 1
2018-06-01 04:00 | 14604.3141 | -0.048233 | 10.25 | 20.19 | 8.23 | 21.88 | 2.61 | 1 | 1 | 1
2018-06-01 05:00 | 14113.8702 | 1.7055 | 9.39 | 20.95 | 9.07 | 22.96 | 3 | 0.99 | 2.96 | 3.01
2018-06-01 06:00 | 17031.8546 | 55.938 | 5.98 | 20.94 | 16.24 | 25.55 | 3.86 | 3 | 2.05 | 3.86
2018-06-01 07:00 | 16399.1745 | 270.289 | 16.32 | 20.92 | 15.64 | 25.98 | 3.91 | 2.51 | 2.11 | 2.5
2018-06-01 08:00 | 16805.3299 | 308.821 | 17.59 | 21.11 | 15.63 | 26.21 | 3.3 | 2.85 | 3.11 | 3
2018-06-01 09:00 | 17461.8987 | 459.946 | 17.75 | 20.88 | 16.18 | 28 | 4.85 | 3.26 | 3.5 | 3.5
2018-06-01 10:00 | 19078.4333 | 431.823 | 18.8 | 21.1 | 16.82 | 31.16 | 4.21 | 6.45 | 2.11 | 4.6
2018-06-01 11:00 | 19124.502 | 719.49 | 19.5 | 21.94 | 17.09 | 34.52 | 5.98 | 6.36 | 1 | 4.91
2018-06-01 12:00 | 19124.9957 | 774.958 | 20.76 | 26.87 | 16.96 | 38.3 | 6.83 | 8.2 | 1 | 5.44
2018-06-01 13:00 | 17689.076 | 1139.08 | 29.54 | 28.21 | 19.48 | 43.58 | 9.02 | 9.18 | 1 | 5.3
2018-06-01 14:00 | 16931.7113 | 922.854 | 30.53 | 30.53 | 19.04 | 57.43 | 15.32 | 10.63 | 0.97 | 11.22
2018-06-01 15:00 | 17567.3146 | 749.483 | 94.16 | 30.64 | 20.06 | 57.21 | 22.68 | 19.27 | 1.2 | 18.45
2018-06-01 16:00 | 16755.1893 | 556.696 | 30.76 | 30.76 | 20.22 | 54.59 | 22.58 | 16.47 | 2 | 19.2
2018-06-01 17:00 | 14301.4748 | 246.184 | 37.56 | 27.29 | 18.38 | 39.33 | 14.78 | 10.62 | 2 | 2.52
2018-06-01 18:00 | 15488.5536 | 52.0935 | 21.09 | 26.51 | 16.98 | 33.45 | 7.01 | 1.49 | 10 | 4
2018-06-01 19:00 | 15352.3091 | -0.048233 | 19.09 | 25.33 | 16.62 | 31.73 | 6.99 | 0.95 | 3.01 | 4
2018-06-01 20:00 | 15317.4941 | -0.048233 | 18.54 | 21.94 | 17.95 | 32.2 | 5.6 | 0.95 | 2.89 | 3.23
2018-06-01 21:00 | 15189.8391 | -0.048233 | 18.18 | 21.75 | 15.65 | 30.38 | 4.51 | 0.95 | 17.33 | 4
2018-06-01 22:00 | 13460.5042 | -0.048233 | 17.61 | 21.7 | 15.33 | 26.91 | 3.75 | 0.3 | 11.79 | 3.75
2018-06-01 23:00 | 14506.1991 | -0.048233 | 15.73 | 21.06 | 14.13 | 23.79 | 3 | 0.3 | 12 | 3
2018-06-02 | 12666.3042 | -0.048233 | 15.55 | 20.53 | 8.21 | 21.94 | 2.93 | 0.3 | 8.29 | 2.62
2018-06-02 01:00 | 13929.1141 | -0.048233 | 15.79 | 20.55 | 8.05 | 20.77 | 2.61 | 0.3 | 8 | 2.11
2018-06-02 02:00 | 13805.6791 | -0.048233 | 14.53 | 20.14 | 4.88 | 20.3 | 2.5 | 0.97 | 12.07 | 1
2018-06-02 03:00 | 12478.2042 | -0.048233 | 14.38 | 19.34 | 4.9 | 20.23 | 2.5 | 0.97 | 1.5 | 0.95
2018-06-02 04:00 | 13149.8542 | -0.048233 | 16.41 | 20.29 | 6.28 | 20.5 | 2.5 | 1 | 1 | 1
2018-06-02 05:00 | 14122.0822 | 1.3497 | 13.92 | 21.11 | 8.3 | 22.03 | 2.95 | 1 | 3.39 | 3
2018-06-02 06:00 | 17011.53 | 58.673 | 10.19 | 21.26 | 14.2 | 23.43 | 3 | 2.95 | 1.89 | 3.6
2018-06-02 07:00 | 18144.0683 | 209.169 | 15.43 | 21.3 | 16.61 | 24.25 | 3 | 2.5 | 1 | 2.5
2018-06-02 08:00 | 18368.3381 | 412.747 | 17.1 | 22 | 17.71 | 24.46 | 3.31 | 3.02 | 1.89 | 3.38
2018-06-02 09:00 | 19034.1064 | 235.807 | 17.47 | 25.05 | 17.72 | 26.51 | 3.39 | 2.5 | 1.43 | 2.98
2018-06-02 10:00 | 17416.6882 | 457.356 | 17.92 | 26.06 | 18.65 | 28.5 | 3.56 | 3.11 | 0.71 | 3.95
2018-06-02 11:00 | 17248.693 | 555.519 | 20.52 | 33.31 | 19.45 | 33.55 | 4.65 | 6.22 | 1 | 4.59
2018-06-02 12:00 | 17647.9011 | 474.738 | 21.77 | 32.32 | 19.48 | 36.78 | 5 | 7 | 1 | 4.32
2018-06-02 13:00 | 17502.7781 | 894.977 | 35.25 | 35.25 | 18.63 | 48.18 | 7.89 | 7.68 | 1 | 4.52
2018-06-02 14:00 | 18292.5722 | 759.931 | 41.79 | 34.28 | 17.72 | 60.14 | 13.68 | 0.99 | 1 | 5.29
2018-06-02 15:00 | 15373.0463 | 482.154 | 91.88 | 77.57 | 17.73 | 62.88 | 19.87 | 16.46 | 1.3 | 17.57
2018-06-02 16:00 | 14801.1938 | 376.204 | 88.25 | 37.82 | 17.79 | 61.02 | 22.43 | 16.09 | 2.11 | 15.95
2018-06-02 17:00 | 14317.9725 | 273.55 | 97.77 | 24.41 | 17.75 | 42.16 | 19.08 | 10.97 | 3 | 3.82
2018-06-02 18:00 | 13896.46 | 50 | 51.51 | 22.94 | 17.71 | 33.63 | 6.9 | 1.27 | 20 | 3.24
2018-06-02 19:00 | 11945.9109 | 1.1383 | 79.06 | 21.82 | 17.67 | 29.3 | 5.36 | 0.97 | 8.61 | 3.44
2018-06-02 20:00 | 12183.0891 | -0.048233 | 20.7 | 21.2 | 18.01 | 28.92 | 5.1 | 0.97 | 3.46 | 3.73
2018-06-02 21:00 | 12012.1791 | -0.048233 | 19.78 | 22.16 | 17.08 | 25.65 | 3.89 | 0.97 | 17.44 | 3.11
2018-06-02 22:00 | 12203.1341 | -0.048233 | 18.88 | 21.56 | 15.21 | 26.63 | 3.11 | 0.3 | 18.39 | 3.11
2018-06-02 23:00 | 12406.9542 | -0.048233 | 119.63 | 21.43 | 12.85 | 24.08 | 3.09 | 0.3 | 17 | 3
2018-06-03 | 13165.2941 | -0.048233 | 16.32 | 20.78 | 7.13 | 22.93 | 3 | 0.3 | 13.33 | 3
2018-06-03 01:00 | 11632.7042 | -0.048233 | 11.47 | 23.76 | 4.9 | 21.19 | 2.54 | 0.3 | 15.11 | 2.11
2018-06-03 02:00 | 12693.7091 | -0.048233 | -0.64 | 21.6 | 3.88 | 20.77 | 2.75 | 0.97 | 12.74 | 1
2018-06-03 03:00 | 11450.3042 | -0.048233 | -0.96 | 20.76 | 3.73 | 20.55 | 2.54 | 0.99 | 11.49 | 0.76
2018-06-03 04:00 | 11592.8042 | -0.048233 | -1.02 | 23.45 | 3.92 | 20.34 | 2.72 | 1.24 | 19.52 | 1
2018-06-03 05:00 | 13460.7254 | 2.9814 | 4.48 | 23.56 | 7.22 | 20.53 | 3 | 1 | 10 | 2.61
2018-06-03 06:00 | 13978.5381 | 83.7991 | 13.93 | 28.65 | 15.06 | 22.52 | 3.2 | 2.2 | 2.61 | 3.2
2018-06-03 07:00 | 14477.5034 | 265.752 | 14.44 | 23.28 | 15.11 | 22.92 | 3 | 2.2 | 2.61 | 2.61
2018-06-03 08:00 | 13228.5096 | 230.747 | 15.26 | 26.29 | 15.98 | 23.33 | 3.3 | 2.59 | 3.01 | 3.5
2018-06-03 09:00 | 13563.453 | 382.319 | 47.58 | 47.58 | 16.98 | 25.51 | 3.5 | 2.61 | 2.61 | 3
2018-06-03 10:00 | 14055.4571 | 688.218 | 17.79 | 21.93 | 16.72 | 29.88 | 4.01 | 6.52 | 2.1 | 4.01
2018-06-03 11:00 | 14082.7411 | 704.938 | 18.86 | 37 | 17 | 31.13 | 4.22 | 9.13 | 0.01 | 4.22
2018-06-03 12:00 | 14017.5435 | 670.309 | 51.81 | 51.81 | 17.57 | 35.04 | 5.01 | 10 | 0 | 4.35
2018-06-03 13:00 | 15565.4278 | 1025.96 | 31.49 | 31.49 | 16.9 | 45 | 8.43 | 10 | 0 | 10.9
2018-06-03 14:00 | 14979.0261 | 961.129 | 36.78 | 36.78 | 16.38 | 57.84 | 15.51 | 11.13 | 0.77 | 13.78
2018-06-03 15:00 | 14934.8923 | 696.296 | 38.22 | 38.22 | 16.98 | 65 | 26.21 | 21.39 | 2.11 | 23.18
2018-06-03 16:00 | 13291.6162 | 548.175 | 34.51 | 34.51 | 17.27 | 59.18 | 26.95 | 20.39 | 12.74 | 22.78
2018-06-03 17:00 | 14271.4545 | 266.445 | 37.41 | 37.41 | 16.78 | 40.3 | 18.01 | 14.6 | 3.5 | 16.02
2018-06-03 18:00 | 12537.2472 | 86.1023 | 19.33 | 25.93 | 15.99 | 32.9 | 7.16 | 1.39 | 20 | 4.51
2018-06-03 19:00 | 12504.9766 | 1.1333 | 18.08 | 22.35 | 16.01 | 31.16 | 5.96 | 0.97 | 2.09 | 3.44
2018-06-03 20:00 | 12404.1042 | -0.048233 | 18.16 | 21.76 | 17.68 | 27.77 | 4.76 | 0.97 | 0.25 | 3.76
2018-06-03 21:00 | 12252.1042 | -0.048233 | 19.92 | 21.94 | 16.04 | 27.58 | 3.37 | 0.95 | 16.59 | 3.37
2018-06-03 22:00 | 11902.5042 | -0.048233 | 18.6 | 30.51 | 13.53 | 26.38 | 3 | 0.3 | 18.42 | 3
2018-06-03 23:00 | 13067.1791 | -0.048233 | 18.26 | 21.94 | 11.71 | 23.71 | 3 | 0.3 | 10 | 3
2018-06-04 | 12990.1641 | -0.048233 | 16.49 | 22.79 | 11.47 | 23.62 | 2.81 | 0.3 | 36.55 | 2.61
2018-06-04 01:00 | 12801.3191 | -0.048233 | 16.02 | 21.86 | 8.81 | 22.03 | 2.51 | 0.3 | 19.24 | 2.01
2018-06-04 02:00 | 11596.6042 | -0.048233 | 5.71 | 21.28 | 6.6 | 21.31 | 2.2 | 0.99 | 12.34 | 1
2018-06-04 03:00 | 11453.1542 | -0.048233 | 1.7 | 19.85 | 6.88 | 20.99 | 2.11 | 0.99 | 12.15 | 0.5
2018-06-04 04:00 | 11244.1542 | -0.048233 | 7.57 | 19.6 | 9.46 | 20.49 | 2.51 | 1 | 20.22 | 1
2018-06-04 05:00 | 11198.918 | 2.3347 | 14.55 | 19.44 | 10.03 | 20.65 | 2.61 | 1 | 14.86 | 2.01
2018-06-04 06:00 | 11228.3436 | 71.3091 | 15.06 | 18.73 | 12.73 | 21.3 | 2.99 | 2 | 3.04 | 3.4
2018-06-04 07:00 | 12647.4487 | 275.103 | 14.46 | 17.95 | 11.96 | 21.76 | 2.71 | 2.5 | 14.11 | 2.25
2018-06-04 08:00 | 13099.5151 | 554.602 | 14.88 | 18.88 | 15.29 | 22.06 | 3 | 2.74 | 34.32 | 3.66
2018-06-04 09:00 | 12120.4059 | 781.322 | 15.54 | 19.92 | 16.95 | 24.99 | 3.5 | 3.22 | 16.57 | 3.5
2018-06-04 10:00 | 12468.503 | 965.74 | 15.6 | 20.44 | 16.4 | 26.84 | 4.76 | 4.74 | 14.61 | 4.76
2018-06-04 11:00 | 14121.9346 | 1074.72 | 16.25 | 23.68 | 16.66 | 31.81 | 5.46 | 6.48 | 1 | 4.59
2018-06-04 12:00 | 12936.207 | 1124.06 | 16.96 | 30.79 | 17.86 | 34.83 | 6.05 | 5.29 | 1 | 5.01
2018-06-04 13:00 | 14384.9777 | 1011.05 | 33.15 | 33.15 | 17.97 | 40.18 | 7.18 | 6.89 | 1 | 3.7
2018-06-04 14:00 | 14511.9597 | 933.412 | 34.17 | 34.17 | 17.9 | 49.81 | 15.69 | 12.49 | 1.21 | 4.34
2018-06-04 15:00 | 14575.6985 | 759.828 | 18.2 | 29.52 | 17.66 | 55 | 23.22 | 18.05 | 2.11 | 21.65
2018-06-04 16:00 | 14209.7496 | 509.957 | 41.76 | 28.23 | 17.8 | 54.04 | 26.37 | 16.26 | 12.79 | 23.49
2018-06-04 17:00 | 13992.5378 | 211.069 | 38.66 | 24.57 | 17.77 | 40.44 | 20.51 | 17.1 | 7.59 | 19.05
2018-06-04 18:00 | 13483.7576 | 60.8129 | 17.91 | 20.97 | 17.9 | 32.73 | 6.93 | 9.61 | 32 | 3
2018-06-04 19:00 | 12745.601 | 1.1384 | 17.87 | 20.14 | 16.77 | 29.13 | 5.75 | 1.3 | 10 | 2.94
2018-06-04 20:00 | 11487.3542 | -0.048233 | 18.02 | 20.86 | 18.34 | 30.54 | 5.77 | 1.25 | 2.6 | 3.03
2018-06-04 21:00 | 11618.4542 | -0.048233 | 18.37 | 20.93 | 16.66 | 27.92 | 4 | 1.19 | 12.02 | 3
2018-06-04 22:00 | 12805.5391 | -0.048233 | 17.82 | 21.03 | 14.49 | 26.57 | 3.18 | 0.3 | 18.17 | 3.18
2018-06-04 23:00 | 12521.7441 | -0.048233 | 17.27 | 26.8 | 13 | 24.15 | 2.83 | 0.3 | 15.11 | 2.72
2018-06-05 | 12513.3041 | -0.048233 | 16.07 | 22.86 | 10.34 | 22.24 | 2.79 | 0.3 | 7.19 | 2.76
2018-06-05 01:00 | 12478.4891 | -0.048233 | 15.4 | 19.75 | 8.68 | 21 | 2.61 | 0.3 | 3.5 | 2.53
2018-06-05 02:00 | 11315.4042 | -0.048233 | 14.88 | 18.98 | 5.93 | 20.36 | 3 | 0.99 | 9.11 | 1.61
2018-06-05 03:00 | 11253.6542 | -0.048233 | 14.29 | 18.51 | 5.92 | 20.04 | 2.79 | 0.99 | 1.03 | 1
2018-06-05 04:00 | 12921.5891 | -0.048233 | 13.77 | 18.42 | 6.13 | 20.28 | 3 | 0.99 | 12.62 | 1
2018-06-05 05:00 | 13711.1802 | 2.3794 | 13.55 | 18.8 | 9.55 | 21.18 | 3 | 1 | 135.7434 | 2.25
2018-06-05 06:00 | 13890.7338 | 51.8251 | 13.72 | 19.2 | 9.66 | 24.19 | 3.2 | 1.78 | 12.7 | 3
2018-06-05 07:00 | 16791.3389 | 177.961 | 13.83 | 19.37 | 4.12 | 24.82 | 3 | 1.25 | 2.61 | 2.25
2018-06-05 08:00 | 18422.5883 | 597.169 | 15.1 | 20.13 | 11.11 | 24.13 | 3.25 | 1.79 | 10 | 3
2018-06-05 09:00 | 18985.3517 | 706.594 | 16.64 | 20.49 | 15.07 | 25.27 | 3.05 | 1.36 | 10.65 | 3
2018-06-05 10:00 | 17799.332 | 977.139 | 17.93 | 20.97 | 15.91 | 27.52 | 3.72 | 2.75 | 2.61 | 3.72
2018-06-05 11:00 | 17484.3985 | 1107.63 | 19.06 | 21.7 | 16.53 | 32.42 | 5.38 | 3.58 | 1 | 4.68
2018-06-05 12:00 | 18573.982 | 1103.56 | 17.15 | 26.2 | 17.31 | 40.13 | 4.99 | 5.57 | 1.61 | 3.99
2018-06-05 13:00 | 21218.5187 | 1109.34 | 70.08 | 70.08 | 17.68 | 51.56 | 5 | 7.35 | 1.07 | 4.8
2018-06-05 14:00 | 19108.8067 | 817.613 | 279.5957 | 235.27 | 17 | 60 | 6.72 | 18.29 | 1.78 | 14.99
2018-06-05 15:00 | 15868.5777 | 796.766 | 320.5057 | 276.18 | 16.85 | 74.08 | 23.09 | 19.68 | 2.42 | 21.23
2018-06-05 16:00 | 14221.7479 | 569.261 | 294.3957 | 250.07 | 16.55 | 69.71 | 29.34 | 26.34 | 2.11 | 25.21
2018-06-05 17:00 | 14003.7571 | 238.797 | 111.08 | 111.08 | 17.02 | 47.5 | 18.21 | 16.84 | 2.11 | 18.21
2018-06-05 18:00 | 15086.0633 | 77.5861 | 20.61 | 24.66 | 16.27 | 33.54 | 5.84 | 11.33 | 10 | 3.6
2018-06-05 19:00 | 15111.9757 | 1.1476 | 19.87 | 22.77 | 16.23 | 29.85 | 6.23 | 1.14 | 3.5 | 3.01
2018-06-05 20:00 | 15225.7091 | -0.048233 | 18.23 | 22.14 | 16.17 | 30.43 | 5.06 | 1.25 | 3.46 | 4
2018-06-05 21:00 | 13029.2042 | -0.048233 | 17.92 | 23.73 | 17.2 | 26.72 | 4.77 | 0.99 | 10.53 | 4
2018-06-05 22:00 | 12637.8042 | -0.048233 | 17.2 | 22.55 | 15.19 | 25.76 | 3 | 0.3 | 10 | 3
2018-06-05 23:00 | 12286.3042 | -0.048233 | 15.09 | 21.47 | 13.24 | 24.38 | 2.84 | 0.3 | 7.87 | 2.84
2018-06-06 | 13349.9191 | -0.048233 | 13.99 | 20.65 | 14.97 | 21.85 | 3 | 0.25 | 13.39 | 2.61
2018-06-06 01:00 | 11981.3542 | -0.048233 | 12.85 | 19.77 | 11.57 | 21.1 | 2.5 | 0.3 | 3.46 | 2.04
2018-06-06 02:00 | 13144.1941 | -0.048233 | 7.13 | 19.1 | 8.48 | 20.22 | 2.25 | 0.99 | 3.01 | 1.61
2018-06-06 03:00 | 11743.8542 | -0.048233 | 12.43 | 18.89 | 5.53 | 19.81 | 2.11 | 0.99 | 1.38 | 1
2018-06-06 04:00 | 12431.6542 | -0.048233 | 12.46 | 18.75 | 5.53 | 19.95 | 2.11 | 0.99 | 1 | 1
2018-06-06 05:00 | 13330.7181 | 2.3348 | 13.48 | 19.19 | 5.43 | 21.04 | 2.76 | 1.18 | 135.7434 | 2.46
2018-06-06 06:00 | 14800.0333 | 54.9824 | 14.88 | 20.5 | 8.54 | 20.78 | 2.94 | 2 | 14.11 | 50
2018-06-06 07:00 | 17866.6782 | 212.24 | 15.26 | 20.42 | 12.25 | 21.02 | 3 | 2 | 2.61 | 2.5
2018-06-06 08:00 | 16622.5129 | 274.382 | 16.31 | 21.32 | 12.53 | 21.87 | 2.94 | 2 | 3.5 | 2.61
2018-06-06 09:00 | 17254.7009 | 608.843 | 18.17 | 22.08 | 15.78 | 24.51 | 2.5 | 3.07 | 2.11 | 2.5
2018-06-06 10:00 | 17555.5535 | 1008.53 | 18.68 | 27.6 | 15.29 | 26.48 | 3.59 | 3.5 | 2.5 | 4.24
2018-06-06 11:00 | 17742.713 | 1043.54 | 51.15 | 51.15 | 16.18 | 30 | 5.2 | 5.41 | 1 | 5.17
2018-06-06 12:00 | 18291.262 | 1148.96 | 31.98 | 31.98 | 16.17 | 34.49 | 5.61 | 5.87 | 1 | 5.61
2018-06-06 13:00 | 17883.8735 | 1086.13 | 35.02 | 35.02 | 16.15 | 42.81 | 7.11 | 8.5 | 1 | 11.37
2018-06-06 14:00 | 17414.1146 | 976.647 | 37.84 | 37.84 | 16.17 | 55.7 | 17.57 | 15.59 | 1.71 | 15.57
2018-06-06 15:00 | 16320.6694 | 803.652 | 33.1 | 33.1 | 16.2 | 68.47 | 23.79 | 16.86 | 2 | 20.54
2018-06-06 16:00 | 17032.3663 | 568.423 | 48.48 | 46.72 | 16.16 | 74.07 | 35.05 | 25.98 | 2.14 | 30.58
2018-06-06 17:00 | 16352.2837 | 238.795 | 54.51 | 34.32 | 16.17 | 52.51 | 22.24 | 15.25 | 2 | 19.07
2018-06-06 18:00 | 14263.5192 | 54.2307 | 34.16 | 34.16 | 13.27 | 38.07 | 13.93 | 10.8 | 7.91 | 3.88
2018-06-06 19:00 | 15891.6207 | 1.1476 | 121.07 | 32.74 | 13.94 | 33.15 | 5.58 | 1.27 | 2.11 | 2.69
2018-06-06 20:00 | 15890.3591 | -0.048233 | 32.45 | 32.45 | 16.22 | 30.54 | 6 | 1.62 | 2.83 | 3.05
2018-06-06 21:00 | 15618.1691 | -0.048233 | 32.47 | 32.47 | 16.15 | 27.83 | 3.89 | 1.25 | 2.11 | 3.42
2018-06-06 22:00 | 14998.8841 | -0.048233 | 22.24 | 25.32 | 12.3 | 27.39 | 3.01 | 0.3 | 9 | 3.01
2018-06-06 23:00 | 13089.0542 | -0.048233 | 17.48 | 23.98 | 8.36 | 24.75 | 3.01 | 0.3 | 8.11 | 2.9
2018-06-07 | 12790.7542 | -0.048233 | 15.99 | 20.9 | 8.46 | 22.01 | 3 | 0.3 | 12.08 | 2.54
2018-06-07 01:00 | 14129.5641 | -0.048233 | 15.43 | 20.3 | 6.32 | 20.73 | 2.61 | 0.3 | 3.44 | 2.01
2018-06-07 02:00 | 12450.6542 | -0.048233 | 14.27 | 19.7 | 5.13 | 20.01 | 2.5 | 0.99 | 2.99 | 1
2018-06-07 03:00 | 11837.9042 | -0.048233 | 13.85 | 18.92 | 4.75 | 19.59 | 2.47 | 0.99 | 2.11 | 0.5
2018-06-07 04:00 | 13703.3441 | -0.048233 | 14.22 | 18.48 | 4.81 | 19.56 | 2.25 | 0.99 | 1.39 | 1
2018-06-07 05:00 | 14906.4581 | 2.3442 | 14.99 | 18.64 | 4.78 | 20.4 | 2.61 | 0.99 | 2.99 | 2.11
2018-06-07 06:00 | 15746.5937 | 62.3618 | 3.66 | 20.79 | 4.89 | 22.48 | 3.11 | 2.25 | 2.11 | 3.15
2018-06-07 07:00 | 16882.8623 | 246.434 | 14.72 | 20.44 | 6.36 | 22.3 | 2.29 | 2 | 2.11 | 2.29
2018-06-07 08:00 | 17183.808 | 225.219 | 16.06 | 23.49 | 9.41 | 24.67 | 2.29 | 2 | 3.01 | 2.29
2018-06-07 09:00 | 20095.6031 | 613.965 | 17.82 | 25.65 | 12.51 | 27.99 | 2.29 | 2.05 | 2 | 2.29
2018-06-07 10:00 | 17843.1945 | 495.31 | 19.36 | 28.76 | 12.81 | 32.47 | 4.11 | 2.65 | 2.5 | 4.07
2018-06-07 11:00 | 20099.0192 | 878.203 | 32.45 | 30.32 | 14.06 | 38.77 | 4.9 | 5 | 1 | 4.4
2018-06-07 12:00 | 19208.1773 | 878.134 | 30.94 | 30.94 | 14.31 | 42.09 | 7.14 | 6.18 | 1 | 6.7
2018-06-07 13:00 | 19608.76 | 891.8 | 40.91 | 40.91 | 13.76 | 60 | 12.83 | 11.83 | 1 | 11.83
2018-06-07 14:00 | 19469.7391 | 431.729 | 32.89 | 32.89 | 14.3 | 70.95 | 15.18 | 13.66 | 1 | 13.08
2018-06-07 15:00 | 16520.995 | 760.521 | 36.53 | 36.53 | 12.92 | 92.49 | 28.11 | 19.67 | 1 | 23.55
2018-06-07 16:00 | 15522.468 | 489.44 | 49.44 | 49.44 | 14.72 | 98.75 | 38.73 | 24.87 | 1 | 30.66
2018-06-07 17:00 | 14853.1417 | 245.886 | 72.68 | 72.68 | 14.84 | 58.72 | 22 | 16.46 | 1 | 21
2018-06-07 18:00 | 14499.4158 | 57.543 | 37.4 | 37.4 | 14.03 | 39.39 | 14.21 | 11.98 | 2.21 | 3.34
2018-06-07 19:00 | 15813.5409 | 1.1383 | 31.98 | 31.98 | 15.32 | 33.43 | 5.85 | 1.45 | 2.61 | 2.96
2018-06-07 20:00 | 14190.1042 | -0.048233 | 30.62 | 30.62 | 16.29 | 31.04 | 5.73 | 1.49 | 1 | 2.4
2018-06-07 21:00 | 15631.8841 | -0.048233 | 31.93 | 31.93 | 16.21 | 27.12 | 3.6 | 0.99 | 2.11 | 2.61
2018-06-07 22:00 | 15229.9291 | -0.048233 | 21 | 23.49 | 12.52 | 26.94 | 3.29 | 0.3 | 8.11 | 3.29
2018-06-07 23:00 | 13317.0542 | -0.048233 | 42.46 | 42.46 | 8.66 | 23.86 | 3 | 0.3 | 7.46 | 3
2018-06-08 | 12968.4042 | -0.048233 | 15.15 | 21.97 | 14.76 | 22.16 | 3 | 0.3 | 12.53 | 2.25
2018-06-08 01:00 | 13052.0042 | -0.048233 | 14.53 | 20.23 | 9.65 | 21.15 | 2.5 | 0.3 | 8 | 1.8
2018-06-08 02:00 | 12881.0042 | -0.048233 | 12.9 | 19.5 | 8.43 | 20.69 | 2.25 | 0.97 | 9.62 | 0.76
2018-06-08 03:00 | 14010.3491 | -0.048233 | 6.08 | 19.23 | 8.42 | 19.91 | 2.5 | 0.97 | 3.5 | 0.5
2018-06-08 04:00 | 13357.9042 | -0.048233 | 1.1 | 19.22 | 5.58 | 20.07 | 2.5 | 0.97 | 10 | 0.69
2018-06-08 05:00 | 15777.9708 | 2.4226 | 12.65 | 19.57 | 9.62 | 21.01 | 2.61 | 0.99 | 4.16 | 2.01
2018-06-08 06:00 | 15825.1444 | 63.0467 | 14.58 | 20.53 | 14.85 | 24.64 | 3 | 2.1 | 2.7 | 2.8
2018-06-08 07:00 | 16951.8266 | 300.028 | 15.05 | 20.07 | 15.23 | 24.58 | 2.59 | 2.1 | 2.2 | 2.11
2018-06-08 08:00 | 19859.5521 | 554.22 | 46.09 | 46.09 | 16.21 | 27.04 | 2.67 | 2.45 | 2.66 | 2.67
2018-06-08 09:00 | 18387.3127 | 750.066 | 17.98 | 21.45 | 16.25 | 28.64 | 3.24 | 2.5 | 2.2 | 3.24
2018-06-08 10:00 | 18344.272 | 1011.76 | 21.09 | 23.29 | 16.79 | 32.37 | 5.29 | 6 | 2.11 | 5.25
2018-06-08 11:00 | 18291.3665 | 1077.07 | 120.5 | 27.94 | 17.34 | 37.26 | 6.15 | 5.25 | 1 | 5.3
2018-06-08 12:00 | 19357.352 | 1101.16 | 35.1 | 35.1 | 16.88 | 39.74 | 6.33 | 6.53 | 0.87 | 5.33
2018-06-08 13:00 | 20792.0138 | 1052.07 | 31.44 | 31.44 | 17.81 | 55.72 | 11.51 | 9.5 | 1 | 10.4
2018-06-08 14:00 | 18046.6892 | 922.515 | 39.2 | 39.2 | 17.71 | 74.57 | 15.43 | 14.14 | 1.37 | 13.89
2018-06-08 15:00 | 16449.8361 | 706.617 | 48.76 | 48.76 | 17.91 | 88.28 | 27.25 | 19.37 | 2.11 | 20.9
2018-06-08 16:00 | 15527.8003 | 581.053 | 181.27 | 181.27 | 17.88 | 93.69 | 36.23 | 24.9 | 2.21 | 25.98
2018-06-08 17:00 | 16315.9326 | 244.339 | 66.65 | 66.65 | 17.12 | 50.44 | 20.99 | 18.94 | 2 | 20.14
2018-06-08 18:00 | 14154.6266 | 58.6069 | 37.36 | 37.36 | 16.99 | 36.64 | 7 | 0.99 | 3.5 | 3
2018-06-08 19:00 | 15594.1106 | 1.1475 | 33.93 | 30.22 | 16.18 | 32.39 | 5.47 | 0.97 | 2.61 | 3
2018-06-08 20:00 | 15671.9741 | -0.048233 | 33.47 | 33.47 | 17.44 | 33.02 | 4.25 | 0.95 | 1 | 3
2018-06-08 21:00 | 14078.9542 | -0.048233 | 17.85 | 26.43 | 16.34 | 28.49 | 4 | 0.95 | 8.11 | 2.99
2018-06-08 22:00 | 14918.7041 | -0.048233 | 17.72 | 22.72 | 14.9 | 25.37 | 3.2 | 0.3 | 12 | 3
2018-06-08 23:00 | 14504.0891 | -0.048233 | 16.83 | 22 | 12.18 | 27.11 | 2.75 | 0.3 | 8.61 | 2.55
2018-06-09 | 14395.4241 | -0.048233 | 16.06 | 19.57 | 9.19 | 20.56 | 2.25 | 0.3 | 15.86 | 3
2018-06-09 01:00 | 14169.6541 | -0.048233 | 15.42 | 18.66 | 6.96 | 19.04 | 2.25 | 0.25 | 10.85 | 2.25
2018-06-09 02:00 | 13985.0291 | -0.048233 | 14.22 | 18.18 | 5.02 | 18.33 | 2.25 | 0.99 | 12.77 | 2
2018-06-09 03:00 | 13897.4641 | -0.048233 | 13.29 | 17.61 | 4.61 | 18.01 | 2.25 | 0.99 | 0.71 | 1.89
2018-06-09 04:00 | 13015.9042 | -0.048233 | 13.32 | 18.98 | 5.01 | 18.33 | 2.25 | 0.99 | 11.28 | 1.98
2018-06-09 05:00 | 15520.0021 | 1.9025 | 13.99 | 20.6 | 7.28 | 19.98 | 2.51 | 0.99 | 6.68 | 2.25
2018-06-09 06:00 | 15797.8896 | 63.3575 | 15.23 | 20.19 | 14.89 | 22.61 | 3 | 2 | 3.98 | 3
2018-06-09 07:00 | 16735.769 | 252.599 | 15.5 | 20.27 | 16.36 | 23.05 | 3 | 2 | 3.31 | 2.25
2018-06-09 08:00 | 19463.7404 | 606.043 | 16.74 | 20.81 | 15.02 | 26.3 | 2.61 | 2.35 | 10.31 | 3.5
2018-06-09 09:00 | 20533.2762 | 825.821 | 15.58 | 20.78 | 16.58 | 28.36 | 2.92 | 2 | 3.46 | 2.61
2018-06-09 10:00 | 19751.0664 | 886.39 | 58.31 | 58.31 | 15.55 | 29.59 | 3.98 | 3 | 2.11 | 4.25
2018-06-09 11:00 | 19826.098 | 1099.51 | 135.58 | 135.58 | 16.48 | 35.2 | 4.26 | 2.94 | 1 | 3.84
2018-06-09 12:00 | 20546.5364 | 1048.39 | 28.83 | 24.72 | 16.85 | 36.98 | 4.72 | 8.5 | 0.71 | 4.32
2018-06-09 13:00 | 19982.4596 | 1072.72 | 29 | 24.12 | 16.93 | 45.63 | 8.36 | 9.48 | 0.61 | 12.19
2018-06-09 14:00 | 17052.1893 | 976.673 | 31.51 | 25.05 | 16.95 | 67.55 | 20.78 | 17.35 | 1.04 | 18.85
2018-06-09 15:00 | 17765.6598 | 831.488 | 27.65 | 25.73 | 17.18 | 84.35 | 39.15 | 57.2673 | 1.09 | 36.96
2018-06-09 16:00 | 16354.6955 | 580.081 | 24.75 | 24.81 | 17.52 | 66.57 | 38.66 | 54.4673 | 2 | 34.66
2018-06-09 17:00 | 13986.3626 | 268.487 | 24.06 | 25.04 | 17.21 | 41.29 | 22.94 | 18.94 | 1 | 21.34
2018-06-09 18:00 | 13487.9914 | 55.8857 | 21.73 | 21.73 | 16.46 | 31.54 | 7.12 | 11.17 | 2.31 | 3
2018-06-09 19:00 | 13370.079 | 1.7674 | 65.08 | 65.08 | 16.06 | 33.35 | 4.82 | 10.86 | 2.11 | 3
2018-06-09 20:00 | 13198.3042 | -0.048233 | 19.63 | 21.26 | 16.04 | 32.73 | 4.07 | 0.99 | 2.11 | 2.25
2018-06-09 21:00 | 14437.6241 | -0.048233 | 21 | 21 | 15.67 | 29.42 | 2.61 | 0.99 | 20 | 2.41
2018-06-09 22:00 | 12584.6042 | -0.048233 | 112.78 | 21.77 | 15.03 | 26.16 | 2.61 | 0.3 | 20 | 4.34
2018-06-09 23:00 | 13505.0041 | -0.048233 | 17.7 | 22.67 | 11.34 | 23.2 | 3 | 0.3 | 12.26 | 3
2018-06-10 | 11969.9542 | -0.048233 | 16.66 | 22.39 | 7.2 | 20.35 | 2.61 | 0.3 | 20 | 2.2
2018-06-10 01:00 | 13230.7041 | -0.048233 | 15.93 | 20.77 | 4.81 | 18.01 | 2.5 | 0.25 | 2.47 | 2.01
2018-06-10 02:00 | 13107.2691 | -0.048233 | 15.04 | 19.56 | 4.4 | 16.75 | 2.61 | 0.97 | 2.56 | 1
2018-06-10 03:00 | 11610.8542 | -0.048233 | 13.72 | 18.84 | 4.39 | 16.05 | 2.61 | 0.97 | 2.74 | 0.94
2018-06-10 04:00 | 11690.6542 | -0.048233 | 13.33 | 18.02 | 4.37 | 15.65 | 2.61 | 0.97 | 3.48 | 1
2018-06-10 05:00 | 12278.1349 | 2.3525 | 13.73 | 17.15 | 6.11 | 16.35 | 2.89 | 0.97 | 10.68 | 2.01
2018-06-10 06:00 | 14228.5566 | 53.7835 | 14.59 | 17.51 | 14.79 | 18.71 | 3 | 1.64 | 2.86 | 3
2018-06-10 07:00 | 14775.4818 | 263.196 | 15.22 | 17 | 13.32 | 19.52 | 3 | 2 | 2 | 2.11
2018-06-10 08:00 | 15106.9533 | 422.387 | 16.77 | 18.82 | 15.17 | 21.5 | 3.25 | 1.94 | 2.3 | 3.25
2018-06-10 09:00 | 15964.855 | 418.564 | 17.49 | 17.78 | 14.34 | 27.58 | 3.25 | 2 | 2.3 | 3
2018-06-10 10:00 | 14755.1416 | 663.728 | 17.91 | 19.16 | 15.78 | 26.73 | 4.66 | 3.21 | 1 | 4.97
2018-06-10 11:00 | 16032.4837 | 622.667 | 20.58 | 20.58 | 16 | 33.04 | 5.45 | 2.74 | 1 | 4.97
2018-06-10 12:00 | 16390.3618 | 743.888 | 21.89 | 21.89 | 15.67 | 45.54 | 7.21 | 7.46 | 1 | 6.65
2018-06-10 13:00 | 15864.0783 | 753.041 | 31.21 | 22.75 | 16.48 | 60.88 | 6.98 | 9.25 | 0.74 | 10.75
2018-06-10 14:00 | 14147.7572 | 957.376 | 34.7 | 24.79 | 15.67 | 59.56 | 17.28 | 15.53 | 1.31 | 16.73
2018-06-10 15:00 | 13663.9022 | 684.055 | 40.28 | 24.6 | 15.95 | 75.55 | 36.08 | 58.3173 | 1.44 | 35.01
2018-06-10 16:00 | 15039.3067 | 545.267 | 28.42 | 25.68 | 16.32 | 67.2 | 35.42 | 55.3173 | 2 | 29.93
2018-06-10 17:00 | 14757.5542 | 257.203 | 28.5 | 27.17 | 15.78 | 35.16 | 18.7 | 17.27 | 2 | 18.07
2018-06-10 18:00 | 13100.1053 | 50.5845 | 22.67 | 23.36 | 15.65 | 29.67 | 7.11 | 10.85 | 3.5 | 3
2018-06-10 19:00 | 13099.335 | 1.7737 | 22.03 | 23.07 | 15.64 | 27.21 | 7.31 | 0.95 | 3.5 | 3.01
2018-06-10 20:00 | 14508.3091 | -0.048233 | 21.32 | 22.01 | 15.95 | 26.22 | 5.96 | 0.95 | 2.1 | 3
2018-06-10 21:00 | 14457.6691 | -0.048233 | 22.07 | 22.26 | 15.08 | 25.55 | 4.69 | 0.95 | 20 | 4.16
2018-06-10 22:00 | 12850.6042 | -0.048233 | 18.02 | 24.18 | 13.95 | 23.13 | 3 | 0.3 | 15.13 | 3
2018-06-10 23:00 | 13908.0141 | -0.048233 | 17.05 | 20.97 | 12.62 | 21.08 | 3 | 0.3 | 11.01 | 2.8
2018-06-11 | 13724.4441 | -0.048233 | 15.13 | 20.54 | 12.08 | 20.16 | 2.94 | 0.25 | 20 | 3.11
2018-06-11 01:00 | 12136.2042 | -0.048233 | 15.34 | 18.44 | 9.66 | 18.66 | 2.31 | 0.25 | 8.43 | 2.11
2018-06-11 02:00 | 11963.3042 | -0.048233 | 15.38 | 17.57 | 5.94 | 17.68 | 2.11 | 0.97 | 6.46 | 1
2018-06-11 03:00 | 11796.1042 | -0.048233 | 14.39 | 17.12 | 5.07 | 17.08 | 2.5 | 0.97 | 6.38 | 0.83
2018-06-11 04:00 | 12949.0191 | -0.048233 | 14.21 | 17.88 | 5.07 | 16.61 | 2.25 | 0.97 | 10.03 | 1
2018-06-11 05:00 | 12909.4053 | 2.4032 | 14.54 | 17.63 | 5.88 | 16.95 | 3 | 0.97 | 135.7434 | 2.61
2018-06-11 06:00 | 11498.8003 | 64.0003 | 15.02 | 15.89 | 9.07 | 19.24 | 2.94 | 1.81 | 18.5 | 3
2018-06-11 07:00 | 11574.0381 | 268.198 | 15.19 | 15.88 | 10 | 19.46 | 3 | 2 | 3.5 | 2.61
2018-06-11 08:00 | 13327.3202 | 499.531 | 17.14 | 19.26 | 15.43 | 20.8 | 3 | 2.45 | 15 | 3.5
2018-06-11 09:00 | 12431.5622 | 822.855 | 15.44 | 18.81 | 14.62 | 22.98 | 3 | 2.5 | 13.6 | 3.8
2018-06-11 10:00 | 13620.1386 | 463.084 | 16.47 | 20.62 | 13.82 | 26.06 | 4.75 | 4.43 | 10.96 | 6.21
2018-06-11 11:00 | 14504.0028 | 1150.87 | 20.88 | 21.66 | 15.37 | 28.35 | 5 | 4.8 | 1.81 | 5
2018-06-11 12:00 | 13150.071 | 1080.18 | 20.69 | 22.79 | 16.62 | 32.79 | 7.31 | 6.1 | 1 | 5.96
2018-06-11 13:00 | 14718.2206 | 1112.92 | 20.87 | 25.53 | 16.06 | 38.5 | 8.24 | 9.08 | 1 | 10.29
2018-06-11 14:00 | 13037.7287 | 970.925 | 46.69 | 27.08 | 16.51 | 47.37 | 18.59 | 16.93 | 1 | 18.42
2018-06-11 15:00 | 14463.5763 | 851.551 | 270.1157 | 35.91 | 16.3 | 54.74 | 26.83 | 23.42 | 1.49 | 26.41
2018-06-11 16:00 | 14185.3823 | 560.86 | 34 | 29.35 | 23.95 | 47.64 | 28.39 | 28.42 | 2.11 | 28.42
2018-06-11 17:00 | 13942.3029 | 276.453 | 31.45 | 31.45 | 22.61 | 35.97 | 18.52 | 16.12 | 2.1 | 18.52
2018-06-11 18:00 | 12447.3405 | 48.4637 | 20.75 | 27.21 | 15.83 | 32.1 | 8.74 | 0.97 | 25 | 3.52
2018-06-11 19:00 | 12394.435 | 1.7737 | 19.89 | 25.52 | 15.27 | 29.33 | 7.11 | 0.97 | 3.5 | 4
2018-06-11 20:00 | 13613.6691 | -0.048233 | 22.37 | 22.37 | 17.34 | 29.6 | 5 | 0.97 | 2.54 | 4
2018-06-11 21:00 | 12375.6042 | -0.048233 | 18.68 | 24.39 | 14.26 | 25.44 | 4.54 | 0.91 | 15 | 3.51
2018-06-11 22:00 | 12211.2542 | -0.048233 | 31.28 | 24.13 | 14.85 | 24.56 | 3.16 | 0.25 | 14.61 | 3.19
2018-06-11 23:00 | 12212.2042 | -0.048233 | 17.23 | 22.29 | 15.99 | 22.33 | 2.84 | 0.25 | 14.61 | 3
2018-06-12 | 13472.2991 | -0.048233 | 16.71 | 20.19 | 16.71 | 20.62 | 2.14 | 0.16 | 20 | 2.14
2018-06-12 01:00 | 11963.3042 | -0.048233 | 16.63 | 19.6 | 16.32 | 19.6 | 2 | 0.12 | 7.35 | 2
2018-06-12 02:00 | 13156.8541 | -0.048233 | 15.87 | 19.13 | 14.66 | 18.97 | 2.01 | 0.97 | 4.88 | 1
2018-06-12 03:00 | 13114.6541 | -0.048233 | 16.04 | 18.91 | 13.77 | 19.07 | 2 | 0.97 | 3.5 | 0.56
2018-06-12 04:00 | 12443.0542 | -0.048233 | 15.39 | 19.28 | 14.15 | 19.75 | 2.01 | 0.97 | 8.61 | 1
2018-06-12 05:00 | 15036.3054 | 2.4222 | 15.36 | 19.36 | 14.89 | 21.98 | 2.92 | 0.99 | 9.11 | 2.01
2018-06-12 06:00 | 15305.7685 | 56.3353 | 15.67 | 21.33 | 12.59 | 23.1 | 2.94 | 1 | 9.51 | 3
2018-06-12 07:00 | 18604.5431 | 260.638 | 15.66 | 20.13 | 12.24 | 22.73 | 2.8 | 2 | 3.3 | 2.09
2018-06-12 08:00 | 17187.8379 | 508.461 | 17.56 | 21.21 | 14.43 | 24.17 | 3.11 | 1.7 | 8.61 | 3
2018-06-12 09:00 | 18348.8557 | 779.585 | 30.73 | 28.45 | 14.1 | 34.07 | 3 | 1.77 | 8.11 | 2.95
2018-06-12 10:00 | 18968.9635 | 1004.33 | 17.64 | 24.05 | 14.58 | 29.46 | 3.82 | 3.15 | 3 | 4.15
2018-06-12 11:00 | 20494.1167 | 999.703 | 18.14 | 26.54 | 33.5 | 34.91 | 5.39 | 6 | 1 | 4.55
2018-06-12 12:00 | 18577.5635 | 1112.33 | 30.32 | 30.32 | 36.84 | 39.5 | 5.61 | 5.62 | 0.62 | 5.61
2018-06-12 13:00 | 20281.0389 | 993.462 | 34.65 | 34.65 | 40.55 | 54.07 | 8.05 | 9.42 | 0.67 | 7.39
2018-06-12 14:00 | 17757.2641 | 900.857 | 63.1 | 46.83 | 43.19 | 69.27 | 20.84 | 18.99 | 1.13 | 20.19
2018-06-12 15:00 | 16341.5495 | 855.631 | 65.24 | 65.24 | 45.24 | 88 | 26 | 19.78 | 1.5 | 25
2018-06-12 16:00 | 15481.4261 | 555.238 | 64.45 | 59.88 | 46.72 | 72.38 | 29.56 | 25 | 2.5 | 23.72
2018-06-12 17:00 | 14793.0931 | 258.677 | 64.09 | 39.76 | 45.84 | 44.26 | 16.06 | 15.12 | 2.11 | 15.92
2018-06-12 18:00 | 14533.4752 | 91.3949 | 18.26 | 29.61 | 41.8 | 34.59 | 6.58 | 1.28 | 3.5 | 4
2018-06-12 19:00 | 14207.0291 | 1.7675 | 33 | 33 | 38.34 | 35.38 | 6.16 | 1.18 | 2.5 | 3
2018-06-12 20:00 | 15882.9741 | -0.048233 | 17.65 | 28.98 | 34.24 | 33.73 | 5.45 | 1.16 | 1.37 | 3.39
2018-06-12 21:00 | 15819.6741 | -0.048233 | 17.01 | 23.42 | 15.72 | 27.94 | 4.42 | 0.99 | 11.98 | 3
2018-06-12 22:00 | 13879.4542 | -0.048233 | 16.14 | 26.96 | 14.38 | 30.56 | 3.16 | 0.3 | 11 | 3
2018-06-12 23:00 | 13501.3542 | -0.048233 | 15.15 | 30.49 | 12.88 | 26.42 | 2.11 | 0.3 | 10.53 | 2.28
2018-06-13 | 15043.1941 | -0.048233 | 15.04 | 22.41 | 12.69 | 20.97 | 2.61 | 0.3 | 20 | 2.41
2018-06-13 01:00 | 13401.6042 | -0.048233 | 14.35 | 22.81 | 11.62 | 19.88 | 2.01 | 0.25 | 5 | 1.9
2018-06-13 02:00 | 13141.3042 | -0.048233 | 13.59 | 21.12 | 10.9 | 19.22 | 2.01 | 1 | 5 | 1
2018-06-13 03:00 | 14527.2991 | -0.048233 | 13.46 | 20.44 | 10.13 | 18.7 | 2 | 1 | 3.53 | 0.69
2018-06-13 04:00 | 13727.4542 | -0.048233 | 13.87 | 20.76 | 10.84 | 19.34 | 2 | 1 | 3.44 | 1
2018-06-13 05:00 | 16483.6832 | 2.3443 | 14.42 | 20.87 | 11.76 | 20.58 | 2.64 | 0.99 | 25 | 2.17
2018-06-13 06:00 | 18755.005 | 59.2559 | 16.06 | 23.25 | 15.89 | 22.03 | 2.94 | 2 | 10.24 | 3
2018-06-13 07:00 | 19481.0424 | 261.443 | 16.6 | 24.01 | 15.44 | 21.51 | 2.59 | 2 | 3.11 | 2.61
2018-06-13 08:00 | 18157.8886 | 353.567 | 16.52 | 21.03 | 15 | 23.89 | 2.59 | 2 | 9.11 | 3
2018-06-13 09:00 | 18967.7389 | 728.041 | 17.52 | 20.29 | 17.77 | 26.42 | 3.28 | 2.25 | 3.5 | 3.16
2018-06-13 10:00 | 21301.2908 | 930.797 | 18.18 | 23.24 | 19.26 | 31.16 | 4.8 | 4.86 | 2.72 | 5.82
2018-06-13 11:00 | 19063.251 | 1088.58 | 23.04 | 24.26 | 33.79 | 36.55 | 6.39 | 7.24 | 1 | 6.2
2018-06-13 12:00 | 19140.049 | 1141.42 | 43.31 | 30.92 | 35.8 | 39.27 | 7.76 | 7.5 | 0.67 | 7.5
2018-06-13 13:00 | 18978.359 | 1087.22 | 108.26 | 69.71 | 37.92 | 52.48 | 12.94 | 11.99 | 0.88 | 11.92
2018-06-13 14:00 | 18352.3423 | 938.255 | 42.97 | 42.97 | 41.56 | 71.35 | 18.4 | 15.54 | 1 | 17.95
2018-06-13 15:00 | 19280.3961 | 803.257 | 32.12 | 30.78 | 41.07 | 80.59 | 28.81 | 23.02 | 1.79 | 27.81
2018-06-13 16:00 | 16265.1942 | 522.257 | 61.88 | 32.59 | 43.71 | 67.42 | 29.14 | 21.99 | 2 | 25.19
2018-06-13 17:00 | 15542.0703 | 244.074 | 63.53 | 33.49 | 40.45 | 42.61 | 14.84 | 15.25 | 1.62 | 17.25
2018-06-13 18:00 | 14974.7769 | 66.9231 | 48.95 | 27.23 | 37.16 | 33.25 | 8.32 | 10.81 | 10 | 4
2018-06-13 19:00 | 14948.022 | 1.76 | 21.05 | 27.95 | 35.18 | 31.04 | 6.78 | 1.46 | 3.46 | 4
2018-06-13 20:00 | 16581.3841 | -0.048233 | 20.61 | 24.03 | 32.58 | 30.7 | 5.27 | 1.33 | 2 | 3.32
2018-06-13 21:00 | 16592.9891 | -0.048233 | 19.43 | 27.24 | 17.44 | 25.58 | 4 | 1 | 11.06 | 3
2018-06-13 22:00 | 14333.5542 | -0.048233 | 17.92 | 25.54 | 15.57 | 26.37 | 4.43 | 0.25 | 25.17 | 3.43
2018-06-13 23:00 | 13441.5042 | -0.048233 | 16.42 | 24.73 | 14.38 | 23.28 | 3 | 0.3 | 20 | 2.61
2018-06-14 | 12939.9042 | -0.048233 | 15.61 | 22.29 | 16 | 23.25 | 2.48 | 0.3 | 22.03 | 2.11
2018-06-14 01:00 | 12815.4542 | -0.048233 | 14.9 | 21.89 | 14.53 | 21.74 | 2.11 | 0.3 | 10 | 2
2018-06-14 02:00 | 12550.4042 | -0.048233 | 13.95 | 20.77 | 11.25 | 20.56 | 2.01 | 0.99 | 5 | 1
2018-06-14 03:00 | 15009.4341 | -0.048233 | 13.86 | 19.96 | 9.66 | 20.37 | 2.01 | 0.99 | 4.59 | 0.5
2018-06-14 04:00 | 14003.9042 | -0.048233 | 13.62 | 21.12 | 10.55 | 21.05 | 2.01 | 0.99 | 8.5 | 1
2018-06-14 05:00 | 15192.5551 | 2.1633 | 14.23 | 21.84 | 9.69 | 22.6 | 2.25 | 1.22 | 54.1862 | 2.01
2018-06-14 06:00 | 18769.7682 | 59.2495 | 16.27 | 22.15 | 11.66 | 24.55 | 2.51 | 2 | 13.55 | 2.61
2018-06-14 07:00 | 19817.888 | 276.728 | 17.96 | 21.4 | 12.24 | 23.41 | 2.59 | 2 | 3.01 | 2.8
2018-06-14 08:00 | 20327.0922 | 552.386 | 16.87 | 21.17 | 14.24 | 24.27 | 2.59 | 2.17 | 11.21 | 3.37
2018-06-14 09:00 | 20977.5894 | 799.971 | 17.76 | 20.2 | 16.21 | 29.09 | 3.24 | 2.5 | 3.5 | 3.4
2018-06-14 10:00 | 18675.2491 | 769.157 | 18.15 | 20.6 | 16.25 | 32.17 | 3.55 | 5.59 | 2.61 | 5.33
2018-06-14 11:00 | 18683.2529 | 954.582 | 19.93 | 24.5 | 16.55 | 35.8 | 4.35 | 5.72 | 1 | 4.35
2018-06-14 12:00 | 19208.9905 | 1119.99 | 21.58 | 28.46 | 18.86 | 39.93 | 6.72 | 6.51 | 0.83 | 5.83
2018-06-14 13:00 | 19335.939 | 1044.62 | 31.52 | 31.52 | 19.55 | 56.87 | 13.38 | 11.84 | 1 | 12.47
2018-06-14 14:00 | 18071.489 | 1000.62 | 32.39 | 32.39 | 19.09 | 84.09 | 18.25 | 15.25 | 1 | 17.25
2018-06-14 15:00 | 18861.3005 | 798.01 | 32.25 | 32.25 | 19.16 | 104.29 | 30.04 | 24.05 | 1 | 26.42
2018-06-14 16:00 | 17787.0289 | 493.743 | 35.64 | 35.64 | 19.84 | 98.16 | 35.83 | 19.05 | 2 | 30.5
2018-06-14 17:00 | 15315.3813 | 211.454 | 41.49 | 41.49 | 21.31 | 54.45 | 18.04 | 12.69 | 1.9 | 15.09
2018-06-14 18:00 | 16426.7907 | 48.4177 | 29.82 | 29.82 | 20.57 | 39.94 | 12.51 | 10.99 | 2.21 | 5.76
2018-06-14 19:00 | 16318.0969 | 2.3905 | 29.54 | 29.54 | 19.56 | 37.27 | 6.98 | 0.97 | 2.31 | 4.35
2018-06-14 20:00 | 16195.2541 | -0.048233 | 22.25 | 26.29 | 19.29 | 35.26 | 5.07 | 0.95 | 1.01 | 4.2
2018-06-14 21:00 | 14630.9042 | -0.048233 | 22.11 | 29.43 | 17.39 | 31.36 | 4.5 | 0.97 | 14.57 | 3
2018-06-14 22:00 | 14285.1042 | -0.048233 | 18.7 | 23.9 | 16.22 | 29.52 | 3.63 | 0.17 | 20 | 3.51
2018-06-14 23:00 | 15259.4691 | -0.048233 | 16.92 | 30.2 | 15.51 | 27.84 | 2.81 | 0.17 | 20.7 | 2.61
2018-06-15 | 14836.4141 | -0.048233 | 15.19 | 26.22 | 15.61 | 20.82 | 2 | 0.25 | 11.93 | 2.11
2018-06-15 01:00 | 14725.6391 | -0.048233 | 15.18 | 17.61 | 14.08 | 22.01 | 2 | 0.12 | 5 | 1.95
2018-06-15 02:00 | 13255.3042 | -0.048233 | 14.1 | 17.41 | 10.55 | 19.93 | 2 | 0.76 | 3.98 | 1
2018-06-15 03:00 | 13262.9042 | -0.048233 | 13.76 | 17.04 | 9.54 | 18.79 | 2 | 0.76 | 3.5 | 0.62
2018-06-15 04:00 | 13879.4542 | -0.048233 | 13.53 | 17.11 | 9.41 | 19.39 | 1.99 | 0.76 | 3.11 | 1
2018-06-15 05:00 | 16773.8165 | 2.3521 | 14.57 | 19.48 | 10.13 | 20.19 | 2 | 0.8 | 25 | 1.95
2018-06-15 06:00 | 18620.7829 | 67.0312 | 16.68 | 19.17 | 16.34 | 21.1 | 2 | 2 | 3.5 | 2.9
2018-06-15 07:00 | 17597.666 | 164.859 | 16.5 | 19.98 | 16.31 | 21.06 | 2 | 2 | 2.61 | 2.01
2018-06-15 08:00 | 18384.2793 | 509.873 | 18.09 | 20.35 | 16.33 | 23.13 | 2.01 | 2.09 | 3.5 | 2.36
2018-06-15 09:00 | 21843.8077 | 779.031 | 17.19 | 21.45 | 18.06 | 27.87 | 2.63 | 2.46 | 2.46 | 3.21
2018-06-15 10:00 | 18777.3893 | 897.673 | 19.89 | 24.38 | 18.9 | 30.87 | 4.43 | 4.52 | 2 | 4.76
2018-06-15 11:00 | 19236.949 | 1047.42 | 29.14 | 27 | 19.68 | 38.7 | 5.02 | 6.62 | 1 | 5.08
2018-06-15 12:00 | 21278.0576 | 873.775 | 29.08 | 29.08 | 19.32 | 44.43 | 6.77 | 9.72 | 1 | 6.13
2018-06-15 13:00 | 19399.5795 | 1015.61 | 56.73 | 31.79 | 19.53 | 67.26 | 16.48 | 14.67 | 1 | 14.67
2018-06-15 14:00 | 20316.596 | 951.437 | 35.08 | 35.08 | 20 | 98.44 | 26.18 | 12.89 | 1 | 23.35
2018-06-15 15:00 | 18787.8652 | 790.403 | 37.66 | 37.66 | 20.5 | 123.23 | 49.8 | 19.85 | 1 | 40.5
2018-06-15 16:00 | 16303.9104 | 539.011 | 43.16 | 31.67 | 20.48 | 113.64 | 47.83 | 24.05 | 1 | 35
2018-06-15 17:00 | 15629.7724 | 233.392 | 32.85 | 30.82 | 20.42 | 57.01 | 19.22 | 14.05 | 1 | 14.79
2018-06-15 18:00 | 15057.639 | 64.1463 | 28.81 | 28.81 | 19.72 | 41.31 | 7.66 | 9.66 | 9.11 | 5.78
2018-06-15 19:00 | 16474.2367 | 2.3902 | 47.89 | 28.94 | 19.4 | 38.47 | 7.25 | 1.42 | 2.61 | 4.51
2018-06-15 20:00 | 16348.2291 | -0.048233 | 26.72 | 24.77 | 19.69 | 35.42 | 4.94 | 1 | 0.51 | 4.83
2018-06-15 21:00 | 16205.8041 | -0.048233 | 33.42 | 28.65 | 17.34 | 29.32 | 4.34 | 0.97 | 2 | 4.34
2018-06-15 22:00 | 15736.3291 | -0.048233 | 23.33 | 23.33 | 16.07 | 27.21 | 3.01 | 0.12 | 11.45 | 3.01
2018-06-15 23:00 | 15223.5991 | -0.048233 | 22.15 | 22.79 | 14.52 | 24.92 | 2.11 | 0.17 | 15.11 | 2.61
2018-06-16 | 13471.9042 | -0.048233 | 17.79 | 20.77 | 16.6 | 21.51 | 2.29 | 0.17 | 8.61 | 2.8
2018-06-16 01:00 | 13222.0542 | -0.048233 | 17.63 | 19.48 | 16.65 | 19.67 | 2 | 0.12 | 2.61 | 2.11
2018-06-16 02:00 | 13205.9042 | -0.048233 | 16.33 | 18.46 | 14.34 | 18.73 | 2 | 0.97 | 2.49 | 1
2018-06-16 03:00 | 14678.1641 | -0.048233 | 15.03 | 17.68 | 14.21 | 17.95 | 2 | 0.97 | 2.11 | 0.5
2018-06-16 04:00 | 13844.3042 | -0.048233 | 14.28 | 17.32 | 14.41 | 17.49 | 2 | 0.97 | 3.15 | 1
2018-06-16 05:00 | 14770.3648 | 2.7524 | 14.82 | 19.35 | 15.88 | 18.86 | 2 | 0.97 | 3.98 | 2.5
2018-06-16 06:00 | 16444.9567 | 58.4807 | 15.76 | 20.21 | 17.04 | 19.58 | 2 | 1.95 | 2.61 | 3.27
2018-06-16 07:00 | 17465.1895 | 236.41 | 16.48 | 18.83 | 18.49 | 20.91 | 2 | 1.95 | 0.51 | 2.5
2018-06-16 08:00 | 20525.0851 | 562.057 | 17.15 | 20.29 | 17.2 | 22.2 | 2.44 | 2.13 | 0.71 | 3.03
2018-06-16 09:00 | 22149.6132 | 789.894 | 17.96 | 21.38 | 18.73 | 26.28 | 2.5 | 2.5 | 0.71 | 3.14
2018-06-16 10:00 | 19039.3433 | 959.414 | 21.94 | 25.12 | 19.4 | 33.5 | 4.51 | 4.6 | 2 | 5.5
2018-06-16 11:00 | 18680.8 | 1108 | 21.79 | 27.43 | 20.16 | 38.53 | 6.01 | 6.04 | 1 | 5.97
2018-06-16 12:00 | 18534.2055 | 1092.69 | 20.08 | 31.82 | 20.89 | 46.4 | 8.55 | 10 | 1 | 10
2018-06-16 13:00 | 18738.8849 | 945.142 | 40.06 | 40.06 | 20.98 | 67.25 | 15.04 | 15.04 | 1 | 14.51
2018-06-16 14:00 | 20091.8789 | 984.435 | 33.85 | 33.85 | 20.98 | 95.43 | 28.32 | 14.05 | 1 | 15.43
2018-06-16 15:00 | 18884.4346 | 804.938 | 63.43 | 33.72 | 19.98 | 118.57 | 52.33 | 19.16 | 1 | 29.97
2018-06-16 16:00 | 18084.8564 | 588.044 | 63.19 | 32.98 | 20.55 | 109.45 | 53.59 | 14.45 | 2.11 | 32.91
2018-06-16 17:00 | 15762.286 | 288.88 | 86.66 | 32.91 | 19.95 | 56.42 | 16.75 | 12.43 | 2.11 | 12.88
2018-06-16 18:00 | 15208.4152 | 39.8581 | 63.37 | 30.77 | 19.04 | 41.18 | 7.75 | 7.27 | 20 | 5.08
2018-06-16 19:00 | 15073.7842 | 1.1412 | 36.2 | 29.72 | 18.61 | 35.92 | 7.25 | 1.26 | 2.21 | 4
2018-06-16 20:00 | 14831.3542 | -0.048233 | 22.08 | 28.4 | 18.41 | 30.87 | 4.53 | 0.97 | 1 | 3.42
2018-06-16 21:00 | 16383.0441 | -0.048233 | 22.43 | 27.31 | 17.55 | 26.93 | 3.8 | 0.97 | 2 | 3
2018-06-16 22:00 | 14206.2542 | -0.048233 | 21.36 | 23.21 | 16 | 27.19 | 3.13 | 0.17 | 2.61 | 3.13
2018-06-16 23:00 | 13861.4042 | -0.048233 | 19.42 | 22.63 | 16 | 24.49 | 2.87 | 0.17 | 3.76 | 2.87
2018-06-17 | 15004.1591 | -0.048233 | 15.41 | 21.61 | 15.33 | 22.66 | 2 | 0.17 | 2.61 | 1.95
2018-06-17 01:00 | 14662.3391 | -0.048233 | 14.15 | 20 | 15.19 | 22.97 | 2 | 0.18 | 2.11 | 1.8
2018-06-17 02:00 | 14492.4841 | -0.048233 | 13.41 | 19.47 | 13.77 | 18.8 | 2 | 0.97 | 2.11 | 1
2018-06-17 03:00 | 12940.8542 | -0.048233 | 12.67 | 17.78 | 13.3 | 18.89 | 2 | 0.97 | 2.11 | 0.33
2018-06-17 04:00 | 13204.0042 | -0.048233 | 13.49 | 17.65 | 13.78 | 18.6 | 2 | 0.97 | 2.84 | 1
2018-06-17 05:00 | 15214.518 | 2.3441 | 13.95 | 17.27 | 14.14 | 19 | 1.93 | 0.97 | 3.5 | 1.73
2018-06-17 06:00 | 14007.9167 | 65.1755 | 14.62 | 17.23 | 14.95 | 25.55 | 2.01 | 1.95 | 1.44 | 2.61
2018-06-17 07:00 | 15769.6842 | 254.568 | 15 | 17.03 | 15 | 23.38 | 2.06 | 1.99 | 0.71 | 2.06
2018-06-17 08:00 | 16480.7722 | 519.585 | 16.18 | 18.7 | 17.01 | 36.94 | 2 | 2 | 3.5 | 2.44
2018-06-17 09:00 | 15321.8356 | 798.248 | 17.2 | 19.95 | 18.14 | 38.45 | 2.5 | 1.95 | 3.11 | 2.61
2018-06-17 10:00 | 16552.7379 | 895.799 | 20.24 | 21.03 | 18.7 | 47.48 | 2.5 | 6.38 | 2.11 | 4
2018-06-17 11:00 | 14694.847 | 1075.26 | 23 | 23.72 | 19.3 | 55.75 | 4.9 | 8.17 | 1 | 5
2018-06-17 12:00 | 15492.0205 | 1100.39 | 27.54 | 27.54 | 20.13 | 61.65 | 17.57 | 12.22 | 1 | 5
2018-06-17 13:00 | 16360.6974 | 1051.77 | 29.95 | 29.95 | 20.34 | 70.88 | 26.13 | 18.02 | 1 | 21.13
2018-06-17 14:00 | 15913.9808 | 958.342 | 39.77 | 29.63 | 20.77 | 100.77 | 45 | 15.15 | 1 | 34.47
2018-06-17 15:00 | 14001.1864 | 773.091 | 81.95 | 31.52 | 21.32 | 111.55 | 112.3041 | 70.0673 | 1 | 102.7262
2018-06-17 16:00 | 13586.3138 | 487.383 | 93.24 | 31.45 | 21.22 | 105.55 | 111.5941 | 69.2873 | 1 | 97.5562
2018-06-17 17:00 | 14729.3603 | 212.479 | 70.39 | 30.69 | 20.94 | 68.64 | 40.25 | 12 | 1 | 27.36
2018-06-17 18:00 | 14608.5846 | 63.9996 | 68.82 | 28.77 | 18.94 | 61.76 | 20.7 | 1 | 15 | 5.32
2018-06-17 19:00 | 13023.8516 | 2.3174 | 27.35 | 26.09 | 19.54 | 49.73 | 6.85 | 1.27 | 2.11 | 4
2018-06-17 20:00 | 14452.3941 | -0.048233 | 22.5 | 22.5 | 20.08 | 38.06 | 5.76 | 1 | 1.19 | 3.11
2018-06-17 21:00 | 14424.9641 | -0.048233 | 22.56 | 23.29 | 17.99 | 27.95 | 4.02 | 1.18 | 10.23 | 3
2018-06-17 22:00 | 14263.5491 | -0.048233 | 20.99 | 21.85 | 17.15 | 28.86 | 3.16 | 0.17 | 8.61 | 3.16
2018-06-17 23:00 | 14107.4091 | -0.048233 | 18.93 | 22.07 | 17.12 | 32.7 | 2.8 | 0.17 | 4 | 2.61
2018-06-18 | 14063.0991 | -0.048233 | 17.77 | 20.1 | 14.98 | 23.82 | 2.11 | 0.25 | 3.11 | 2.21
2018-06-18 01:00 | 13918.5641 | -0.048233 | 16.98 | 19.18 | 13.53 | 22.41 | 2 | 0.25 | 2.51 | 1.97
2018-06-18 02:00 | 12335.7042 | -0.048233 | 16.06 | 18.41 | 8.61 | 21.07 | 1.9 | 1 | 3.8 | 1.5
2018-06-18 03:00 | 12265.4042 | -0.048233 | 14.29 | 17.58 | 7.65 | 19.17 | 1.81 | 1 | 3.5 | 1.11
2018-06-18 04:00 | 13527.1591 | -0.048233 | 14.31 | 16.99 | 10.26 | 20.05 | 1.87 | 1 | 3.11 | 1.13
2018-06-18 05:00 | 13492.1776 | 1.794 | 14.97 | 16.95 | 13.65 | 21.3 | 2 | 1 | 3.96 | 2.17
2018-06-18 06:00 | 13243.3862 | 71.9727 | 16 | 16.78 | 13.61 | 22.95 | 2.11 | 2 | 2.11 | 3
2018-06-18 07:00 | 11879.768 | 249.019 | 16.32 | 16.56 | 15.39 | 23.56 | 2 | 2 | 0.61 | 2
2018-06-18 08:00 | 13648.3936 | 528.866 | 18.67 | 18.78 | 17.04 | 25.55 | 2 | 2 | 2 | 2.82
2018-06-18 09:00 | 12718.9914 | 767.412 | 18.34 | 20.05 | 17.91 | 32.79 | 2.5 | 10 | 2 | 3.35
2018-06-18 10:00 | 14531.4476 | 945.884 | 21.07 | 21.07 | 17.47 | 41.75 | 3.36 | 7.05 | 1.4 | 5.54
2018-06-18 11:00 | 14906.3376 | 1076.23 | 23.61 | 23.61 | 19.17 | 52.38 | 2.5 | 8.27 | 0.83 | 3.6
2018-06-18 12:00 | 13474.4105 | 1125.59 | 28.47 | 25.68 | 19.84 | 59.04 | 4.9 | 14.88 | 1 | 14.88
2018-06-18 13:00 | 13532.731 | 1106.98 | 35.17 | 31.37 | 20.52 | 77.54 | 15.5 | 15.99 | 1.23 | 12.91
2018-06-18 14:00 | 14964.6433 | 955.496 | 32.56 | 32.05 | 20.7 | 101.59 | 21.13 | 12.75 | 1.82 | 14.25
2018-06-18 15:00 | 14854.3251 | 794.929 | 40.42 | 35.51 | 20.12 | 111.55 | 40.75 | 18.36 | 2.11 | 30.85
2018-06-18 16:00 | 14653.8656 | 565.92 | 57.8 | 33.12 | 20.05 | 111.35 | 52.25 | 23.68 | 2.31 | 32.52
2018-06-18 17:00 | 14398.6643 | 257.023 | 30.96 | 29.74 | 20.72 | 71.78 | 21.06 | 14.7 | 2 | 17.11
2018-06-18 18:00 | 12821.234 | 66.0358 | 28.73 | 28.73 | 18.54 | 55.61 | 14.28 | 1.48 | 10 | 6.22
2018-06-18 19:00 | 13928.4977 | 2.3674 | 28.39 | 23.71 | 17.76 | 51.07 | 6.85 | 1 | 2.61 | 3.8
2018-06-18 20:00 | 12521.9042 | -0.048233 | 23.78 | 23.78 | 18.03 | 35.8 | 6.29 | 0.99 | 2 | 4.8
2018-06-18 21:00 | 14125.3441 | -0.048233 | 26.98 | 26.98 | 17.93 | 32.9 | 4.82 | 1.15 | 8.61 | 4.01
2018-06-18 22:00 | 12662.5042 | -0.048233 | 32.46 | 25.67 | 17.01 | 28.07 | 3 | 0.25 | 8.11 | 3
2018-06-18 23:00 | 13725.4991 | -0.048233 | 20.21 | 21.83 | 16.38 | 35.28 | 2.59 | 0.25 | 3.48 | 2.74
2018-06-19 | 13549.3141 | -0.048233 | 18.13 | 21 | 15.98 | 23.74 | 2.25 | 0.17 | 2.67 | 2.4
2018-06-19 01:00 | 12123.8542 | -0.048233 | 17.89 | 20.67 | 12.59 | 24.26 | 2 | 0.17 | 2.24 | 1.87
2018-06-19 02:00 | 12043.1042 | -0.048233 | 17.29 | 20.26 | 10.73 | 21.22 | 1.95 | 0.99 | 3.11 | 1.5
2018-06-19 03:00 | 13372.0741 | -0.048233 | 16.48 | 19.9 | 8.84 | 20.52 | 1.85 | 0.99 | 2.61 | 1.5
2018-06-19 04:00 | 13940.7191 | -0.048233 | 16.15 | 20.1 | 8.29 | 20.52 | 1.81 | 0.99 | 2.61 | 1.5
2018-06-19 05:00 | 13439.4419 | 1.781 | 15.96 | 20.72 | 9.36 | 22.72 | 1.85 | 0.99 | 3.44 | 2.21
2018-06-19 06:00 | 15705.0702 | 61.6528 | 15.94 | 21.18 | 11.05 | 24.08 | 2.25 | 2 | 2 | 3
2018-06-19 07:00 | 18884.5538 | 241.051 | 15.5 | 21.96 | 13.73 | 23.24 | 2.11 | 1.81 | 0.51 | 2.1
2018-06-19 08:00 | 17535.7431 | 543.677 | 17.55 | 22.14 | 15.95 | 29.56 | 2.5 | 2.1 | 1.95 | 2.5
2018-06-19 09:00 | 20005.5958 | 811.65 | 18.07 | 22.81 | 17.33 | 30 | 3.55 | 2.59 | 1.95 | 3.55
2018-06-19 10:00 | 19984.1972 | 887.367 | 19.31 | 26.14 | 18.34 | 54.9 | 5.84 | 6 | 1.36 | 5.84
2018-06-19 11:00 | 18122.8555 | 1068.69 | 68.24 | 68.24 | 20.85 | 67.02 | 6.63 | 11.86 | 1 | 11.86
2018-06-19 12:00 | 18084.4888 | 908.304 | 35.12 | 35.12 | 19.81 | 75.55 | 16 | 15 | 1 | 15
2018-06-19 13:00 | 20300.8059 | 1125.47 | 244.8657 | 200.54 | 20.26 | 95.55 | 22.25 | 18.75 | 1 | 19.94
2018-06-19 14:00 | 19293.9307 | 899.086 | 729.1411 | 461.53 | 21.19 | 120.57 | 39.93 | 14.35 | 1.74 | 25
2018-06-19 15:00 | 16204.6174 | 698.492 | 1535.5311 | 1267.92 | 22.91 | 137.03 | 91.3241 | 26.55 | 1.95 | 44.69
2018-06-19 16:00 | 17211.4219 | 508.144 | 664.9711 | 397.36 | 23.18 | 113.87 | 85.0641 | 25 | 2.31 | 42.19
2018-06-19 17:00 | 14934.931 | 268.98 | 276.7057 | 232.38 | 23.07 | 74.92 | 29.91 | 14.23 | 1.45 | 24.91
2018-06-19 18:00 | 16134.5374 | 62.4004 | 114.48 | 114.48 | 21.05 | 55.39 | 19.08 | 6.78 | 10 | 12.48
2018-06-19 19:00 | 14302.577 | 2.3442 | 109.34 | 109.34 | 20.01 | 58.72 | 19.26 | 1.23 | 2.31 | 12.52
2018-06-19 20:00 | 15909.3491 | -0.048233 | 32.41 | 32.41 | 20.72 | 41.38 | 5.81 | 1.29 | 2.61 | 3.69
2018-06-19 21:00 | 15843.9391 | -0.048233 | 35.15 | 35.15 | 18.65 | 36.43 | 4.39 | 1.14 | 8.11 | 4.15
2018-06-19 22:00 | 15350.1991 | -0.048233 | 23.22 | 23.22 | 16.37 | 30.79 | 3.29 | 0.3 | 8.39 | 3.29
2018-06-19 23:00 | 15089.6141 | -0.048233 | 18.09 | 30.4 | 16.33 | 29.34 | 2.76 | 0.25 | 3.01 | 3
2018-06-20 | 13356.9542 | -0.048233 | 17.78 | 21.88 | 17 | 21.78 | 2 | 0.25 | 3.36 | 1.8
2018-06-20 01:00 | 14715.0891 | -0.048233 | 17.02 | 19.99 | 15.08 | 22.58 | 2 | 0.25 | 2.61 | 1.5
2018-06-20 02:00 | 14543.1241 | -0.048233 | 16.23 | 19.47 | 11.69 | 19.83 | 2 | 0.99 | 2.67 | 1.25
2018-06-20 03:00 | 12990.2542 | -0.048233 | 15.64 | 19.39 | 11.65 | 19.5 | 2 | 0.99 | 2.27 | 1
2018-06-20 04:00 | 14916.5941 | -0.048233 | 15.65 | 19.41 | 11.66 | 19.46 | 2 | 0.99 | 2.11 | 1.01
2018-06-20 05:00 | 14454.9849 | 1.7736 | 16.49 | 20.04 | 15.82 | 20.2 | 2 | 0.99 | 3.01 | 1.5
2018-06-20 06:00 | 18092.5121 | 56.3006 | 17.29 | 20.4 | 16.44 | 21.9 | 2 | 1.82 | 2.61 | 2.31
2018-06-20 07:00 | 19000.2303 | 197.697 | 17.59 | 20.91 | 13.9 | 22.14 | 2 | 1.82 | 2.11 | 2
2018-06-20 08:00 | 17828.2871 | 250.618 | 18.1 | 21.62 | 14.46 | 23.35 | 2 | 1.95 | 2.31 | 2
2018-06-20 09:00 | 20421.0368 | 240.433 | 17.65 | 23.52 | 16.97 | 28.02 | 2.5 | 2.24 | 2.6 | 2.5
2018-06-20 10:00 | 21143.62 | 921.346 | 18.13 | 28.46 | 16.26 | 41.81 | 3.6 | 5.71 | 2 | 3.6
2018-06-20 11:00 | 21119.4014 | 1071.39 | 31.64 | 31.64 | 16.55 | 50.59 | 5.55 | 7.5 | 1 | 4.69
2018-06-20 12:00 | 19670.776 | 1114.08 | 32.79 | 32.79 | 17.52 | 54.98 | 13.68 | 13.5 | 0.83 | 13.68
2018-06-20 13:00 | 21298.0551 | 1042.73 | 37.28 | 37.28 | 18.35 | 71 | 22.25 | 20.44 | 1 | 20.44
2018-06-20 14:00 | 20738.308 | 952.164 | 88.21 | 88.21 | 18.82 | 82.78 | 27.8 | 14.5 | 1.83 | 20.65
2018-06-20 15:00 | 19298.6371 | 761.547 | 67.91 | 67.91 | 22.15 | 107.17 | 80.8241 | 25.01 | 2 | 42.53
2018-06-20 16:00 | 16723.1939 | 566.362 | 103.76 | 103.76 | 22.99 | 83.99 | 37.94 | 20 | 2.12 | 24.45
2018-06-20 17:00 | 17827.5693 | 261.17 | 54.2 | 54.2 | 22.17 | 52.17 | 19.22 | 13.16 | 2.11 | 16.79
2018-06-20 18:00 | 17311.0772 | 55.604 | 55.44 | 55.44 | 18 | 41.32 | 15.01 | 6.86 | 10 | 6.41
2018-06-20 19:00 | 17190.5049 | 2.3174 | 55.27 | 55.27 | 16.41 | 38.22 | 6.85 | 1.92 | 2.31 | 3.95
2018-06-20 20:00 | 15402.3042 | -0.048233 | 37.68 | 37.68 | 16.97 | 34.85 | 5.01 | 1.24 | 2.11 | 3.33
2018-06-20 21:00 | 15086.9042 | -0.048233 | 158.64 | 158.64 | 16.4 | 40.1 | 4.29 | 1.25 | 7.75 | 4.09
2018-06-20 22:00 | 16362.9991 | -0.048233 | 95.02 | 95.02 | 16.33 | 33.35 | 3 | 0.3 | 3 | 3
2018-06-20 23:00 | 14235.7042 | -0.048233 | 117.44 | 117.44 | 16.01 | 24.93 | 2.11 | 0.25 | 3.46 | 2.29
2018-06-21 | 15604.4541 | -0.048233 | 18.19 | 21.63 | 16.35 | 32.63 | 2 | 0.17 | 3.46 | 1.5
2018-06-21 01:00 | 15485.2391 | -0.048233 | 17.84 | 20.84 | 13.89 | 31.73 | 2 | 0.17 | 2.59 | 1.5
2018-06-21 02:00 | 15276.3491 | -0.048233 | 16.48 | 22.18 | 13.48 | 23.57 | 2 | 0.99 | 3 | 1.01
2018-06-21 03:00 | 13530.8042 | -0.048233 | 16.12 | 20.72 | 12.09 | 21.06 | 2 | 0.99 | 3.11 | 1
2018-06-21 04:00 | 15854.4891 | -0.048233 | 16.06 | 19.45 | 11.58 | 20.63 | 2 | 0.99 | 2.96 | 1.01
2018-06-21 05:00 | 15210.4901 | 3.0422 | 16.76 | 20.33 | 8.5 | 21.55 | 2 | 0.99 | 3.5 | 1.5
2018-06-21 06:00 | 18357.9686 | 60.9181 | 17.75 | 25 | 11.4 | 22.28 | 2 | 1.31 | 3.95 | 2.25
2018-06-21 07:00 | 19775.0561 | 228.129 | 18 | 19.68 | 13.47 | 21.62 | 2 | 1.62 | 2.61 | 2
2018-06-21 08:00 | 19576.8522 | 403.258 | 17.86 | 20.39 | 12.65 | 27.06 | 2 | 1.82 | 3.01 | 2
2018-06-21 09:00 | 21155.3063 | 677.423 | 17.97 | 21.02 | 15.26 | 38.32 | 2 | 2.23 | 2.11 | 2
2018-06-21 10:00 | 20469.398 | 710.273 | 17.87 | 21.46 | 15.54 | 61.61 | 3.2 | 3.05 | 2 | 3.2
2018-06-21 11:00 | 20959.8559 | 971.162 | 67.81 | 67.81 | 16.35 | 67.02 | 4.94 | 6.72 | 1 | 4.25
2018-06-21 12:00 | 22887.4338 | 1073.25 | 38.25 | 38.25 | 16.58 | 77.49 | 6.24 | 10.56 | 0.97 | 5.24
2018-06-21 13:00 | 22189.1925 | 1011.41 | 31.48 | 31.48 | 18.32 | 88.02 | 16 | 13.3 | 1 | 13.22
2018-06-21 14:00 | 20292.2435 | 751.354 | 76.22 | 76.22 | 19.14 | 102.29 | 21.27 | 9.81 | 2 | 18.56
2018-06-21 15:00 | 17287.3561 | 767.217 | 48.56 | 48.56 | 23.63 | 111.55 | 31.03 | 15.92 | 2 | 29.43
2018-06-21 16:00 | 15948.0252 | 294.395 | 139.61 | 139.61 | 24.23 | 98.8 | 30.49 | 15.12 | 2.11 | 23.86
2018-06-21 17:00 | 15399.6643 | 191.173 | 42.09 | 42.09 | 23.68 | 53.95 | 14.37 | 11.25 | 2 | 13.37
2018-06-21 18:00 | 15371.5293 | 65.5572 | 63.23 | 63.23 | 21.29 | 39 | 8.04 | 2.4 | 10 | 4
2018-06-21 19:00 | 16703.1481 | 2.3679 | 80.23 | 80.23 | 21.1 | 33.5 | 6.4 | 1.56 | 2.31 | 3
2018-06-21 20:00 | 16455.8391 | -0.048233 | 163.64 | 163.64 | 20.94 | 34.21 | 5.37 | 1.08 | 2 | 3
2018-06-21 21:00 | 16376.7141 | -0.048233 | 19.25 | 28.21 | 20.38 | 34.54 | 4.6 | 0.99 | 4.46 | 2.31
2018-06-21 22:00 | 15837.6091 | -0.048233 | 51.47 | 51.47 | 17.84 | 30.82 | 3 | 0.12 | 2.73 | 3
2018-06-21 23:00 | 13643.8542 | -0.048233 | 18.2 | 21.84 | 16.42 | 24.9 | 2.25 | 0.17 | 3 | 1.87
2018-06-22 | 13395.9042 | -0.048233 | 17.53 | 27.93 | 16.38 | 30.9 | 2 | 0.17 | 4 | 1.8
2018-06-22 01:00 | 13137.5042 | -0.048233 | 15.83 | 19.01 | 16.18 | 35.52 | 2 | 0.17 | 2.61 | 1.5
2018-06-22 02:00 | 14270.9341 | -0.048233 | 12.24 | 18.06 | 15.79 | 29.02 | 1.8 | 0.97 | 2.99 | 1.5
2018-06-22 03:00 | 14053.6041 | -0.048233 | 14.58 | 18.62 | 14.44 | 24.15 | 1.8 | 0.97 | 2.61 | 1.2
2018-06-22 04:00 | 13314.2042 | -0.048233 | 13.82 | 18.62 | 14.62 | 20.89 | 1.8 | 0.97 | 2.61 | 1.5
2018-06-22 05:00 | 14378.029 | 1.7674 | 14.21 | 19.23 | 16.18 | 21.54 | 2 | 0.97 | 3.5 | 1.8
2018-06-22 06:00 | 17421.1344 | 70.9236 | 17.16 | 19.14 | 17.08 | 22.75 | 2.11 | 1.52 | 2.64 | 2.61
2018-06-22 07:00 | 18153.1128 | 105.742 | 17.64 | 19.46 | 18.25 | 22.16 | 2 | 1.6 | 1.89 | 2
2018-06-22 08:00 | 19231.3059 | 330.726 | 18.14 | 20 | 19.29 | 32.63 | 2.14 | 1.25 | 2.63 | 2.25
2018-06-22 09:00 | 19896.2366 | 576.992 | 18.08 | 20.47 | 20.5 | 38.11 | 2.63 | 2.5 | 3.5 | 2.63
2018-06-22 10:00 | 19848.3111 | 496.565 | 18.21 | 21.34 | 20.27 | 62.28 | 5.21 | 5.41 | 2.31 | 5.38
2018-06-22 11:00 | 17968.3912 | 752.096 | 42.91 | 42.91 | 21.33 | 82.08 | 7.15 | 6.21 | 1 | 6.15
2018-06-22 12:00 | 21011.5699 | 1108.18 | 59.61 | 59.61 | 21.37 | 92.37 | 9.18 | 8.64 | 1 | 10.04
2018-06-22 13:00 | 21059.469 | 974.582 | 159.31 | 159.31 | 21.87 | 111.7 | 20.68 | 19.79 | 1 | 19.79
2018-06-22 14:00 | 19961.8533 | 559.188 | 258.0257 | 213.7 | 21.88 | 131.96 | 21.83 | 11.65 | 2.02 | 19.04
2018-06-22 15:00 | 19248.4328 | 769.96 | 267.0957 | 222.77 | 22.75 | 141.04 | 35.66 | 21.33 | 2 | 33.55
2018-06-22 16:00 | 16453.0376 | 515.987 | 263.7857 | 219.46 | 22.42 | 135.76 | 33.29 | 15 | 2.39 | 27.35
2018-06-22 17:00 | 15801.9846 | 269.668 | 247.9357 | 203.61 | 22 | 83.57 | 17.54 | 15.57 | 2 | 16.77
2018-06-22 18:00 | 15202.3693 | 80.494 | 179.43 | 179.43 | 21.71 | 58.85 | 13.16 | 8.62 | 10 | 5.26
2018-06-22 19:00 | 14919.1016 | 2.3175 | 275.9157 | 231.59 | 21.55 | 41.66 | 5.69 | 1.08 | 3.01 | 4
2018-06-22 20:00 | 15053.6542 | -0.048233 | 32.21 | 32.21 | 21.57 | 35.13 | 5.01 | 1.15 | 2 | 3.01
2018-06-22 21:00 | 15031.8042 | -0.048233 | 30.97 | 30.97 | 20.98 | 35.44 | 4.18 | 0.97 | 4.37 | 3.11
2018-06-22 22:00 | 14749.6542 | -0.048233 | 20.6 | 21.86 | 18.78 | 31.72 | 2.89 | 0.25 | 2.61 | 3.03
2018-06-22 23:00 | 15843.9391 | -0.048233 | 17.94 | 23.78 | 17.85 | 32.89 | 2 | 0.25 | 3.2 | 2.31
2018-06-23 | 14059.0042 | -0.048233 | 17.62 | 21.47 | 17.59 | 20.41 | 2 | 0.17 | 3.25 | 2.09
2018-06-23 01:00 | 15511.6141 | -0.048233 | 16.56 | 20.94 | 17.03 | 20.04 | 2 | 0.12 | 3.95 | 1.5
2018-06-23 02:00 | 13931.7042 | -0.048233 | 15.69 | 19.96 | 16.45 | 18.97 | 1.81 | 0.81 | 3.28 | 1.5
2018-06-23 03:00 | 13723.6542 | -0.048233 | 15.16 | 18.72 | 16.39 | 18.49 | 1.8 | 0.81 | 3.11 | 1
2018-06-23 04:00 | 16007.4641 | -0.048233 | 15.51 | 18.6 | 16.39 | 19.28 | 1.8 | 0.81 | 2.79 | 1.11
2018-06-23 05:00 | 17116.0812 | 1.7736 | 16.83 | 20.04 | 17 | 21.76 | 2 | 0.81 | 3.5 | 2.02
2018-06-23 06:00 | 16958.4136 | 47.9617 | 19.16 | 20.39 | 18.25 | 21.53 | 2.01 | 1.64 | 2.11 | 2.11
2018-06-23 07:00 | 19601.7291 | 217.838 | 18.44 | 20.54 | 16.98 | 21.11 | 2 | 1.25 | 2.16 | 2.11
2018-06-23 08:00 | 20343.4352 | 469.877 | 19.5 | 22.66 | 18.84 | 23.44 | 2.39 | 2 | 2.61 | 2.5
2018-06-23 09:00 | 18909.427 | 621.66 | 19.92 | 23.06 | 20.98 | 28.64 | 3.75 | 3.7 | 2.61 | 3.75
2018-06-23 10:00 | 19089.3513 | 844.054 | 46.38 | 23.14 | 21.06 | 32.5 | 4.77 | 5.85 | 2 | 5.27
2018-06-23 11:00 | 19149.7865 | 857.67 | 28.77 | 28.77 | 21.54 | 42.04 | 7.3 | 6.91 | 1 | 5.64
2018-06-23 12:00 | 21209.2041 | 738.511 | 30.89 | 30.89 | 22.28 | 55.56 | 8.55 | 11.47 | 1 | 11.47
2018-06-23 13:00 | 21075.3974 | 742.68 | 51.24 | 51.24 | 22.81 | 79.22 | 23.73 | 23.81 | 1.3 | 22.73
2018-06-23 14:00 | 20561.662 | 731.727 | 64.43 | 64.43 | 28.13 | 128.72 | 37.84 | 22.94 | 2 | 30.81
2018-06-23 15:00 | 19405.996 | 618.309 | 152.32 | 152.32 | 32.12 | 150 | 80.7741 | 29.7 | 2 | 46.69
2018-06-23 16:00 | 16393.6997 | 292.526 | 48.48 | 48.48 | 32.39 | 122.8 | 40.16 | 19.99 | 2 | 30.5
2018-06-23 17:00 | 15876.8969 | 252.523 | 33.78 | 33.78 | 28.64 | 68.13 | 19.17 | 15.76 | 2 | 17.86
2018-06-23 18:00 | 15210.2267 | 78.765 | 29.96 | 29.96 | 22.08 | 46.12 | 12.62 | 1.53 | 3 | 5
2018-06-23 19:00 | 15139.975 | 1.8158 | 29.56 | 29.56 | 20.91 | 37.29 | 8.14 | 1.25 | 2.61 | 4
2018-06-23 20:00 | 16805.0441 | -0.048233 | 27.08 | 27.08 | 20.38 | 34.68 | 6.09 | 1.11 | 1.26 | 4
2018-06-23 21:00 | 15061.2542 | -0.048233 | 28.32 | 28.32 | 18.57 | 30.62 | 4.61 | 0.81 | 10.76 | 3
2018-06-23 22:00 | 14571.0542 | -0.048233 | 18.96 | 25.31 | 18.44 | 33.42 | 3 | 0.12 | 9 | 3
2018-06-23 23:00 | 15715.2291 | -0.048233 | 17.64 | 26.26 | 17.59 | 29.4 | 2 | 0.12 | 3.62 | 2.61
2018-06-24 | 15118.0991 | -0.048233 | 63.26 | 63.26 | 17.17 | 26.62 | 2.22 | 0.17 | 3.47 | 2.61
2018-06-24 01:00 | 13382.6042 | -0.048233 | 15.83 | 29.78 | 16.36 | 21.74 | 2 | 0.17 | 3.98 | 2.01
2018-06-24 02:00 | 13333.2042 | -0.048233 | 51.92 | 51.92 | 15.21 | 19.92 | 1.8 | 0.99 | 3.5 | 1.6
2018-06-24 03:00 | 13080.5042 | -0.048233 | 80.19 | 80.19 | 14.62 | 19.3 | 1.8 | 0.99 | 3.46 | 1.11
2018-06-24 04:00 | 13310.4042 | -0.048233 | 102 | 102 | 14.55 | 18.67 | 1.8 | 1 | 3.5 | 1.6
2018-06-24 05:00 | 14352.379 | 1.7673 | 149.86 | 149.86 | 15.31 | 18.54 | 2 | 1 | 4.5 | 2.11
2018-06-24 06:00 | 15142.7839 | 59.7725 | 18.06 | 20.83 | 17.01 | 20.09 | 2 | 1.3 | 2.61 | 2.5
2018-06-24 07:00 | 17014.541 | 262.527 | 18.28 | 27.12 | 16.42 | 21.13 | 2 | 1.84 | 1.74 | 2
2018-06-24 08:00 | 17310.402 | 348.964 | 19.33 | 19.48 | 18.24 | 23.39 | 2.5 | 2 | 3.01 | 2.83
2018-06-24 09:00 | 17621.3949 | 399.744 | 18.86 | 19.16 | 18.78 | 27.38 | 3.62 | 2.5 | 3.24 | 3.4
2018-06-24 10:00 | 16092.4841 | 685.457 | 19.39 | 19.39 | 19.68 | 31.67 | 4.81 | 5.57 | 2.45 | 6.5
2018-06-24 11:00 | 15783.8985 | 586.63 | 20.58 | 20.58 | 19.65 | 35.77 | 3.18 | 6.45 | 1 | 4.52
2018-06-24 12:00 | 16253.8065 | 1095.27 | 28.04 | 25.72 | 21 | 40.68 | 3.72 | 8.5 | 1 | 4.22
2018-06-24 13:00 | 15653.5319 | 941.402 | 32.38 | 27.14 | 21.51 | 49.79 | 14.27 | 9.71 | 1 | 13.91
2018-06-24 14:00 | 16531.2275 | 570.41 | 21.66 | 23.21 | 21.67 | 58.03 | 16.3 | 11.24 | 1 | 15.09
2018-06-24 15:00 | 14794.653 | 491.319 | 37.32 | 22.01 | 21.7 | 64.03 | 30.72 | 21.24 | 2 | 29.99
2018-06-24 16:00 | 13941.2918 | 346.044 | 32.5 | 22.73 | 21.69 | 60.66 | 28.94 | 21.55 | 2 | 26.17
2018-06-24 17:00 | 15266.0789 | 148.217 | 34.59 | 24.72 | 21.63 | 38.85 | 17.79 | 12.5 | 2 | 16.47
2018-06-24 18:00 | 15122.0776 | 59.7228 | 28.36 | 26 | 20.36 | 34.44 | 6.43 | 1.47 | 10.43 | 4.04
2018-06-24 19:00 | 13664.6378 | 4.8293 | 20.06 | 21.79 | 20.28 | 29.93 | 5.77 | 1.23 | 3.5 | 4
2018-06-24 20:00 | 13659.0542 | -0.048233 | 21.2 | 21.44 | 18.81 | 31.29 | 5.02 | 0.99 | 2 | 4
2018-06-24 21:00 | 13555.5042 | -0.048233 | 22.34 | 22.57 | 19.23 | 28.38 | 4.12 | 0.99 | 19.23 | 3.63
2018-06-24 22:00 | 14874.3941 | -0.048233 | 19.67 | 21.61 | 17.16 | 27.17 | 3.25 | 0.12 | 15.96 | 3.34
2018-06-24 23:00 | 13169.8042 | -0.048233 | 78.25 | 78.25 | 16.69 | 24.93 | 2.59 | 0.12 | 20 | 3
2018-06-25 | 12733.7542 | -0.048233 | 16.74 | 19.73 | 14.57 | 26.72 | 2.25 | 0.25 | 9.01 | 3
2018-06-25 01:00 | 14183.3691 | -0.048233 | 16.38 | 20.13 | 13.63 | 24.35 | 2.01 | 0.25 | 3.95 | 2.1
2018-06-25 02:00 | 14159.1041 | -0.048233 | 14.87 | 19.43 | 13.53 | 22.69 | 1.8 | 0.97 | 3.5 | 1.6
2018-06-25 03:00 | 13959.7091 | -0.048233 | 14.25 | 19.08 | 10.83 | 22.07 | 1.75 | 0.97 | 3.11 | 1.55
2018-06-25 04:00 | 12387.9542 | -0.048233 | 13.85 | 19.08 | 10.85 | 21.56 | 1.75 | 0.97 | 3.11 | 1.61
2018-06-25 05:00 | 12491.6989 | 1.1568 | 13.76 | 19.19 | 10.85 | 21.36 | 1.8 | 0.99 | 4.66 | 2.11
2018-06-25 06:00 | 12631.6417 | 37.4649 | 13.85 | 19.34 | 14.78 | 21.31 | 2.01 | 1.25 | 2.77 | 2.5
2018-06-25 07:00 | 13800.5879 | 109.126 | 14.65 | 19.38 | 16.02 | 21.62 | 2.11 | 1.7 | 2 | 2.11
2018-06-25 08:00 | 12901.6992 | 396.736 | 16.92 | 20.06 | 15.37 | 23.47 | 2.61 | 2 | 2.4 | 2.77
2018-06-25 09:00 | 13211.2605 | 444.59 | 17 | 20.34 | 17.76 | 25.1 | 3.8 | 2.5 | 2.63 | 3.4
2018-06-25 10:00 | 14508.9782 | 572.586 | 18.48 | 21.02 | 18.04 | 30.38 | 5.2 | 5.31 | 2 | 5.2
2018-06-25 11:00 | 14153.3082 | 595.458 | 19.35 | 21.59 | 18.01 | 33.95 | 7.31 | 7.48 | 1 | 5.77
2018-06-25 12:00 | 14131.8189 | 517.089 | 19.22 | 26.63 | 19.33 | 37.89 | 7.81 | 7.81 | 1 | 12
2018-06-25 13:00 | 14505.6149 | 544.398 | 33.38 | 28.87 | 19.59 | 44.21 | 19.47 | 9.01 | 1 | 17.12
2018-06-25 14:00 | 13181.3089 | 503.062 | 37.14 | 29.82 | 19.73 | 52.56 | 20.02 | 1.33 | 1.16 | 14.9
2018-06-25 15:00 | 14835.6189 | 458.198 | 54.04 | 31 | 20.15 | 61.79 | 27.37 | 17.66 | 2 | 21.61
2018-06-25 16:00 | 14663.2846 | 185.848 | 91.6 | 31.26 | 21.17 | 61.06 | 28.92 | 12.5 | 2.11 | 20.32
2018-06-25 17:00 | 13245.3332 | 113.456 | 45.86 | 32.32 | 21.59 | 40.46 | 16.79 | 11.38 | 2 | 14.23
2018-06-25 18:00 | 14545.1796 | 51.9001 | 35 | 30.62 | 20.29 | 34.83 | 9.98 | 1.37 | 10 | 4.04
2018-06-25 19:00 | 14541.4281 | 2.3442 | 17.74 | 26.56 | 17.85 | 30.5 | 7.11 | 0.81 | 3.46 | 3.86
2018-06-25 20:00 | 14429.1841 | -0.048233 | 18.09 | 22.49 | 19.16 | 38.4 | 6.73 | 0.81 | 1.22 | 4
2018-06-25 21:00 | 14552.6191 | -0.048233 | 18.77 | 23.4 | 18.63 | 32.67 | 5.27 | 0.81 | 15.96 | 4.99
2018-06-25 22:00 | 14674.9991 | -0.048233 | 18.89 | 21.95 | 16.36 | 29.2 | 3.4 | 0.25 | 11.89 | 3.72
2018-06-25 23:00 | 14526.2441 | -0.048233 | 18.36 | 20.9 | 16.33 | 26.86 | 2.25 | 0.25 | 3.98 | 2.61
2018-06-26 | 14292.0341 | -0.048233 | 16.85 | 20.54 | 15.17 | 22.05 | 2.1 | 0.25 | 10 | 2.61
2018-06-26 01:00 | 14172.8191 | -0.048233 | 17.17 | 18.8 | 12.95 | 21.25 | 1.8 | 0.25 | 4.58 | 2
2018-06-26 02:00 | 12703.3542 | -0.048233 | 16.89 | 17.85 | 11.4 | 20.49 | 1.8 | 0.97 | 4.52 | 1.75
2018-06-26 03:00 | 13981.8641 | -0.048233 | 16.82 | 18.11 | 9.53 | 20.3 | 1.75 | 0.97 | 3.5 | 1.55
2018-06-26 04:00 | 14844.8541 | -0.048233 | 16.11 | 18.57 | 9.64 | 20.31 | 1.8 | 0.99 | 3.11 | 1.75
2018-06-26 05:00 | 13735.2624 | 1.171 | 15.99 | 20.28 | 11.05 | 21.07 | 1.8 | 0.99 | 5 | 2.21
2018-06-26 06:00 | 16981.4335 | 86.1455 | 15.81 | 20.89 | 10.92 | 21.6 | 2 | 1.45 | 2.39 | 2.5
2018-06-26 07:00 | 16594.9011 | 108.317 | 16.35 | 21.06 | 14.06 | 22.34 | 2 | 1.73 | 0.8 | 2
2018-06-26 08:00 | 17266.1018 | 218.844 | 16.97 | 23.59 | 17.33 | 24.15 | 2.11 | 1.25 | 2.8 | 2.11
2018-06-26 09:00 | 20304.5173 | 474.988 | 18.03 | 26.63 | 18.12 | 25.67 | 2.64 | 2.5 | 2.11 | 3.25
2018-06-26 10:00 | 19528.0848 | 650.033 | 19.28 | 27.37 | 18.58 | 27.55 | 5.51 | 5.06 | 1.66 | 5.89
2018-06-26 11:00 | 17641.0592 | 595.536 | 29.15 | 29.15 | 19.39 | 30.54 | 6.48 | 5.8 | 1 | 6.42
2018-06-26 12:00 | 21002.7543 | 606.824 | 32.38 | 32.38 | 19.56 | 34.77 | 7.11 | 6.2 | 1 | 10.01
2018-06-26 13:00 | 21243.5866 | 586.101 | 41.16 | 41.16 | 20.15 | 43.53 | 14.62 | 10.44 | 1 | 12.62
2018-06-26 14:00 | 17883.4859 | 802.722 | 52.76 | 52.76 | 19.89 | 45.58 | 21.98 | 12.73 | 1.65 | 19.98
2018-06-26 15:00 | 16109.8055 | 340.69 | 35.05 | 35.05 | 20.11 | 62.95 | 31.42 | 22 | 2 | 28.65
2018-06-26 16:00 | 17035.0671 | 250.983 | 35.82 | 35.82 | 21.06 | 59.34 | 31.66 | 22 | 2.31 | 27.66
2018-06-26 17:00 | 14729.7443 | 100.994 | 34.23 | 32.24 | 21.57 | 39.77 | 22.46 | 17.91 | 2 | 20.65
2018-06-26 18:00 | 15902.6415 | 54.5938 | 31.65 | 31.65 | 20 | 33.35 | 15.08 | 1.2 | 7.5 | 4.62
2018-06-26 19:00 | 15592.1715 | 2.3095 | 30.39 | 30.39 | 19.35 | 28.18 | 7.3 | 0.99 | 2.61 | 4
2018-06-26 20:00 | 13945.0042 | -0.048233 | 24.1 | 25.14 | 20.05 | 28.7 | 7.63 | 0.97 | 1.47 | 4
2018-06-26 21:00 | 13940.2542 | -0.048233 | 28.84 | 28.84 | 18.28 | 26.51 | 5.08 | 0.97 | 11.3 | 3
2018-06-26 22:00 | 13470.9542 | -0.048233 | 21.75 | 21.75 | 17.21 | 26.32 | 4.13 | 0.25 | 2.8 | 4.72
2018-06-26 23:00 | 13369.3042 | -0.048233 | 21.16 | 21.16 | 15.85 | 24.37 | 2.21 | 0.25 | 11 | 3
2018-06-27 | 13108.0542 | -0.048233 | 18.32 | 21.63 | 16.29 | 21.43 | 2.01 | 0.17 | 10.03 | 2.61
2018-06-27 01:00 | 14370.1041 | -0.048233 | 18.09 | 20.96 | 14.51 | 20.4 | 1.75 | 0.17 | 2.61 | 2.11
2018-06-27 02:00 | 14224.5141 | -0.048233 | 17.57 | 20.66 | 11.8 | 19.59 | 1.61 | 0.97 | 4.11 | 1.5
2018-06-27 03:00 | 12750.8542 | -0.048233 | 16.93 | 20 | 10.86 | 19.45 | 1.61 | 0.97 | 2.61 | 1.5
2018-06-27 04:00 | 14960.9041 | -0.048233 | 16.6 | 19.98 | 11.74 | 19.5 | 1.75 | 0.97 | 2.99 | 1.5
2018-06-27 05:00 | 14463.529 | 1.7674 | 17.02 | 20.63 | 10.73 | 20.03 | 1.8 | 0.97 | 3.51 | 2.11
2018-06-27 06:00 | 17664.1644 | 59.2838 | 18.11 | 21.51 | 11.14 | 21.25 | 2.1 | 1.49 | 2.61 | 2.79
2018-06-27 07:00 | 16557.2761 | 88.7117 | 18.3 | 21.64 | 12 | 22.09 | 2.47 | 1.96 | 2 | 2.47
2018-06-27 08:00 | 17197.1907 | 351.306 | 19.43 | 23.05 | 17.66 | 23.13 | 2.55 | 2 | 2.83 | 2.55
2018-06-27 09:00 | 19878.4471 | 778.13 | 20.42 | 29.22 | 17.07 | 26.09 | 4 | 2.25 | 1.63 | 3
2018-06-27 10:00 | 19891.871 | 913.854 | 33.6 | 33.6 | 16.23 | 30.36 | 5.72 | 3.04 | 2.21 | 5.71
2018-06-27 11:00 | 17793.9845 | 1059.51 | 30.3 | 30.3 | 16.3 | 33.96 | 5.85 | 4.96 | 1 | 5
2018-06-27 12:00 | 20226.154 | 1123.71 | 33.77 | 33.77 | 16.27 | 38.19 | 15.71 | 8.36 | 1 | 5.95
2018-06-27 13:00 | 21077.0432 | 1015.24 | 34.41 | 32.72 | 16.27 | 45.31 | 18.25 | 15.5 | 1 | 15.39
2018-06-27 14:00 | 18602.5491 | 906.748 | 32.67 | 32.67 | 16.28 | 48.99 | 21.93 | 10.95 | 2 | 15.34
2018-06-27 15:00 | 17558.2141 | 801.857 | 30.18 | 29.94 | 16.2 | 53.11 | 42.72 | 16.3 | 2 | 33.93
2018-06-27 16:00 | 14897.4041 | 583.478 | 64.89 | 64.89 | 16.29 | 49.1 | 52.35 | 15.39 | 2.11 | 43.28
2018-06-27 17:00 | 14171.2013 | 264.054 | 31.25 | 29.96 | 16.28 | 34.46 | 22.48 | 11.87 | 1.75 | 13.97
2018-06-27 18:00 | 15347.695 | 50.5782 | 421.5557 | 377.23 | 14.71 | 31.7 | 16.82 | 1 | 2.2 | 4
2018-06-27 19:00 | 13838.4679 | 1.8083 | 27.54 | 24.95 | 13.99 | 29.36 | 7.21 | 0.99 | 1.82 | 3.06
2018-06-27 20:00 | 13793.9542 | -0.048233 | 23.81 | 23.81 | 16.27 | 30.13 | 5.52 | 0.62 | 0.61 | 2.97
2018-06-27 21:00 | 13930.7542 | -0.048233 | 50.05 | 50.05 | 15.01 | 26.25 | 4.22 | 0.62 | 1.4 | 3.22
2018-06-27 22:00 | 13537.4542 | -0.048233 | 315.9057 | 218.81 | 14.26 | 25.79 | 4.64 | 0.12 | 2.61 | 4
2018-06-27 23:00 | 13105.2042 | -0.048233 | 20.5 | 23.68 | 14.14 | 23.97 | 2.86 | 0.12 | 10.89 | 3.17
2018-06-28 | 14334.2341 | -0.048233 | 19.28 | 22.4 | 13.1 | 20.81 | 2.21 | 0.17 | 20 | 2.38
2018-06-28 01:00 | 12721.4042 | -0.048233 | 18.22 | 21.76 | 11.75 | 19.96 | 2 | 0.17 | 2.36 | 2
2018-06-28 02:00 | 14016.6791 | -0.048233 | 17.63 | 20.87 | 11.19 | 19.36 | 1.77 | 0.97 | 3.5 | 1
2018-06-28 03:00 | 13882.6941 | -0.048233 | 17.23 | 19.5 | 10.53 | 19.63 | 1.61 | 0.97 | 2.61 | 1
2018-06-28 04:00 | 13207.8042 | -0.048233 | 17.2 | 19.4 | 10.29 | 19.73 | 1.61 | 0.97 | 3.5 | 1.11
2018-06-28 05:00 | 15818.83 | 1.1517 | 17.52 | 19.92 | 9.02 | 20.32 | 1.9 | 0.97 | 3.44 | 2
2018-06-28 06:00 | 16156.4114 | 53.7488 | 18.07 | 21.07 | 8.74 | 22.49 | 2 | 1.49 | 3.21 | 2.1
2018-06-28 07:00 | 17314.414 | 117.699 | 18.2 | 21.29 | 10.53 | 23.13 | 2 | 1.92 | 2.62 | 2
2018-06-28 08:00 | 17538.3727 | 399.445 | 18.23 | 21.43 | 10.47 | 24.42 | 2.48 | 1.98 | 3 | 2.48
2018-06-28 09:00 | 18224.1834 | 301.351 | 19.61 | 27.37 | 11.53 | 25.14 | 3.11 | 2.5 | 2 | 3.11
2018-06-28 10:00 | 18631.2337 | 926.825 | 20.56 | 22.03 | 14.25 | 27.55 | 5.36 | 3.25 | 2.74 | 5.35
2018-06-28 11:00 | 20225.3734 | 1069.97 | 71.44 | 25 | 14.08 | 31.38 | 6.51 | 5.96 | 1 | 4.75
2018-06-28 12:00 | 20496.1813 | 1123.66 | 66.77 | 28.83 | 13.88 | 35.69 | 15.45 | 9.11 | 1 | 11.15
2018-06-28 13:00 | 18359.5537 | 967.846 | 60.69 | 39.71 | 13.75 | 42.54 | 16.84 | 14.19 | 1 | 13.7
2018-06-28 14:00 | 19970.7523 | 936.623 | 650.5711 | 382.96 | 14.59 | 47.93 | 19.54 | 12.99 | 2 | 14.54
2018-06-28 15:00 | 18926.7179 | 555.017 | 840.0511 | 572.44 | 15.01 | 51.96 | 27.6 | 17.51 | 2.14 | 19.07
2018-06-28 16:00 | 17740.3599 | 367.507 | 262.5457 | 218.22 | 16.29 | 49.11 | 26.46 | 19.12 | 3 | 22.46
2018-06-28 17:00 | 16800.875 | 119 | 54.61 | 54.61 | 16.35 | 34.6 | 30.53 | 27.12 | 2.02 | 27.52
2018-06-28 18:00 | 16303.1257 | 58.1997 | 33.45 | 33.45 | 16.3 | 30.8 | 16.64 | 1.41 | 10.91 | 4.72
2018-06-28 19:00 | 14466.574 | 2.9726 | 35.19 | 35.19 | 16.29 | 29.85 | 8.12 | 0.99 | 2.73 | 3.82
2018-06-28 20:00 | 14399.1042 | -0.048233 | 21.37 | 24.44 | 16.26 | 28.56 | 4.67 | 0.97 | 0.61 | 4.13
2018-06-28 21:00 | 14371.5542 | -0.048233 | 48.96 | 48.96 | 16.25 | 26.24 | 4.43 | 0.97 | 11.83 | 4.43
2018-06-28 22:00 | 13963.0542 | -0.048233 | 79.94 | 79.94 | 12.81 | 26.18 | 3.83 | 0.12 | 12 | 3.75
2018-06-28 23:00 | 15159.2441 | -0.048233 | 1174.4611 | 906.85 | 13.96 | 24.09 | 2.61 | 0.12 | 12 | 2.86
2018-06-29 | 13560.2542 | -0.048233 | 16.98 | 26.97 | 10.44 | 22.06 | 2.06 | 0.25 | 20 | 2.01
2018-06-29 01:00 | 14679.2191 | -0.048233 | 15.59 | 23.74 | 6.01 | 20.82 | 2 | 0.12 | 2.88 | 2
2018-06-29 02:00 | 14547.3441 | -0.048233 | 16.03 | 22.61 | 4.71 | 20.21 | 1.8 | 0.99 | 2.61 | 1.11
2018-06-29 03:00 | 13147.9542 | -0.048233 | 15.95 | 20.87 | 4.68 | 19.95 | 1.8 | 0.99 | 2.91 | 1
2018-06-29 04:00 | 15521.1091 | -0.048233 | 15.7 | 20.33 | 5.27 | 19.94 | 1.8 | 0.99 | 3.41 | 1.21
2018-06-29 05:00 | 16649.13 | 1.1659 | 16.48 | 20.6 | 8.45 | 21.06 | 1.8 | 0.99 | 3.5 | 2.11
2018-06-29 06:00 | 16438.5435 | 52.73 | 17.8 | 20.79 | 15.27 | 25.18 | 2.15 | 1.56 | 2.61 | 2.15
2018-06-29 07:00 | 17311.0795 | 168.189 | 17.37 | 19.55 | 16.4 | 25.05 | 2.11 | 1.61 | 1.4 | 2.11
2018-06-29 08:00 | 18123.4141 | 310.278 | 17.48 | 21.94 | 16.36 | 24.24 | 2.37 | 1.25 | 2.61 | 2.37
2018-06-29 09:00 | 19265.3036 | 782.267 | 18.43 | 18.84 | 16.96 | 25.35 | 3 | 2.61 | 2 | 3.62
2018-06-29 10:00 | 21164.8656 | 603.484 | 20.08 | 20.08 | 18 | 29.3 | 5 | 5.01 | 2.61 | 5.76
2018-06-29 11:00 | 21183.6246 | 711.265 | 29.81 | 22.41 | 18.89 | 30.9 | 5.62 | 6.05 | 1 | 5.62
2018-06-29 12:00 | 18542.0896 | 642.989 | 29.22 | 24.44 | 19.88 | 37.51 | 14.12 | 7.79 | 1 | 10.31
2018-06-29 13:00 | 19304.6793 | 895.715 | 41.23 | 30.61 | 20.12 | 45.95 | 17.7 | 11.09 | 1 | 11.72
2018-06-29 14:00 | 18401.785 | 690.3 | 34.7 | 34.7 | 20.79 | 53.64 | 19.55 | 9.99 | 2.11 | 17.08
2018-06-29 15:00 | 17444.9611 | 594.117 | 39.88 | 39.88 | 20.73 | 63.91 | 35.08 | 25.6 | 2 | 28.01
2018-06-29 16:00 | 18596.1158 | 467.65 | 58.86 | 58.86 | 20.98 | 63.79 | 42.35 | 23.92 | 2.11 | 32.92
2018-06-29 17:00 | 15964.9856 | 246.248 | 47.73 | 47.73 | 20.97 | 43.18 | 21.83 | 12.02 | 2 | 19.51
2018-06-29 18:00 | 14910.895 | 56.6789 | 37 | 37 | 20.24 | 36.4 | 15.83 | 1.1 | 8.11 | 4
2018-06-29 19:00 | 16465.3561 | 2.9726 | 35.16 | 31.43 | 18.66 | 31.55 | 6.04 | 0.99 | 2.61 | 3.09
2018-06-29 20:00 | 14937.7542 | -0.048233 | 29.4 | 29.27 | 18.97 | 30.39 | 6.98 | 1.22 | 1.48 | 3.19
2018-06-29 21:00 | 15154.3542 | -0.048233 | 30.3 | 30.3 | 18.01 | 29.16 | 6.14 | 1.25 | 10.9 | 5.92
2018-06-29 22:00 | 16763.8991 | -0.048233 | 20.39 | 24.69 | 16.35 | 28.32 | 4.44 | 0.12 | 12 | 4.44
2018-06-29 23:00 | 14598.6042 | -0.048233 | 18.48 | 23.67 | 16.39 | 25.07 | 2.51 | 0.12 | 12 | 2.76
2018-06-30 | 15894.5791 | -0.048233 | 18.51 | 24.96 | 14.22 | 24.46 | 2.11 | 0.12 | 15 | 2.61
2018-06-30 01:00 | 15884.0291 | -0.048233 | 17.96 | 23.99 | 8.6 | 23.3 | 2 | 0.17 | 1.84 | 2
2018-06-30 02:00 | 14190.1042 | -0.048233 | 17.67 | 23.7 | 6.67 | 22.67 | 1.8 | 0.7 | 2.01 | 1.6
2018-06-30 03:00 | 13960.2042 | -0.048233 | 16.25 | 20.93 | 5.89 | 22.11 | 1.8 | 0.7 | 3.5 | 1.11
2018-06-30 04:00 | 14799.0542 | -0.048233 | 15.08 | 20.99 | 5.99 | 22.16 | 1.8 | 0.7 | 3.5 | 1.6
2018-06-30 05:00 | 17615.5196 | 1.175 | 16.83 | 20.9 | 9.97 | 22.28 | 2 | 0.7 | 4.01 | 2.45
2018-06-30 06:00 | 17044.7156 | 46.8059 | 18.49 | 20.18 | 16.26 | 25.68 | 2.76 | 1.25 | 1.39 | 3
2018-06-30 07:00 | 19590.0903 | 126.806 | 18.59 | 20.54 | 15.75 | 23.98 | 2.45 | 0.99 | 2.15 | 2.45
2018-06-30 08:00 | 20041.6915 | 168.864 | 19.05 | 20.76 | 16.34 | 26.47 | 3 | 1.68 | 3.46 | 3
2018-06-30 09:00 | 20514.8864 | 408.39 | 20.38 | 20.38 | 18.37 | 27.96 | 3.45 | 2.59 | 3.46 | 3.5
2018-06-30 10:00 | 19138.1794 | 971.452 | 22.02 | 22.02 | 19.91 | 31.61 | 4.26 | 3 | 1.3 | 4.85
2018-06-30 11:00 | 19026.087 | 1108.46 | 27.86 | 24.88 | 20.52 | 35 | 6.04 | 5.87 | 1 | 5.84
2018-06-30 12:00 | 19134.862 | 1095.96 | 31.36 | 26.83 | 20.97 | 47.44 | 15.25 | 5.93 | 1 | 12.07
2018-06-30 13:00 | 18793.394 | 1085.52 | 35.45 | 34.05 | 22.05 | 61.69 | 19.98 | 15 | 1.04 | 15
2018-06-30 14:00 | 19512.9762 | 969.712 | 49.43 | 49.43 | 23.1 | 74.7 | 24.46 | 14.07 | 2.07 | 21.92
2018-06-30 15:00 | 18766.0921 | 815.765 | 45.78 | 40.75 | 32.09 | 82.79 | 32.09 | 21.21 | 1.95 | 28.08
2018-06-30 16:00 | 16329.0037 | 559.425 | 38.14 | 37.37 | 32.42 | 69.44 | 31.43 | 22.57 | 2.11 | 26.77
2018-06-30 17:00 | 15969.9446 | 307.468 | 45.36 | 32.22 | 30.75 | 55.28 | 20.8 | 14.31 | 2 | 17.3
2018-06-30 18:00 | 15422.7311 | 52.4538 | 32.41 | 28.01 | 22.35 | 41.62 | 13.32 | 1.66 | 4 | 4
2018-06-30 19:00 | 15312.8735 | 1.8142 | 31.21 | 25.22 | 19.68 | 37.47 | 9.46 | 0.99 | 3.5 | 4
2018-06-30 20:00 | 15175.2542 | -0.048233 | 30.3 | 24.67 | 19.92 | 33.93 | 6.84 | 0.99 | 1.61 | 3.16
2018-06-30 21:00 | 15117.3042 | -0.048233 | 28.75 | 25.15 | 19.15 | 33.98 | 5.45 | 0.99 | 8.01 | 3
2018-06-30 22:00 | 16257.4991 | -0.048233 | 22.37 | 22.37 | 16.54 | 34.02 | 3.5 | 0.12 | 12.09 | 3.5
2018-06-30 23:00 | 15940.9991 | -0.048233 | 20.99 | 21.3 | 16.13 | 29.85 | 3 | 0.12 | 9 | 3
2018-07-01 | 15361.8041 | -0.048233 | 19.34 | 21.53 | 12.74 | 27.44 | 2.1 | 0.01 | 3.98 | 2.01
2018-07-01 01:00 | 14923.9791 | -0.048233 | 17.91 | 21.96 | 12.53 | 24.65 | 2.01 | 0.01 | 3.11 | 1.75
2018-07-01 02:00 | 14727.7491 | -0.048233 | 17.56 | 20.03 | 12.04 | 23.54 | 1.8 | 0.5 | 2.61 | 1.29
2018-07-01 03:00 | 14587.4341 | -0.048233 | 16.18 | 18.96 | 11.23 | 22.18 | 1.8 | 0.5 | 2.11 | 1
2018-07-01 04:00 | 14677.1091 | -0.048233 | 10.09 | 18.81 | 11.2 | 21.43 | 1.8 | 0.5 | 1 | 1.6
2018-07-01 05:00 | 14573.9114 | 1.1341 | 16.29 | 18.47 | 12.69 | 21.58 | 2 | 0.5 | 1.4 | 2
2018-07-01 06:00 | 14339.5522 | 60.9926 | 17.83 | 18.69 | 13.76 | 22.75 | 2.01 | 0.97 | 2.11 | 2.11
2018-07-01 07:00 | 12963.6421 | 245.939 | 17.67 | 18.24 | 15.9 | 23.25 | 2.5 | 0.97 | 1.97 | 2.11
2018-07-01 08:00 | 14865.9322 | 406.931 | 18.5 | 19.11 | 16.45 | 23.55 | 3.08 | 0.97 | 2.11 | 3.08
2018-07-01 09:00 | 13815.5222 | 808.655 | 18.53 | 19.83 | 16.55 | 26.45 | 3.49 | 0.97 | 2 | 3.49
2018-07-01 10:00 | 13719.3281 | 621.398 | 20.67 | 21.6 | 18.55 | 34.36 | 5 | 0.95 | 1.4 | 5
2018-07-01 11:00 | 15497.508 | 837.581 | 23.44 | 24.93 | 20.01 | 37.22 | 7.56 | 0.95 | 2 | 7.03
2018-07-01 12:00 | 14103.4407 | 878.727 | 30.75 | 25.47 | 20.02 | 41.64 | 14.3 | 5.74 | 1.13 | 13.3
2018-07-01 13:00 | 15914.0314 | 1076.39 | 34.11 | 28.75 | 20.47 | 43.75 | 18.25 | 11.49 | 1.38 | 15.23
2018-07-01 14:00 | 14041.228 | 1032.24 | 32.89 | 26.56 | 20.63 | 57.28 | 22.71 | 11.84 | 1 | 20.17
2018-07-01 15:00 | 15766.802 | 849.836 | 32.33 | 29.21 | 20.64 | 75.36 | 39.59 | 20.81 | 1 | 35
2018-07-01 16:00 | 13836.2303 | 578.453 | 32.85 | 31.65 | 21.91 | 83.49 | 49.3 | 22.38 | 1.4 | 45.66
2018-07-01 17:00 | 13539.5045 | 276.11 | 31.4 | 30.38 | 20.63 | 42.63 | 16.06 | 12.56 | 2 | 15.06
2018-07-01 18:00 | 13431.6312 | 66.5592 | 29.84 | 28.58 | 19.12 | 35 | 13.92 | 1.85 | 3.11 | 5
2018-07-01 19:00 | 14858.4018 | 1.7932 | 22.82 | 25.79 | 18.34 | 31.96 | 7.31 | 0.99 | 3.5 | 4
2018-07-01 20:00 | 14654.9541 | -0.048233 | 22.05 | 22.05 | 18.69 | 30.86 | 6.41 | 0.99 | 3.5 | 4.01
2018-07-01 21:00 | 14681.3291 | -0.048233 | 22.43 | 22.43 | 17.72 | 27.61 | 5.01 | 0.99 | 8.11 | 4.44
2018-07-01 22:00 | 14577.9391 | -0.048233 | 20.6 | 21.08 | 15.47 | 27.49 | 4.09 | 0.01 | 2.61 | 4.09
2018-07-01 23:00 | 14207.6341 | -0.048233 | 19.47 | 21.17 | 13.51 | 25.58 | 2.47 | 0.01 | 8.11 | 2.61
2018-07-02 | 14273.0441 | -0.048233 | 18.05 | 21.54 | 10.92 | 22.44 | 2.01 | 0.12 | 8.61 | 2.61
2018-07-02 01:00 | 14007.1841 | -0.048233 | 17.04 | 20.65 | 10.98 | 20.51 | 1.75 | 0.12 | 3.21 | 2
2018-07-02 02:00 | 13993.4691 | -0.048233 | 3.86 | 20.27 | 5.72 | 19.22 | 1.61 | 0.61 | 3.5 | 1.93
2018-07-02 03:00 | 13864.7591 | -0.048233 | 6.55 | 19.01 | 5.2 | 18.03 | 1.61 | 0.61 | 3.46 | 2
2018-07-02 04:00 | 13775.0841 | -0.048233 | 15.02 | 18.76 | 5.47 | 18.02 | 1.61 | 0.61 | 2.61 | 2.01
2018-07-02 05:00 | 13951.4615 | 1.1341 | 15.24 | 18.35 | 6.67 | 18 | 1.61 | 0.61 | 2.61 | 2.3
2018-07-02 06:00 | 12360.3438 | 55.8882 | 15.38 | 20 | 8.86 | 18.05 | 1.75 | 1.12 | 2.61 | 2.3
2018-07-02 07:00 | 12473.3641 | 257.857 | 16.58 | 20.22 | 13.08 | 18.98 | 1.75 | 1.21 | 2.7 | 2.1
2018-07-02 08:00 | 12762.547 | 479.26 | 18.1 | 21.49 | 14.14 | 20.55 | 2 | 1.19 | 1.92 | 2.8
2018-07-02 09:00 | 13086.2167 | 665.965 | 18.65 | 21.93 | 16.42 | 23.09 | 2.86 | 1.28 | 1.95 | 3.11
2018-07-02 10:00 | 14643.1352 | 861.749 | 20.47 | 22.04 | 16.79 | 26.1 | 3.75 | 0.97 | 1.95 | 3.75
2018-07-02 11:00 | 15168.0093 | 1044.26 | 22.52 | 22.52 | 17.79 | 30.35 | 5.19 | 1.51 | 1 | 5.19
2018-07-02 12:00 | 13806.5495 | 1065.21 | 27.12 | 27.12 | 18.56 | 35.03 | 8.53 | 2.4 | 1.05 | 7.95
2018-07-02 13:00 | 15390.4455 | 1058.1 | 30.63 | 30.63 | 19.15 | 40.76 | 15 | 7.5 | 1.5 | 12.6
2018-07-02 14:00 | 15657.3056 | 998.048 | 33.91 | 31.88 | 19.8 | 49.56 | 19.97 | 12 | 1.89 | 18.49
2018-07-02 15:00 | 13925.7526 | 787.687 | 37.81 | 37.81 | 20.28 | 70.27 | 34.84 | 20.06 | 1 | 28.3
2018-07-02 16:00 | 15406.6777 | 551.486 | 36.63 | 36.63 | 20.67 | 86.41 | 49.85 | 55.9873 | 1.52 | 44.9
2018-07-02 17:00 | 14878.1122 | 277.476 | 34.21 | 34.21 | 19.97 | 45.66 | 19.41 | 12 | 2 | 17.98
2018-07-02 18:00 | 13313.8079 | 65.5346 | 31.18 | 31.18 | 17.59 | 35.47 | 14.84 | 1.41 | 3.5 | 6
2018-07-02 19:00 | 14496.6544 | 2.9047 | 27.68 | 27.68 | 17.55 | 31.55 | 8 | 1.19 | 3.5 | 4
2018-07-02 20:00 | 14344.7841 | -0.048233 | 22.21 | 28.93 | 17.66 | 32.96 | 7.04 | 0.99 | 3.5 | 5.15
2018-07-02 21:00 | 12925.6542 | -0.048233 | 41.8 | 41.8 | 16.49 | 28.7 | 5 | 0.97 | 8.11 | 4.81
2018-07-02 22:00 | 12740.4042 | -0.048233 | 20.85 | 23.48 | 12.52 | 26.3 | 4.25 | 0.12 | 9 | 4.25
2018-07-02 23:00 | 14007.1841 | -0.048233 | 20.15 | 23.82 | 11.29 | 23.92 | 2.45 | 0.12 | 17 | 3
2018-07-03 | 12510.5042 | -0.048233 | 19.28 | 21.81 | 4.15 | 21.69 | 1.97 | 0.12 | 9.03 | 2.42
2018-07-03 01:00 | 12399.3542 | -0.048233 | 17.72 | 20.09 | 3.63 | 19.93 | 1.71 | 0.12 | 3.59 | 2.11
2018-07-03 02:00 | 12354.7042 | -0.048233 | 16.99 | 19 | 3.33 | 19.13 | 1.61 | 0.75 | 3.61 | 1.98
2018-07-03 03:00 | 12461.1042 | -0.048233 | 16.13 | 19.05 | 2.77 | 18 | 1.61 | 0.75 | 3.5 | 2
2018-07-03 04:00 | 12855.3542 | -0.048233 | 15.82 | 19.51 | 2.98 | 19.07 | 1.61 | 0.7 | 2.61 | 2.11
2018-07-03 05:00 | 13025.5774 | 1.1341 | 15.84 | 19.53 | 2.47 | 20.39 | 1.71 | 0.7 | 2.11 | 2.54
2018-07-03 06:00 | 14615.6279 | 56.6757 | 15.75 | 20.45 | 2.21 | 21.02 | 1.75 | 1 | 2.18 | 2.63
2018-07-03 07:00 | 14846.458 | 236.472 | 15.91 | 20.48 | 5.01 | 20.81 | 1.75 | 1 | 3 | 2.1
2018-07-03 08:00 | 15584.8103 | 526.332 | 16.81 | 21.16 | 8.18 | 22 | 1.75 | 1 | 2.61 | 2.42
2018-07-03 09:00 | 14133.3495 | 779.21 | 17.72 | 21.1 | 9.95 | 24.68 | 2.11 | 0.99 | 2.15 | 2.61
2018-07-03 10:00 | 14384.4868 | 996.565 | 53.77 | 53.77 | 7.94 | 28.67 | 3.97 | 1.24 | 2.25 | 4.82
2018-07-03 11:00 | 14278.2435 | 1012.73 | 59.04 | 59.04 | 9.9 | 34.73 | 5.49 | 2.29 | 2 | 5.49
2018-07-03 12:00 | 15134.754 | 1085.32 | 107.24 | 107.24 | 12.51 | 47.98 | 8.43 | 2.49 | 1.33 | 6.49
2018-07-03 13:00 | 15263.8875 | 1107.25 | 244.9157 | 200.59 | 14.5 | 43.85 | 15 | 7.25 | 1 | 12.01
2018-07-03 14:00 | 16621.3668 | 1005.85 | 30.82 | 30.82 | 15.97 | 56.87 | 22.12 | 12.09 | 1 | 19.98
2018-07-03 15:00 | 16080.1697 | 821.867 | 38.02 | 38.02 | 16.43 | 68.47 | 31.63 | 20.19 | 1 | 30.66
2018-07-03 16:00 | 15715.7569 | 570.452 | 41.58 | 41.58 | 16.43 | 67.97 | 42.21 | 20 | 1.98 | 37.21
2018-07-03 17:00 | 15248.7653 | 278.806 | 35.26 | 30.99 | 16.07 | 42.97 | 19.53 | 11.82 | 2 | 15.88
2018-07-03 18:00 | 14909.229 | 65.9706 | 33.19 | 29.75 | 15 | 37.27 | 12.81 | 8.07 | 3.5 | 5
2018-07-03 19:00 | 14865.9395 | 2.9379 | 33.74 | 28.35 | 9.9 | 33.55 | 7.43 | 1.25 | 3.5 | 4
2018-07-03 20:00 | 13151.7542 | -0.048233 | 28.57 | 25.2 | 9.79 | 31.62 | 5.31 | 1.2 | 3.46 | 4.06
2018-07-03 21:00 | 14728.8041 | -0.048233 | 23.46 | 26.54 | 8.35 | 27.73 | 4.26 | 0.97 | 8.15 | 4
2018-07-03 22:00 | 14384.8741 | -0.048233 | 22.61 | 22.61 | 7.84 | 26.32 | 4.63 | 0.12 | 10.53 | 4.63
2018-07-03 23:00 | 14427.0741 | -0.048233 | 20.33 | 27.63 | 4.4 | 23.41 | 3.29 | 0.12 | 11.12 | 3
2018-07-04 | 14307.8591 | -0.048233 | 19.21 | 21.79 | 3.49 | 22.56 | 2.01 | 0.12 | 8.61 | 2.61
2018-07-04 01:00 | 12619.7542 | -0.048233 | 17.28 | 23.01 | 2.31 | 20.84 | 1.75 | 0.17 | 3.09 | 2.3
2018-07-04 02:00 | 13740.2691 | -0.048233 | 18.24 | 21.46 | 2.12 | 20.01 | 1.75 | 0.97 | 3.46 | 1.87
2018-07-04 03:00 | 13623.1641 | -0.048233 | 18.42 | 20.87 | 1.91 | 19.58 | 1.61 | 0.97 | 3.06 | 2.01
2018-07-04 04:00 | 14200.2491 | -0.048233 | 17.98 | 20.95 | 1.44 | 19.49 | 1.61 | 0.97 | 2.11 | 2.08
2018-07-04 05:00 | 14297.5111 | 1.1432 | 18.03 | 20.82 | 1.91 | 19.47 | 1.61 | 0.97 | 2.43 | 2.12
2018-07-04 06:00 | 14128.0427 | 54.5097 | 18.34 | 20.73 | 2.41 | 19.84 | 1.61 | 0.99 | 2.61 | 2.61
2018-07-04 07:00 | 14181.5948 | 252.27 | 17.74 | 19.32 | 3.42 | 20.12 | 1.61 | 1.19 | 2.99 | 2.1
2018-07-04 08:00 | 14774.4289 | 545.198 | 17.96 | 19.58 | 4.27 | 21.79 | 1.75 | 1.25 | 1.91 | 2.61
2018-07-04 09:00 | 15088.2713 | 749.679 | 18.51 | 19.73 | 5.11 | 26.82 | 2.8 | 0.99 | 1.4 | 3.1
2018-07-04 10:00 | 15528.1568 | 962.632 | 19.37 | 21.31 | 7.8 | 33.27 | 3.8 | 1.22 | 1.4 | 3.8
2018-07-04 11:00 | 14108.5545 | 1026.11 | 22.23 | 22.95 | 9.74 | 36.23 | 6.56 | 2.18 | 2.11 | 5.73
2018-07-04 12:00 | 14190.0645 | 1068.91 | 29.96 | 24.29 | 9.73 | 40.27 | 6.57 | 1.83 | 1 | 5.65
2018-07-04 13:00 | 15862.8534 | 1057.88 | 34.52 | 29.07 | 8.77 | 48.3 | 18.25 | 8.76 | 1.01 | 13.67
2018-07-04 14:00 | 15834.4633 | 984.97 | 38.71 | 32.64 | 8.33 | 59.74 | 20.96 | 10 | 1.4 | 15.96
2018-07-04 15:00 | 13855.3225 | 827.55 | 53.88 | 32.15 | 9.79 | 72.76 | 41.39 | 20 | 1.4 | 34.46
2018-07-04 16:00 | 13556.0411 | 443.517 | 33.6 | 33.6 | 10 | 73.19 | 44.19 | 20.37 | 2 | 38.69
2018-07-04 17:00 | 14768.6633 | 239.733 | 34.93 | 34.93 | 7.71 | 45.59 | 19.6 | 14.62 | 2 | 17.05
2018-07-04 18:00 | 13016.5513 | 69.6329 | 29.61 | 29.61 | 7.78 | 37.38 | 15.22 | 6.63 | 2.31 | 5
2018-07-04 19:00 | 12934.2021 | 2.9496 | 26.69 | 26.29 | 7.06 | 33.19 | 6.58 | 2.32 | 2.31 | 4.13
2018-07-04 20:00 | 12839.2042 | -0.048233 | 22.29 | 22.29 | 7.77 | 31.79 | 5.55 | 1.61 | 2.61 | 4
2018-07-04 21:00 | 12844.9042 | -0.048233 | 21.84 | 23.33 | 6.77 | 29.14 | 5 | 1.31 | 8.11 | 4
2018-07-04 22:00 | 12768.9042 | -0.048233 | 20.23 | 22.08 | 4.31 | 25.95 | 3 | 0.12 | 9 | 3.01
2018-07-04 23:00 | 12495.3042 | -0.048233 | 19.3 | 26.72 | 4.28 | 24.68 | 2.16 | 0.12 | 11.14 | 2.61
2018-07-05 | 12540.9042 | -0.048233 | 17.19 | 22.19 | 3.48 | 21.32 | 2.11 | 0.17 | 4 | 2.73
2018-07-05 01:00 | 12453.5042 | -0.048233 | 14.65 | 20.23 | 2.23 | 20.34 | 2 | 0.17 | 3.11 | 2.3
2018-07-05 02:00 | 12215.0542 | -0.048233 | 15.24 | 20.27 | 1.85 | 19.77 | 1.61 | 0.97 | 2.99 | 2
2018-07-05 03:00 | 12268.2542 | -0.048233 | 14.11 | 21.3 | 1.16 | 19.12 | 1.61 | 0.97 | 2.61 | 1.8
2018-07-05 04:00 | 12736.6042 | -0.048233 | 15.16 | 21.28 | 1.04 | 19.73 | 1.61 | 0.7 | 1.5 | 2
2018-07-05 05:00 | 13925.2533 | 1.1613 | 15.56 | 21.94 | 0.66 | 20.62 | 1.61 | 0.7 | 1.11 | 2.5
2018-07-05 06:00 | 17099.5843 | 37.1368 | 16.93 | 23.47 | 0.56 | 21.08 | 2.1 | 1 | 1.88 | 2.61
2018-07-05 07:00 | 16556.3929 | 242.782 | 16.33 | 24.99 | 2.05 | 22.39 | 2.11 | 0.99 | 2.61 | 2.11
2018-07-05 08:00 | 19302.9225 | 534.609 | 17.7 | 25.81 | 3.42 | 24.12 | 2.84 | 0.99 | 2 | 2.84
2018-07-05 09:00 | 17994.367 | 699.439 | 18.42 | 25.85 | 4.13 | 27.74 | 3 | 0.99 | 1.5 | 3
2018-07-05 10:00 | 18272.1366 | 933.828 | 18.92 | 29.5 | 5.15 | 31.47 | 3.28 | 0.99 | 1.9 | 3.28
2018-07-05 11:00 | 18397.8235 | 1017.13 | 33.97 | 33.97 | 9.89 | 37.63 | 6.86 | 2 | 2.11 | 5.43
2018-07-05 12:00 | 18954.5235 | 1099.13 | 31.68 | 31.68 | 12.28 | 47.03 | 6.61 | 3.09 | 1.1 | 11.29
2018-07-05 13:00 | 21084.2488 | 1065.07 | 38.4 | 38.4 | 13.65 | 55.63 | 24.73 | 13.02 | 1 | 16.81
2018-07-05 14:00 | 19820.8125 | 1008.5 | 39.84 | 39.84 | 14.66 | 71.57 | 29.13 | 13.45 | 1 | 22.66
2018-07-05 15:00 | 16932.8465 | 760.049 | 57.37 | 57.37 | 14.79 | 92.22 | 52.35 | 20 | 1.5 | 43.07
2018-07-05 16:00 | 16199.6166 | 601.228 | 314.6857 | 270.36 | 22.96 | 89.46 | 88.9641 | 23.69 | 2 | 78.8062
2018-07-05 17:00 | 15406.7912 | 259.675 | 88.1 | 38.54 | 22.97 | 52.76 | 25.92 | 14.6 | 2 | 18.73
2018-07-05 18:00 | 15031.4306 | 59.5585 | 84.07 | 31.78 | 16.36 | 41.43 | 16.31 | 9.17 | 2.61 | 11.27
2018-07-05 19:00 | 14812.931 | 1.5589 | 31.08 | 31.08 | 16.33 | 35.85 | 6.35 | 1.47 | 2.31 | 4
2018-07-05 20:00 | 14752.5042 | -0.048233 | 36.48 | 28.67 | 16.39 | 33.89 | 6.16 | 1.35 | 2.61 | 4
2018-07-05 21:00 | 14762.9542 | -0.048233 | 48.18 | 27.73 | 15.32 | 31 | 5.46 | 1.43 | 7.73 | 4.46
2018-07-05 22:00 | 14382.0042 | -0.048233 | 22.63 | 24.15 | 10.77 | 26.24 | 4.9 | 0.17 | 9 | 4.9
2018-07-05 23:00 | 13940.2542 | -0.048233 | 78.04 | 24.43 | 8.65 | 23.88 | 2.15 | 0.17 | 12 | 2.44
2018-07-06 | 15203.5541 | -0.048233 | 17.6 | 22.29 | 4.51 | 22.02 | 2.01 | 0.3 | 3.98 | 1.5
2018-07-06 01:00 | 15022.0941 | -0.048233 | 16.67 | 21.34 | 4.27 | 20.53 | 2 | 0.25 | 3.5 | 1.5
2018-07-06 02:00 | 14944.0241 | -0.048233 | 16.24 | 20.04 | 4.19 | 19.9 | 1.85 | 0.97 | 3.05 | 1.2
2018-07-06 03:00 | 14807.9291 | -0.048233 | 16.26 | 19.86 | 3.22 | 19.38 | 1.85 | 0.91 | 2.61 | 1.2
2018-07-06 04:00 | 15454.6441 | -0.048233 | 16.59 | 19.65 | 3.18 | 19.53 | 1.81 | 0.7 | 0.71 | 1.5
2018-07-06 05:00 | 14804.0033 | 1.1613 | 15.42 | 20.17 | 4.18 | 20.08 | 2 | 0.7 | 2.11 | 1.5
2018-07-06 06:00 | 18465.2994 | 41.6535 | 17.28 | 20.85 | 8.04 | 23.31 | 2.01 | 0.99 | 1.22 | 2.44
2018-07-06 07:00 | 19393.471 | 241.437 | 17.83 | 20.97 | 10.82 | 22.61 | 2.12 | 0.99 | 1.29 | 2.12
2018-07-06 08:00 | 19162.1095 | 402.137 | 17.88 | 21.58 | 14.22 | 25.34 | 2.4 | 0.99 | 1.93 | 3
2018-07-06 09:00 | 20472.3193 | 802.042 | 18.42 | 22.79 | 16.36 | 29.02 | 3.11 | 0.99 | 2 | 3.5
2018-07-06 10:00 | 21006.3002 | 666.185 | 20.66 | 29.26 | 19.32 | 33.21 | 3.9 | 0.99 | 2 | 3.9
2018-07-06 11:00 | 19350.9756 | 996.448 | 21.54 | 30.96 | 20.2 | 36.85 | 6.16 | 1.99 | 1 | 6.16
2018-07-06 12:00 | 21132.3358 | 1158.65 | 34.99 | 34.99 | 29.16 | 44.56 | 7.43 | 5.02 | 1 | 12.5
2018-07-06 13:00 | 18469.4088 | 795.483 | 36.82 | 36.82 | 30.59 | 54.96 | 18.28 | 14.99 | 1 | 14.49
2018-07-06 14:00 | 17496.2469 | 693.102 | 129.17 | 39.65 | 32.61 | 74.54 | 25.99 | 16.01 | 2 | 23.73
2018-07-06 15:00 | 18711.7079 | 692.216 | 53.6 | 53.6 | 36.16 | 88.17 | 42 | 23 | 1.92 | 38.15
2018-07-06 16:00 | 17902.5767 | 574.267 | 42.7 | 42.7 | 38.05 | 93.28 | 50.39 | 53.3073 | 2 | 45.59
2018-07-06 17:00 | 16909.6539 | 191.108 | 35.1 | 35.1 | 36.59 | 55.33 | 23.26 | 15.54 | 2.11 | 17.49
2018-07-06 18:00 | 14610.3224 | 71.2867 | 32.83 | 32.83 | 32.34 | 40.47 | 12.69 | 9.28 | 2.11 | 6.66
2018-07-06 19:00 | 14765.6538 | 1.7934 | 30.58 | 30.58 | 28.5 | 33.99 | 7.58 | 1.46 | 2.37 | 4
2018-07-06 20:00 | 14876.0042 | -0.048233 | 29.93 | 29.93 | 20.05 | 33.1 | 6.37 | 1.49 | 2.9 | 4.61
2018-07-06 21:00 | 16421.0241 | -0.048233 | 29.87 | 29.87 | 18.88 | 33.24 | 4.42 | 1.39 | 9.35 | 4.22
2018-07-06 22:00 | 15862.9291 | -0.048233 | 22.35 | 25.88 | 14.66 | 26.06 | 2.51 | 0.25 | 11.64 | 3.42
2018-07-06 23:00 | 15471.5241 | -0.048233 | 20.18 | 22.73 | 11.84 | 24.82 | 2.11 | 0.25 | 3 | 2
2018-07-07 | 13640.0542 | -0.048233 | 18.51 | 21.62 | 15.22 | 21.13 | 2 | 0.25 | 3.98 | 1.5
2018-07-07 01:00 | 12261.6042 | -0.048233 | 18.17 | 20.94 | 14.68 | 20.47 | 2 | 0.25 | 3.11 | 1.5
2018-07-07 02:00 | 12946.9091 | -0.048233 | 16.11 | 20.52 | 13.03 | 19.82 | 2 | 0.7 | 3.29 | 1.2
2018-07-07 03:00 | 12453.5042 | -0.048233 | 15.54 | 19.91 | 10.87 | 19.17 | 1.85 | 0.7 | 2.61 | 1.2
2018-07-07 04:00 | 14088.4542 | -0.048233 | 15.37 | 19.61 | 11.99 | 19.1 | 2 | 0.7 | 2.16 | 1.5
2018-07-07 05:00 | 14505.5042 | -0.048233 | 15.91 | 20.12 | 13.57 | 19.72 | 2 | 0.7 | 2.11 | 1.5
2018-07-07 06:00 | 16546.6174 | 48.492 | 16.65 | 20.4 | 15.18 | 22.03 | 1.75 | 0.99 | 1.24 | 2.31
2018-07-07 07:00 | 17252.8978 | 254.945 | 16.71 | 20.79 | 16.42 | 22.36 | 2 | 1.26 | 1.04 | 2.11
2018-07-07 08:00 | 19130.0723 | 467.77 | 17.87 | 21.37 | 17.81 | 24.5 | 2.01 | 1.22 | 0.71 | 2.61
2018-07-07 09:00 | 20234.5867 | 609.703 | 18.52 | 26.81 | 18.72 | 29.59 | 3 | 1.24 | 1.4 | 3.4
2018-07-07 10:00 | 19042.844 | 855.099 | 19.61 | 29.83 | 19.55 | 36.82 | 4.67 | 1 | 2 | 4.67
2018-07-07 11:00 | 21074.4722 | 977.803 | 31.51 | 31.51 | 23.69 | 41.76 | 6.66 | 2 | 1 | 6.66
2018-07-07 12:00 | 20720.1462 | 974.949 | 41.25 | 41.25 | 31.04 | 46.96 | 12.45 | 0.99 | 1.09 | 13.39
2018-07-07 13:00 | 21011.3905 | 1008.01 | 47.59 | 47.59 | 32.47 | 54.31 | 20.2 | 10.05 | 1.15 | 15.47
2018-07-07 14:00 | 19274.5863 | 710.75 | 35.25 | 35.25 | 34.7 | 70.13 | 30.02 | 18.28 | 1 | 25.02
2018-07-07 15:00 | 18493.7523 | 681.623 | 33.74 | 33.74 | 34.04 | 93.4 | 52.72 | 56.3373 | 1 | 45.5
2018-07-07 16:00 | 17431.4612 | 392.712 | 35.56 | 32.6 | 35.69 | 81.25 | 46.69 | 29 | 1.4 | 39.69
2018-07-07 17:00 | 17149.8584 | 304.79 | 31.56 | 31.56 | 34.91 | 47.12 | 17.34 | 12.96 | 2 | 15.06
2018-07-07 18:00 | 16336.8411 | 85.1574 | 31.5 | 31.5 | 33.81 | 44.62 | 12.88 | 8.12 | 2 | 4.52
2018-07-07 19:00 | 16128.1545 | 2.3502 | 30.27 | 30.27 | 31.51 | 39.75 | 7 | 1.08 | 2.31 | 4.26
2018-07-07 20:00 | 14434.2542 | -0.048233 | 28.93 | 28.93 | 28.46 | 37.96 | 6.19 | 1 | 2.61 | 4.19
2018-07-07 21:00 | 14227.1542 | -0.048233 | 29.13 | 29.13 | 19.17 | 35.07 | 5.14 | 1 | 3.11 | 4.94
2018-07-07 22:00 | 15068.5141 | -0.048233 | 20.37 | 27.66 | 17.99 | 31.46 | 3.15 | 0.25 | 3.4 | 3.37
2018-07-07 23:00 | 13030.1542 | -0.048233 | 18.98 | 21.99 | 17.14 | 28.6 | 2 | 0.25 | 12 | 2.17
2018-07-08 | 14156.9941 | -0.048233 | 17.58 | 24.22 | 18.08 | 25.42 | 2 | 0.25 | 3.7 | 2.01
2018-07-08 01:00 | 12616.9042 | -0.048233 | 16.92 | 21.11 | 16.95 | 22.64 | 1.75 | 0.25 | 2.43 | 1.42
2018-07-08 02:00 | 13884.8041 | -0.048233 | 17.02 | 20.85 | 15 | 21.19 | 1.75 | 0.7 | 2.61 | 1.5
2018-07-08 03:00 | 13456.4741 | -0.048233 | 16.8 | 19.64 | 14.92 | 20.31 | 1.75 | 0.7 | 2.11 | 1.44
2018-07-08 04:00 | 13632.6591 | -0.048233 | 17.01 | 19.47 | 14.91 | 20.43 | 1.75 | 0.7 | 1.23 | 1.5
2018-07-08 05:00 | 14514.6391 | -0.048233 | 17.59 | 19.48 | 11.64 | 20.44 | 1.75 | 0.7 | 1.49 | 1.8
2018-07-08 06:00 | 13329.2076 | 49.7448 | 18.8 | 19.56 | 12.51 | 22.36 | 1.75 | 1 | 2 | 2.1
2018-07-08 07:00 | 14791.7182 | 157.586 | 18.79 | 19.59 | 14.4 | 23.55 | 2.01 | 1 | 1 | 2.1
2018-07-08 08:00 | 13650.948 | 397.419 | 19.5 | 21.09 | 17.24 | 27.34 | 2.11 | 1 | 2 | 2.27
2018-07-08 09:00 | 15320.8461 | 274.129 | 19.92 | 22.33 | 18.55 | 32 | 3.49 | 0.99 | 2.59 | 3.49
2018-07-08 10:00 | 14117.0465 | 435.049 | 32.1 | 29.08 | 19.38 | 39.59 | 6.05 | 1.42 | 2 | 5.63
2018-07-08 11:00 | 16031.5774 | 543.808 | 31.61 | 31.61 | 23.62 | 42.52 | 5.95 | 2.1 | 1 | 13.6
2018-07-08 12:00 | 14878.7575 | 1067.85 | 32.57 | 32.57 | 24.63 | 45.54 | 14.87 | 4.82 | 1.1 | 15.35
2018-07-08 13:00 | 16491.2641 | 1058.53 | 52.11 | 52.11 | 30.52 | 56.51 | 23.55 | 9.5 | 1 | 19.86
2018-07-08 14:00 | 16286.2914 | 920.243 | 46.79 | 46.79 | 32.44 | 66.89 | 33.38 | 19.65 | 1.15 | 28.38
2018-07-08 15:00 | 14598.8343 | 804.194 | 53.66 | 53.66 | 31.67 | 82.18 | 49.17 | 57.0673 | 1.87 | 44.17
2018-07-08 16:00 | 15965.8889 | 577.544 | 35.44 | 35.44 | 31.72 | 75.04 | 44.44 | 29.95 | 2 | 38.63
2018-07-08 17:00 | 13758.4624 | 283.592 | 33.09 | 33.09 | 29.85 | 44.14 | 16.89 | 10.43 | 2.28 | 13.79
2018-07-08 18:00 | 14972.6178 | 61.0548 | 31.72 | 31.72 | 23.76 | 37.7 | 13.03 | 7.36 | 2.31 | 5.97
2018-07-08 19:00 | 13315.8275 | 2.6605 | 32.09 | 32.09 | 21.37 | 33.69 | 7.34 | 0.99 | 2.21 | 6.19
2018-07-08 20:00 | 14668.6691 | -0.048233 | 29.33 | 29.33 | 20.78 | 32.14 | 5.29 | 0.97 | 2.61 | 5.23
2018-07-08 21:00 | 13338.9042 | -0.048233 | 29.17 | 29.17 | 19.2 | 29.41 | 3.75 | 0.97 | 15.85 | 3.75
2018-07-08 22:00 | 14462.9441 | -0.048233 | 21.7 | 27.84 | 18.61 | 28.11 | 4.25 | 0.25 | 9 | 4.2
2018-07-08 23:00 | 12813.5542 | -0.048233 | 20.7 | 22.41 | 17.17 | 24.85 | 2.31 | 0.12 | 15 | 2.89
2018-07-09 | 12713.8042 | -0.048233 | 19.36 | 21.24 | 16.49 | 23.2 | 2.76 | 0.12 | 9.11 | 2.11
2018-07-09 01:00 | 13960.7641 | -0.048233 | 18.3 | 21.1 | 15.37 | 21.18 | 2 | 0.17 | 3.91 | 1.42
2018-07-09 02:00 | 13919.6191 | -0.048233 | 17.56 | 20.73 | 13.38 | 20.19 | 1.75 | 0.61 | 3.5 | 1.11
2018-07-09 03:00 | 12171.3542 | -0.048233 | 17.45 | 19.94 | 12.07 | 19.32 | 1.61 | 0.61 | 2.62 | 1.44
2018-07-09 04:00 | 12039.3042 | -0.048233 | 17.4 | 19.45 | 10.25 | 18.57 | 1.75 | 0.61 | 1 | 1.11
2018-07-09 05:00 | 13249.6941 | -0.048233 | 17.06 | 18.91 | 9.93 | 18.57 | 1.75 | 0.61 | 2.89 | 1.8
2018-07-09 06:00 | 11665.4046 | 46.3733 | 17.79 | 19.03 | 10.24 | 19.99 | 1.37 | 1.16 | 2.61 | 2.61
2018-07-09 07:00 | 13171.2752 | 214.621 | 17.04 | 18.67 | 12.94 | 20.31 | 1.61 | 1.2 | 3.01 | 2.1
2018-07-09 08:00 | 13400.0508 | 221.47 | 18.15 | 19.7 | 14.65 | 21.47 | 2 | 0.99 | 3.5 | 3
2018-07-09 09:00 | 12516.591 | 501.359 | 19.39 | 20.97 | 17.16 | 25.21 | 3.32 | 1.24 | 2.86 | 3.32
2018-07-09 10:00 | 14152.2395 | 631.445 | 20.19 | 21.33 | 17.22 | 27.93 | 4.07 | 0.99 | 2.61 | 4.07
2018-07-09 11:00 | 13283.0615 | 1110.17 | 21.71 | 25.95 | 17.83 | 33.29 | 5.84 | 0.99 | 2 | 5.2
2018-07-09 12:00 | 13602.0335 | 1124.93 | 30.38 | 29.78 | 18.18 | 40.22 | 5.81 | 0.99 | 1.15 | 12.65
2018-07-09 13:00 | 15300.6755 | 1046.01 | 35.3 | 31.24 | 18.55 | 43.01 | 15.19 | 7.13 | 1 | 14.13
2018-07-09 14:00 | 13594.8021 | 869.318 | 33 | 31.67 | 18.99 | 55.77 | 24.54 | 11.51 | 1 | 23.54
2018-07-09 15:00 | 13609.6582 | 728.956 | 32.79 | 30.95 | 19.18 | 76.55 | 43.32 | 25 | 1.76 | 42.32
2018-07-09 16:00 | 13365.1994 | 390.631 | 32.23 | 30.89 | 19.75 | 65.14 | 36.21 | 22.92 | 2 | 34.21
2018-07-09 17:00 | 13419.0844 | 281.352 | 30.57 | 29.55 | 20.19 | 41.81 | 17.34 | 11.02 | 2.11 | 13.12
2018-07-09 18:00 | 13169.2114 | 88.3278 | 28.84 | 28.84 | 19.18 | 38.37 | 12.9 | 0.99 | 2.31 | 6.85
2018-07-09 19:00 | 14561.4442 | 2.3168 | 22.83 | 24.98 | 18.8 | 34.5 | 5.77 | 1.21 | 2.61 | 5.52
2018-07-09 20:00 | 13102.3542 | -0.048233 | 21.66 | 21.66 | 19.2 | 32.03 | 4.37 | 0.99 | 2 | 4.11
2018-07-09 21:00 | 13204.9542 | -0.048233 | 20.75 | 21.49 | 17.07 | 30.67 | 3.75 | 0.97 | 9.96 | 3.75
2018-07-09 22:00 | 13010.2042 | -0.048233 | 20.2 | 21.06 | 16.92 | 27.29 | 3.79 | 0.25 | 10.53 | 3.79
2018-07-09 23:00 | 14369.0491 | -0.048233 | 18.76 | 20.89 | 15.51 | 23.69 | 2.1 | 0.12 | 15 | 3
2018-07-10 | 12767.0042 | -0.048233 | 16.85 | 19.94 | 10.19 | 20.4 | 2 | 0.12 | 10 | 2.11
2018-07-10 01:00 | 12505.7542 | -0.048233 | 16.06 | 18.29 | 9.2 | 19.23 | 2 | 0.12 | 4.68 | 1.25
2018-07-10 02:00 | 12390.8042 | -0.048233 | 15.55 | 16.99 | 8.95 | 18.64 | 2 | 0.7 | 3.5 | 1.25
2018-07-10 03:00 | 13589.4041 | -0.048233 | 15.12 | 16.65 | 8.38 | 18.21 | 1.99 | 0.7 | 2.61 | 1.25
2018-07-10 04:00 | 14313.1341 | -0.048233 | 14.97 | 16.3 | 7.26 | 17.94 | 2 | 0.7 | 1 | 1.5
2018-07-10 05:00 | 15265.7991 | -0.048233 | 14.9 | 16.88 | 7.25 | 18.91 | 2 | 0.7 | 2.61 | 1.8
2018-07-10 06:00 | 16882.1648 | 55.0519 | 15.04 | 17.75 | 6.26 | 21.06 | 1.61 | 1 | 2.15 | 2.31
2018-07-10 07:00 | 17136.6624 | 208.592 | 14.92 | 18.04 | 3.39 | 21.16 | 1.61 | 1 | 2.99 | 2.09
2018-07-10 08:00 | 17558.2059 | 352.322 | 16.53 | 19.28 | 10.24 | 22.78 | 2.1 | 1.12 | 0.85 | 2.23
2018-07-10 09:00 | 21440.4485 | 653.7 | 16.49 | 20.39 | 13.16 | 24.55 | 3.01 | 0.99 | 2.11 | 3.01
2018-07-10 10:00 | 22264.202 | 881.509 | 17.42 | 20.96 | 15.46 | 29.5 | 3.62 | 1.38 | 2.11 | 3.62
2018-07-10 11:00 | 19135.1859 | 912.301 | 19.2 | 21.15 | 15.02 | 32.78 | 6.85 | 2 | 2 | 5.52
2018-07-10 12:00 | 20769.1204 | 962.232 | 20.34 | 22.24 | 15.43 | 39.55 | 7.16 | 3.75 | 1 | 11.55
2018-07-10 13:00 | 18874.5145 | 884.91 | 22.63 | 27.9 | 15.72 | 47.04 | 18.27 | 7.59 | 1.02 | 17.27
2018-07-10 14:00 | 17973.1336 | 897.088 | 29.36 | 29.36 | 16.03 | 57.55 | 26.01 | 13.58 | 1.78 | 22.67
2018-07-10 15:00 | 16692.9848 | 783.563 | 30.56 | 30.56 | 16.04 | 74.78 | 42.23 | 26.77 | 2 | 36.67
2018-07-10 16:00 | 17789.1885 | 471.79 | 31.04 | 31.04 | 17.97 | 69.17 | 39.55 | 24.43 | 2 | 35
2018-07-10 17:00 | 17045.9789 | 257.326 | 31.4 | 31.4 | 18.77 | 40.52 | 16.51 | 10.42 | 2.67 | 12.53
2018-07-10 18:00 | 16234.3784 | 65.0364 | 29.19 | 29.19 | 18.78 | 36.98 | 8.42 | 0.97 | 2 | 6.39
2018-07-10 19:00 | 14647.9594 | 2.9046 | 29.74 | 25.73 | 17.87 | 32.32 | 4.94 | 0.97 | 2 | 4.75
2018-07-10 20:00 | 16181.5391 | -0.048233 | 22.46 | 25.6 | 17.98 | 31.81 | 4 | 0.97 | 2.03 | 4
2018-07-10 21:00 | 14470.3542 | -0.048233 | 21.1 | 23.32 | 16.83 | 28.54 | 3.32 | 0.97 | 3.11 | 3.32
2018-07-10 22:00 | 14211.0042 | -0.048233 | 19.13 | 21.09 | 15.25 | 24.8 | 3.75 | 0.12 | 10.9 | 3.75
2018-07-10 23:00 | 13788.2542 | -0.048233 | 18.46 | 20.5 | 15 | 22.77 | 2.25 | 0.12 | 15 | 2.61
2018-07-11 | 13544.1042 | -0.048233 | 16.3 | 19.74 | 9.49 | 20.1 | 2 | 0.12 | 10.53 | 2.11
2018-07-11 01:00 | 14756.2341 | -0.048233 | 14.82 | 19.58 | 9.01 | 18.84 | 2 | 0.12 | 3.71 | 1.25
2018-07-11 02:00 | 13340.8042 | -0.048233 | 14.67 | 18.51 | 7.07 | 17.89 | 2 | 0.7 | 3.08 | 1.25
2018-07-11 03:00 | 13252.4542 | -0.048233 | 0.64 | 17.94 | 6.84 | 17.4 | 2 | 0.7 | 3.5 | 1.25
2018-07-11 04:00 | 13961.1542 | -0.048233 | 0 | 17.45 | 6.38 | 17.34 | 2 | 0.7 | 2.61 | 1.25
2018-07-11 05:00 | 16662.8115 | 1.1341 | 3.53 | 17.82 | 6.79 | 18.55 | 2 | 0.7 | 3.06 | 2
2018-07-11 06:00 | 18457.8474 | 46.59 | 8.19 | 18.43 | 11.29 | 19.78 | 1.88 | 0.99 | 1 | 2.43
2018-07-11 07:00 | 19365.9218 | 198.324 | 12.58 | 18.67 | 14.15 | 20.39 | 2 | 1 | 2.61 | 2
2018-07-11 08:00 | 20361.7701 | 419.256 | 17.11 | 20.32 | 16.98 | 21.71 | 2.23 | 0.99 | 2.19 | 2.23
2018-07-11 09:00 | 19331.6574 | 813.113 | 17.62 | 20.82 | 18.02 | 25.76 | 2.6 | 1 | 2.14 | 3
2018-07-11 10:00 | 19337.7621 | 839.539 | 18.81 | 21.3 | 19.61 | 28.19 | 4 | 0.99 | 2 | 3.75
2018-07-11 11:00 | 20910.6634 | 757.534 | 20.87 | 21.88 | 21.11 | 34.63 | 6.03 | 2 | 1 | 5.03
2018-07-11 12:00 | 19527.8941 | 840.678 | 24.24 | 24.99 | 21.54 | 37.56 | 7.27 | 0.99 | 1 | 6.27
2018-07-11 13:00 | 19738.378 | 1001.24 | 31.69 | 31.69 | 22.08 | 43.33 | 13.1 | 7.39 | 1 | 12.1
2018-07-11 14:00 | 18045.7069 | 678.481 | 36.64 | 36.64 | 23.52 | 49.74 | 17.36 | 7.04 | 1 | 15.75
2018-07-11 15:00 | 17000.8551 | 698.637 | 36 | 31.13 | 24.76 | 52.91 | 22.41 | 15 | 1.11 | 19.59
2018-07-11 16:00 | 15815.9553 | 510.374 | 36.99 | 30.85 | 24.62 | 51.74 | 26.17 | 15 | 1.26 | 22.6
2018-07-11 17:00 | 15128.0042 | 259.215 | 32.58 | 30.75 | 24.74 | 41.41 | 17.41 | 11 | 2.11 | 16.14
2018-07-11 18:00 | 14634.0988 | 59.3145 | 31.96 | 30.56 | 22.49 | 35.11 | 7.24 | 0.99 | 3.5 | 5
2018-07-11 19:00 | 16243.9291 | 2.0892 | 30.1 | 30.1 | 21.56 | 31.65 | 6.71 | 0.99 | 3.26 | 4.5
2018-07-11 20:00 | 14674.6042 | -0.048233 | 20.98 | 28.44 | 21.56 | 31.24 | 5.17 | 0.99 | 2.61 | 4
2018-07-11 21:00 | 14421.9042 | -0.048233 | 20.64 | 29.17 | 20.85 | 27.5 | 3.31 | 0.97 | 4 | 3.31
2018-07-11 22:00 | 15546.4291 | -0.048233 | 18.78 | 26.31 | 18.54 | 25.21 | 3.11 | 0.12 | 9 | 3.31
2018-07-11 23:00 | 13833.8542 | -0.048233 | 18.78 | 22.23 | 15.92 | 23.54 | 2.01 | 0.12 | 3.01 | 2.32
2018-07-12 | 15106.4941 | -0.048233 | 17.21 | 21.5 | 15.75 | 20.88 | 2 | 0.12 | 8.22 | 2.11
2018-07-12 01:00 | 13212.5542 | -0.048233 | 17.08 | 21.11 | 15.82 | 20.06 | 2 | 0.12 | 4.64 | 1.25
2018-07-12 02:00 | 13207.8042 | -0.048233 | 15.75 | 21.01 | 11.51 | 19.42 | 2 | 0.75 | 3.5 | 1.11
2018-07-12 03:00 | 14761.5091 | -0.048233 | 14.84 | 20.48 | 9.5 | 18.84 | 1.95 | 0.75 | 3.5 | 1.25
2018-07-12 04:00 | 14053.3042 | -0.048233 | 13.68 | 20.46 | 9.52 | 19.21 | 2 | 0.75 | 2.61 | 1.25
2018-07-12 05:00 | 16779.7241 | -0.048233 | 13.02 | 20.66 | 11.24 | 20.09 | 2 | 0.75 | 23.16 | 2.5
2018-07-12 06:00 | 18852.2101 | 45.3935 | 16.17 | 21.28 | 11.2 | 21.69 | 1.92 | 0.99 | 2.31 | 2.31
2018-07-12 07:00 | 20078.5047 | 229.758 | 14.4 | 21.06 | 12.43 | 21.45 | 2 | 0.99 | 2.61 | 2
2018-07-12 08:00 | 18639.3401 | 444.358 | 17.2 | 21.26 | 16.33 | 22.6 | 2.02 | 1.26 | 2 | 2.14
2018-07-12 09:00 | 21974.2711 | 713.693 | 17.66 | 20.58 | 17.37 | 23.29 | 2.67 | 1.31 | 2.61 | 3
2018-07-12 10:00 | 19576.9739 | 826.341 | 18.97 | 24.15 | 19.47 | 26.79 | 3 | 1.85 | 2.11 | 3.4
2018-07-12 11:00 | 19960.4975 | 1067.05 | 20.15 | 24.46 | 22.4 | 31.23 | 6 | 2.11 | 2.11 | 5.76
2018-07-12 12:00 | 23299.8575 | 940.173 | 28.97 | 28.97 | 23.75 | 35.97 | 6.98 | 3.87 | 1.14 | 6.31
2018-07-12 13:00 | 20462.544 | 1061.52 | 30.09 | 30.09 | 31.74 | 41.69 | 14.36 | 11.16 | 1.18 | 13.36
2018-07-12 14:00 | 18521.6465 | 1001.47 | 32.49 | 32.49 | 31.85 | 48.24 | 18.94 | 10.51 | 1 | 18.09
2018-07-12 15:00 | 16870.5246 | 821.447 | 33.74 | 30.5 | 32.74 | 54.83 | 28.5 | 17.87 | 2 | 27.58
2018-07-12 16:00 | 16051.8745 | 525.71 | 40.67 | 31.15 | 33.4 | 60.04 | 34.85 | 21.01 | 2 | 31.15
2018-07-12 17:00 | 15187.0088 | 223.325 | 34.13 | 30.58 | 32.71 | 41.09 | 29.05 | 20.64 | 2.11 | 25.25
2018-07-12 18:00 | 16262.6979 | 80.8795 | 31.21 | 29.92 | 30.99 | 33.93 | 14.2 | 1 | 2.46 | 4
2018-07-12 19:00 | 14565.7232 | 2.3402 | 28.92 | 28.25 | 24.31 | 30.45 | 7.57 | 1 | 2.61 | 4.16
2018-07-12 20:00 | 16116.1291 | -0.048233 | 23.38 | 26.43 | 22.39 | 30.38 | 7.01 | 1.25 | 2.31 | 4.29
2018-07-12 21:00 | 16156.2191 | -0.048233 | 31.21 | 31.21 | 21.13 | 25.53 | 3.52 | 0.99 | 3.49 | 3
2018-07-12 22:00 | 13952.6042 | -0.048233 | 20.04 | 23.44 | 20.11 | 25 | 3.44 | 0.12 | 5 | 3.43
2018-07-12 23:00 | 13773.0542 | -0.048233 | 19.14 | 21.87 | 18.89 | 22.66 | 2.11 | 0.12 | 7.93 | 2.31
2018-07-13 | 15021.0391 | -0.048233 | 14.97 | 20.72 | 17.09 | 22.11 | 2 | 0.17 | 7.4 | 1.48
2018-07-13 01:00 | 13187.8542 | -0.048233 | 15.49 | 20.79 | 16.44 | 20.65 | 2 | 0.17 | 3.5 | 1.25
2018-07-13 02:00 | 13154.6042 | -0.048233 | 15.06 | 20.33 | 14.61 | 20.23 | 1.78 | 0.75 | 3.51 | 1.11
2018-07-13 03:00 | 14549.4541 | -0.048233 | 14.89 | 20.11 | 10.11 | 19.86 | 1.75 | 0.75 | 3.46 | 1.25
2018-07-13 04:00 | 13960.2042 | -0.048233 | 14.99 | 19.86 | 10.17 | 19.86 | 1.75 | 0.75 | 2.61 | 1.25
2018-07-13 05:00 | 16658.3991 | -0.048233 | 15.82 | 20.1 | 13.31 | 20.33 | 2 | 0.75 | 112.7434 | 1.48
2018-07-13 06:00 | 18085.2033 | 54.3728 | 17.15 | 20.92 | 18.19 | 21.37 | 1.75 | 0.99 | 2.31 | 2.11
2018-07-13 07:00 | 17418.8998 | 153.684 | 16.61 | 20.99 | 18.66 | 21.55 | 2 | 0.99 | 2.61 | 2.11
2018-07-13 08:00 | 20166.5265 | 379.191 | 17 | 21.24 | 20.09 | 23.27 | 2.61 | 1.36 | 3.5 | 2.79
2018-07-13 09:00 | 21344.7484 | 816.989 | 17.01 | 21.91 | 21.45 | 26.63 | 2.25 | 1.41 | 2.79 | 2.64
2018-07-13 10:00 | 21045.6137 | 932.449 | 18.32 | 26.49 | 21.66 | 32.61 | 4.22 | 1.84 | 2.31 | 4.22
2018-07-13 11:00 | 21017.9315 | 1013.21 | 30.92 | 30.92 | 21.75 | 37.7 | 5.37 | 1.48 | 2 | 5.37
2018-07-13 12:00 | 19420.983 | 1003.14 | 32.59 | 32.59 | 22.36 | 49.02 | 16.6 | 13.19 | 1.07 | 14.6
2018-07-13 13:00 | 21645.8253 | 1040.37 | 34.74 | 34.74 | 22.48 | 50 | 19.99 | 15 | 1 | 18.34
2018-07-13 14:00 | 18332.5585 | 985.43 | 50.07 | 50.07 | 28.21 | 63.67 | 34.99 | 54.2873 | 1 | 33.99
2018-07-13 15:00 | 19081.0222 | 803.277 | 40.44 | 40.44 | 31.11 | 71.89 | 84.1441 | 73.3073 | 2.11 | 78.6162
2018-07-13 16:00 | 16183.744 | 552.52 | 36.1 | 36.1 | 33.24 | 64.29 | 90.4241 | 74.3073 | 2 | 83.7262
2018-07-13 17:00 | 15464.9864 | 298.933 | 32.67 | 32.67 | 30.97 | 45.61 | 42.55 | 58.3073 | 2 | 37.4
2018-07-13 18:00 | 14903.6419 | 70.0441 | 31.75 | 31.75 | 23.24 | 40.03 | 24.58 | 16.08 | 3.5 | 17.58
2018-07-13 19:00 | 14649.6277 | 2.6607 | 30.06 | 30.06 | 22.05 | 33.95 | 7.31 | 1.32 | 2.21 | 4.03
2018-07-13 20:00 | 14679.3542 | -0.048233 | 29.15 | 29.15 | 21.66 | 33.72 | 5.48 | 0.99 | 2.31 | 3.48
2018-07-13 21:00 | 16276.4891 | -0.048233 | 31.95 | 31.95 | 21.32 | 32.44 | 5 | 1.15 | 3.5 | 5
2018-07-13 22:00 | 14381.0542 | -0.048233 | 20.11 | 28.15 | 19.96 | 25.84 | 4.41 | 0.3 | 4 | 2.61
2018-07-13 23:00 | 15575.9691 | -0.048233 | 18.18 | 25.85 | 18.46 | 22.8 | 2.1 | 0.3 | 5 | 1.48
2018-07-14 | 15225.7091 | -0.048233 | 18.36 | 21.58 | 17.24 | 21.06 | 1.85 | 0.25 | 3.5 | 1.48
2018-07-14 01:00 | 13515.6042 | -0.048233 | 16.9 | 21.06 | 15.49 | 20.13 | 1.75 | 0.25 | 3.45 | 1.25
2018-07-14 02:00 | 13299.9542 | -0.048233 | 16.51 | 20.65 | 14.22 | 19.42 | 1.61 | 0.89 | 3.45 | 1
2018-07-14 03:00 | 14799.4891 | -0.048233 | 15.42 | 20.35 | 13 | 18.94 | 1.61 | 0.89 | 2.61 | 1
2018-07-14 04:00 | 15664.5891 | -0.048233 | 16.33 | 20.31 | 12.36 | 18.66 | 1.61 | 0.89 | 2.11 | 1.2
2018-07-14 05:00 | 14892.1542 | -0.048233 | 16.79 | 20.65 | 15.79 | 19.69 | 1.75 | 0.97 | 25 | 1.48
2018-07-14 06:00 | 18354.334 | 53.473 | 17.94 | 21.35 | 16.97 | 20.8 | 1.75 | 0.99 | 2.31 | 2.1
2018-07-14 07:00 | 19041.9619 | 141.253 | 17.6 | 21.29 | 17.5 | 21.11 | 1.75 | 0.99 | 2.4 | 2.1
2018-07-14 08:00 | 18115.9974 | 233.471 | 18.32 | 27.79 | 19.72 | 22.94 | 2.5 | 1.34 | 2.74 | 2.61
2018-07-14 09:00 | 19021.8187 | 619.967 | 18.53 | 28.12 | 20.53 | 25.11 | 3.11 | 1.34 | 2 | 3.11
2018-07-14 10:00 | 21812.3381 | 842.202 | 19.85 | 28.95 | 21.22 | 32.64 | 5.27 | 1.41 | 0.66 | 5.27
2018-07-14 11:00 | 19313.6045 | 1044.11 | 32.08 | 32.08 | 21.47 | 35.58 | 8.25 | 1.54 | 2 | 9.35
2018-07-14 12:00 | 21322.4175 | 1098.65 | 46.09 | 46.09 | 21.74 | 42.91 | 14.98 | 8.73 | 1.73 | 12.98
2018-07-14 13:00 | 20865.9483 | 1115.15 | 37.38 | 37.38 | 23.18 | 53.83 | 20.5 | 12.35 | 1 | 19.65
2018-07-14 14:00 | 20066.2266 | 1001.12 | 41.18 | 41.18 | 27.28 | 69.75 | 37.64 | 26.29 | 2 | 32.1
2018-07-14 15:00 | 18799.5873 | 841.514 | 38.23 | 34.25 | 29.02 | 85.7 | 53.15 | 64.6073 | 2.11 | 44.69
2018-07-14 16:00 | 15980.7261 | 470.817 | 39.78 | 33.92 | 29.51 | 67.84 | 48.8 | 66.3473 | 2.31 | 47.8
2018-07-14 17:00 | 17276.009 | 272.364 | 37.31 | 37.31 | 23.7 | 45.62 | 31.16 | 28.13 | 2.67 | 30.54
2018-07-14 18:00 | 16793.4631 | 75.9745 | 38.13 | 38.13 | 22.11 | 38.71 | 18.8 | 12.78 | 2.11 | 15.28
2018-07-14 19:00 | 16524.7714 | 2.2904 | 32.48 | 32.48 | 20.56 | 34.17 | 14.89 | 1.42 | 2 | 4.88
2018-07-14 20:00 | 14808.5542 | -0.048233 | 31.48 | 31.48 | 19.01 | 31.06 | 5 | 0.99 | 2.31 | 3
2018-07-14 21:00 | 16150.9441 | -0.048233 | 36.14 | 36.14 | 18.18 | 26.95 | 4.98 | 1.07 | 3.11 | 4.93
2018-07-14 22:00 | 13907.9542 | -0.048233 | 37.61 | 37.61 | 17.98 | 25.35 | 3.46 | 0.12 | 3.12 | 2.4
2018-07-14 23:00 | 13346.5042 | -0.048233 | 20.84 | 29.04 | 17.2 | 23.24 | 2.49 | 0.12 | 3.01 | 1.48
2018-07-15 | 14361.6641 | -0.048233 | 19.76 | 24.24 | 16.69 | 22.03 | 2 | 0.25 | 2.99 | 0.95
2018-07-15 01:00 | 12680.5542 | -0.048233 | 19.6 | 21.88 | 15.27 | 20.91 | 1.85 | 0.25 | 2.99 | 0.95
2018-07-15 02:00 | 13894.2991 | -0.048233 | 18.75 | 21.07 | 15 | 20.1 | 1.75 | 0.7 | 2.61 | 0.95
2018-07-15 03:00 | 12448.7542 | -0.048233 | 17.96 | 20.89 | 15 | 19.43 | 1.75 | 0.7 | 2.61 | 0.95
2018-07-15 04:00 | 12692.9042 | -0.048233 | 17.88 | 20.74 | 15.73 | 19.05 | 1.75 | 0.7 | 2 | 0.95
2018-07-15 05:00 | 13192.6042 | -0.048233 | 18.21 | 20.77 | 15 | 19.15 | 1.75 | 0.7 | 112.7434 | 0.95
2018-07-15 06:00 | 15237.2634 | 45.9037 | 19.33 | 20.95 | 15 | 19.97 | 1.75 | 0.99 | 2.61 | 1.96
2018-07-15 07:00 | 15256.201 | 219.854 | 18.97 | 21.05 | 16.72 | 20.54 | 1.75 | 0.99 | 3.01 | 2.1
2018-07-15 08:00 | 13958.8364 | 366.512 | 20.43 | 22.03 | 17.18 | 22.27 | 1.97 | 0.99 | 3.11 | 2.61
2018-07-15 09:00 | 16330.7965 | 749.428 | 20.41 | 27.31 | 18.08 | 26.69 | 2.69 | 1.2 | 3.01 | 3.11
2018-07-15 10:00 | 15161.8793 | 958.873 | 23.03 | 27.8 | 18.22 | 31.67 | 5.19 | 0.99 | 1.54 | 5.19
2018-07-15 11:00 | 15039.9601 | 793.537 | 29.88 | 29.88 | 30.62 | 36.89 | 13.43 | 0.99 | 0.92 | 12.58
2018-07-15 12:00 | 15542.322 | 974.339 | 31.99 | 31.99 | 33.8 | 41.26 | 14.61 | 7 | 1.24 | 13.72
2018-07-15 13:00 | 16940.3544 | 816.208 | 32.7 | 32.7 | 36.67 | 47.67 | 24.68 | 10.23 | 1.15 | 20.3
2018-07-15 14:00 | 16511.6731 | 815.875 | 39.31 | 39.31 | 37.22 | 61.55 | 39.36 | 20.08 | 2.11 | 30.71
2018-07-15 15:00 | 15013.5331 | 820.719 | 33.29 | 32.79 | 39.48 | 70.74 | 53.59 | 54.1973 | 2.11 | 45.05
2018-07-15 16:00 | 16457.3575 | 546.391 | 35.5 | 35.5 | 38.83 | 65 | 50 | 58.8873 | 2.11 | 44.58
2018-07-15 17:00 | 14467.6279 | 262.082 | 33.12 | 32.18 | 36.31 | 40.31 | 28.32 | 16.12 | 2.34 | 24.32
2018-07-15 18:00 | 14199.5141 | 65.857 | 31.35 | 31.35 | 30.62 | 35.48 | 16.33 | 8 | 2.11 | 12.47
2018-07-15 19:00 | 15664.9462 | 2.2902 | 29.96 | 28.9 | 29.42 | 32.09 | 19.48 | 1.16 | 2.11 | 16.26
2018-07-15 20:00 | 13916.5042 | -0.048233 | 27.7 | 27.7 | 19.9 | 30.77 | 7.83 | 1.17 | 3.01 | 5.78
2018-07-15 21:00 | 13937.4042 | -0.048233 | 24.08 | 24.08 | 18.25 | 27.08 | 5.5 | 0.97 | 3.5 | 5.57
2018-07-15 22:00 | 14608.5341 | -0.048233 | 22.62 | 25.48 | 17.15 | 25.23 | 4.14 | 0.12 | 2.99 | 2.61
2018-07-15 23:00 | 12750.8542 | -0.048233 | 19.77 | 21.53 | 17.11 | 23.51 | 2.4 | 0.12 | 3.11 | 1.33
2018-07-16 | 12493.4042 | -0.048233 | 18.94 | 20.91 | 16.52 | 21.97 | 2.47 | 0.17 | 3.01 | 0.95
2018-07-16 01:00 | 13652.7041 | -0.048233 | 18.72 | 20.38 | 16.47 | 21.07 | 1.99 | 0.17 | 2.99 | 0.95
2018-07-16 02:00 | 12294.8542 | -0.048233 | 18.11 | 19.41 | 15.3 | 20.32 | 1.75 | 0.97 | 2.61 | 0.95
2018-07-16 03:00 | 12353.7542 | -0.048233 | 16.31 | 19.29 | 13.12 | 19.43 | 1.75 | 0.97 | 2.51 | 0.95
2018-07-16 04:00 | 12330.9542 | -0.048233 | 4.91 | 19.38 | 11.45 | 18.93 | 1.75 | 0.97 | 2 | 0.95
2018-07-16 05:00 | 13604.1741 | -0.048233 | 16.16 | 19.33 | 10.1 | 18.84 | 1.75 | 0.97 | 2.11 | 0.95
2018-07-16 06:00 | 12232.1957 | 50.9955 | 17.91 | 19.66 | 10.04 | 19.95 | 1.61 | 1.24 | 2.61 | 1.87
2018-07-16 07:00 | 12081.0474 | 230.892 | 18.01 | 19.75 | 16.73 | 20.37 | 1.75 | 1.26 | 2.61 | 2.01
2018-07-16 08:00 | 13537.9467 | 440.177 | 19.34 | 21.1 | 17.11 | 22.16 | 1.85 | 1.27 | 3.44 | 2.21
2018-07-16 09:00 | 12491.6564 | 660.112 | 20.1 | 21.34 | 18.38 | 24.23 | 3.11 | 1.61 | 3 | 3.11
2018-07-16 10:00 | 14350.1701 | 951.057 | 20.56 | 24.3 | 18.48 | 27.26 | 5 | 2.52 | 1.83 | 5
2018-07-16 11:00 | 13161.3285 | 1084.03 | 28.85 | 28.85 | 19.25 | 33.26 | 7.57 | 5.65 | 1 | 11.23
2018-07-16 12:00 | 12883.824 | 1022.92 | 31.16 | 30.21 | 19.8 | 39.59 | 15.51 | 7.47 | 1 | 14.66
2018-07-16 13:00 | 14208.2652 | 1072.55 | 36.33 | 31.88 | 20.86 | 44.54 | 18.42 | 10 | 1 | 17.19
2018-07-16 14:00 | 12776.0693 | 939.494 | 35.7 | 33.41 | 21.57 | 50.24 | 28.28 | 14.49 | 1.46 | 24.34
2018-07-16 15:00 | 12563.7291 | 760.978 | 362.5257 | 52.38 | 21.63 | 58.55 | 32.44 | 26.13 | 2 | 30.63
2018-07-16 16:00 | 13872.3722 | 548.168 | 107.14 | 107.14 | 21.37 | 59.33 | 38.41 | 29.37 | 2.11 | 37.13
2018-07-16 17:00 | 12322.2932 | 270.835 | 34.11 | 34.11 | 21.29 | 42.45 | 24.48 | 14.47 | 2.61 | 22
2018-07-16 18:00 | 12255.6998 | 69.7366 | 64.47 | 64.47 | 20.18 | 34.59 | 17.18 | 7.76 | 2.25 | 16.18
2018-07-16 19:00 | 13614.0262 | 2.2902 | 37.2 | 37.2 | 20.39 | 32.12 | 9.62 | 1.53 | 1.35 | 7.82
2018-07-16 20:00 | 12216.9542 | -0.048233 | 32.27 | 32.27 | 20.73 | 30.75 | 6.53 | 1.43 | 2 | 4.11
2018-07-16 21:00 | 12391.7542 | -0.048233 | 31.32 | 31.32 | 20.05 | 27.85 | 5.57 | 1.26 | 2.22 | 5.47
2018-07-16 22:00 | 13636.8791 | -0.048233 | 32.04 | 32.04 | 17.21 | 26.28 | 4.03 | 0.17 | 2.99 | 2.91
2018-07-16 23:00 | 12191.3042 | -0.048233 | 6.47 | 26.41 | 16.67 | 23.84 | 2.76 | 0.17 | 3.03 | 1.79
2018-07-17 | 13405.8341 | -0.048233 | 17.69 | 21.87 | 14.26 | 20.86 | 1.85 | 0.12 | 3.46 | 0.95
2018-07-17 01:00 | 13384.7341 | -0.048233 | 18.97 | 21.1 | 11.2 | 20.24 | 1.75 | 0.17 | 2.99 | 0.95
2018-07-17 02:00 | 11997.5042 | -0.048233 | 15.76 | 20.82 | 8.84 | 19.44 | 1.75 | 0.9 | 2.99 | 0.95
2018-07-17 03:00 | 13105.1591 | -0.048233 | 15.27 | 20.75 | 6.74 | 19.08 | 1.75 | 0.75 | 2.61 | 0.95
2018-07-17 04:00 | 12586.5042 | -0.048233 | 14.93 | 20.91 | 6.82 | 19.07 | 1.75 | 0.75 | 2 | 0.95
2018-07-17 05:00 | 13609.6542 | -0.048233 | 14.7 | 21.04 | 11.02 | 19.79 | 1.85 | 0.97 | 2.11 | 0.95
2018-07-17 06:00 | 15443.023 | 60.8137 | 14.87 | 21.19 | 10.33 | 21.36 | 1.75 | 1 | 2.56 | 1.5
2018-07-17 07:00 | 18316.9142 | 222.004 | 14.8 | 21.25 | 12.72 | 21.75 | 1.75 | 1 | 2.11 | 1.5
2018-07-17 08:00 | 17490.6524 | 491.213 | 17.83 | 26.37 | 12.82 | 23.07 | 2.44 | 1.41 | 1.68 | 2.61
2018-07-17 09:00 | 19777.7495 | 668.682 | 16.56 | 27.73 | 15.97 | 25.54 | 2.62 | 1.35 | 2 | 3
2018-07-17 10:00 | 18169.1129 | 903.382 | 17.79 | 30.08 | 18.14 | 30.72 | 5 | 1.01 | 0.61 | 5
2018-07-17 11:00 | 19952.2866 | 1063.12 | 30.81 | 30.81 | 19.74 | 35.62 | 7.62 | 2 | 0.59 | 7.54
2018-07-17 12:00 | 18779.0585 | 1034.43 | 36.77 | 36.77 | 19.94 | 40.58 | 13.76 | 8.5 | 1 | 12.91
2018-07-17 13:00 | 21631.2452 | 1111.55 | 53.57 | 53.57 | 20.59 | 47.21 | 18.83 | 12.71 | 1 | 15.97
2018-07-17 14:00 | 19947.9716 | 975.03 | 57.45 | 57.45 | 20.92 | 54.07 | 26.5 | 16.15 | 2 | 22.5
2018-07-17 15:00 | 16469.9087 | 829.746 | 73.38 | 73.38 | 21.13 | 56.69 | 40.39 | 21.48 | 2.11 | 35.91
2018-07-17 16:00 | 15581.7167 | 592.807 | 48.03 | 48.03 | 21.89 | 53.3 | 42.56 | 23.73 | 2.03 | 38.18
2018-07-17 17:00 | 16593.4187 | 283.359 | 43.2 | 43.2 | 22.03 | 36.49 | 23.2 | 15 | 2.11 | 19.66
2018-07-17 18:00 | 14376.3984 | 58.0509 | 38.86 | 38.86 | 21.2 | 32.06 | 15.02 | 5.61 | 2.11 | 12.13
2018-07-17 19:00 | 16126.057 | 2.3621 | 31.55 | 31.55 | 20.13 | 29.88 | 8.25 | 1.82 | 2.31 | 5.4
2018-07-17 20:00 | 16202.6391 | -0.048233 | 19.45 | 28.96 | 20.1 | 30.44 | 6.91 | 1.46 | 2.61 | 3.81
2018-07-17 21:00 | 14351.6042 | -0.048233 | 19.93 | 30.52 | 18.94 | 25.62 | 5.02 | 1.25 | 2 | 2.61
2018-07-17 22:00 | 15455.6991 | -0.048233 | 52.3 | 52.3 | 17.33 | 25.39 | 3.16 | 0.12 | 2.99 | 2.21
2018-07-17 23:00 | 13569.7542 | -0.048233 | 15.11 | 23.68 | 17.27 | 23.2 | 2.06 | 0.12 | 2.99 | 1.01
2018-07-18 | 14882.8341 | -0.048233 | 16.22 | 21.33 | 15.63 | 21.01 | 1.75 | 0.12 | 13.3 | 0.95
2018-07-18 01:00 | 13250.5542 | -0.048233 | 14.95 | 20.99 | 12.57 | 20.42 | 1.75 | 0.12 | 2.99 | 0.95
2018-07-18 02:00 | 14527.2991 | -0.048233 | 15.45 | 20.29 | 11.17 | 19.66 | 1.61 | 0.75 | 2.99 | 0.95
2018-07-18 03:00 | 13043.4542 | -0.048233 | 15.4 | 19.69 | 8.59 | 19.4 | 1.61 | 0.75 | 2.29 | 0.95
2018-07-18 04:00 | 13811.0542 | -0.048233 | 15.24 | 19.71 | 5.96 | 19.22 | 1.61 | 0.75 | 2 | 0.95
2018-07-18 05:00 | 16493.8191 | -0.048233 | 15.68 | 20.41 | 5.34 | 20.15 | 1.75 | 0.75 | 20 | 0.95
2018-07-18 06:00 | 15882.9545 | 49.8995 | 16.52 | 20.96 | 9.22 | 21.77 | 1.86 | 1.41 | 2 | 1.92
2018-07-18 07:00 | 17242.6026 | 231.108 | 15.91 | 21.06 | 12.01 | 22.48 | 2.01 | 1.33 | 1 | 2.11
2018-07-18 08:00 | 17745.0367 | 463.986 | 18.35 | 21.86 | 13.65 | 24.58 | 3.03 | 1.29 | 2.99 | 3.11
2018-07-18 09:00 | 21043.8729 | 630.799 | 18.52 | 24.63 | 16.37 | 26.78 | 4.65 | 1.55 | 2.2 | 4
2018-07-18 10:00 | 21027.2219 | 928.016 | 20.25 | 27.72 | 18.38 | 29.06 | 5 | 0.99 | 2.31 | 5
2018-07-18 11:00 | 19178.372 | 979.76 | 29.44 | 29.44 | 18.73 | 33.63 | 7.97 | 1.94 | 1.8 | 13.83
2018-07-18 12:00 | 19588.468 | 1052.44 | 31.36 | 31.36 | 23.13 | 39.87 | 17.88 | 8.28 | 1.18 | 15.95
2018-07-18 13:00 | 21382.7748 | 868.033 | 36.86 | 36.86 | 23.13 | 45.5 | 21.91 | 16.66 | 1 | 19.86
2018-07-18 14:00 | 18414.7981 | 884.998 | 42.45 | 42.45 | 30.53 | 55.99 | 28.5 | 16.84 | 1 | 22.18
2018-07-18 15:00 | 18793.8038 | 603.032 | 66.05 | 66.05 | 32 | 64.01 | 34.31 | 20 | 1.2 | 29.27
2018-07-18 16:00 | 17809.2672 | 437.822 | 51.99 | 51.99 | 32.97 | 64.85 | 40.16 | 20 | 1.68 | 38.41
2018-07-18 17:00 | 15477.0067 | 187.586 | 43.86 | 36.28 | 31.57 | 40.42 | 25.99 | 10.39 | 2.11 | 23.06
2018-07-18 18:00 | 15016.3606 | 62.6954 | 56.56 | 56.56 | 23.12 | 35.28 | 15.2 | 3.32 | 2.11 | 5
2018-07-18 19:00 | 14932.7896 | 1.7259 | 43.15 | 43.15 | 22.85 | 33.55 | 9.12 | 1.73 | 2.11 | 5.34
2018-07-18 20:00 | 14948.2042 | -0.048233 | 32.57 | 32.57 | 22.77 | 33.5 | 8.8 | 0.99 | 2.59 | 5.86
2018-07-18 21:00 | 16526.5241 | -0.048233 | 32.03 | 32.03 | 19.6 | 31.63 | 5.86 | 0.99 | 4.22 | 5.86
2018-07-18 22:00 | 14416.2042 | -0.048233 | 22.92 | 26.26 | 18.71 | 26 | 4.11 | 0.12 | 2.99 | 2.4
2018-07-18 23:00 | 15479.9641 | -0.048233 | 19.63 | 23.2 | 17.29 | 24.4 | 2.37 | 0.12 | 3.18 | 1.53
2018-07-19 | 15297.4491 | -0.048233 | 18.24 | 21.92 | 18.05 | 21.06 | 1.05 | 0.25 | 8.61 | 0.95
2018-07-19 01:00 | 13597.3042 | -0.048233 | 18.1 | 20.98 | 16.44 | 20.15 | 1 | 0.25 | 3.25 | 0.95
2018-07-19 02:00 | 13482.3542 | -0.048233 | 17.37 | 20.13 | 15.73 | 19.59 | 1 | 0.7 | 2.99 | 0.95
2018-07-19 03:00 | 14973.5641 | -0.048233 | 16.73 | 19.36 | 15.6 | 19.15 | 1 | 0.7 | 2.35 | 0.95
2018-07-19 04:00 | 14231.9042 | -0.048233 | 16.68 | 19.2 | 15.19 | 19.01 | 1 | 0.7 | 2 | 0.95
2018-07-19 05:00 | 16808.2091 | -0.048233 | 17.46 | 19.76 | 13.18 | 19.95 | 1 | 0.7 | 20 | 0.95
2018-07-19 06:00 | 18471.9828 | 46.9884 | 17.99 | 21 | 15.57 | 22.03 | 1.51 | 0.99 | 1 | 1.51
2018-07-19 07:00 | 19693.8686 | 245.174 | 17.97 | 20.78 | 16.17 | 22.57 | 1.89 | 1 | 2 | 2.01
2018-07-19 08:00 | 18295.9075 | 419.85 | 18.75 | 22.29 | 16.99 | 23.49 | 2.34 | 1.28 | 2.99 | 2.34
2018-07-19 09:00 | 19156.0945 | 470.31 | 18.77 | 23.31 | 19.04 | 26.12 | 3.73 | 1.33 | 1 | 3.53
2018-07-19 10:00 | 21099.2636 | 571.302 | 106.93 | 26.12 | 20.35 | 32.08 | 5 | 0.99 | 2.31 | 4.93
2018-07-19 11:00 | 18947.7215 | 489.97 | 118.33 | 30.05 | 30.01 | 37.5 | 8.31 | 2.84 | 2 | 10.96
2018-07-19 12:00 | 20072.5025 | 1155.95 | 165.99 | 32.65 | 32.1 | 40.91 | 15.89 | 7.69 | 1.51 | 14.02
2018-07-19 13:00 | 21999.4824 | 1095.59 | 84.02 | 31.71 | 35 | 51.68 | 22.28 | 13.62 | 1 | 18.34
2018-07-19 14:00 | 18909.806 | 935.059 | 35.16 | 34.42 | 37.29 | 65.47 | 33.52 | 20 | 1 | 25.72
2018-07-19 15:00 | 17486.0629 | 807.382 | 40.23 | 34.04 | 41.01 | 75.52 | 43.89 | 29.13 | 1.2 | 34
2018-07-19 16:00 | 16897.6481 | 534.998 | 36.33 | 33.48 | 41.75 | 66.22 | 48.19 | 62.5073 | 1.64 | 44.6
2018-07-19 17:00 | 17972.1972 | 266.258 | 34.07 | 34.07 | 39.78 | 46.77 | 37.5 | 26.27 | 2.11 | 34.24
2018-07-19 18:00 | 15793.9985 | 60.2616 | 38.53 | 38.53 | 36.23 | 38.14 | 19.88 | 8.56 | 2.19 | 14.63
2018-07-19 19:00 | 15703.2396 | 1.7259 | 31.76 | 31.76 | 31.84 | 36.19 | 15.33 | 1.28 | 2.11 | 5.34
2018-07-19 20:00 | 17176.4041 | -0.048233 | 32.73 | 32.73 | 24.7 | 34.44 | 7.48 | 1.02 | 2.51 | 5.86
2018-07-19 21:00 | 17035.0341 | -0.048233 | 32 | 32 | 22.41 | 34.61 | 5 | 0.99 | 3.5 | 4.52
2018-07-19 22:00 | 16492.7641 | -0.048233 | 23.47 | 24.98 | 19.47 | 27.57 | 4.32 | 0.12 | 2.99 | 2.4
2018-07-19 23:00 | 14260.4042 | -0.048233 | 20.4 | 22.6 | 17.41 | 24.07 | 2.5 | 0.12 | 3.11 | 1
2018-07-20 | 15523.2191 | -0.048233 | 18.96 | 21.24 | 17.84 | 21.36 | 1.51 | 0.25 | 2.61 | 0.95
2018-07-20 01:00 | 15211.9941 | -0.048233 | 18.44 | 20.22 | 16.51 | 20.24 | 1.01 | 0.45 | 2.11 | 0.95
2018-07-20 02:00 | 13475.7042 | -0.048233 | 17.65 | 19.67 | 14.29 | 19.65 | 1 | 0.89 | 1.76 | 0.95
2018-07-20 03:00 | 13509.9042 | -0.048233 | 17.12 | 19.05 | 10.75 | 19.08 | 1 | 0.89 | 2.61 | 0.95
2018-07-20 04:00 | 14259.4542 | -0.048233 | 16.99 | 18.53 | 12.27 | 18.95 | 1 | 0.89 | 2.11 | 0.95
2018-07-20 05:00 | 17158.4691 | -0.048233 | 17.73 | 18.78 | 15.46 | 20.03 | 1 | 0.89 | 2.11 | 0.95
2018-07-20 06:00 | 17056.0069 | 50.6915 | 18.65 | 20.16 | 16.75 | 21.07 | 1.32 | 0.99 | 2 | 1.5
2018-07-20 07:00 | 18026.3203 | 187.074 | 18.15 | 20.19 | 18.1 | 21.62 | 1.51 | 1.26 | 0.68 | 1.61
2018-07-20 08:00 | 18607.2035 | 420.53 | 20.19 | 21.2 | 19.77 | 22.72 | 1.65 | 1.35 | 1.99 | 2.11
2018-07-20 09:00 | 19818.8497 | 640.947 | 20.88 | 21.78 | 22.77 | 25.86 | 3.85 | 1.41 | 1.99 | 3.4
2018-07-20 10:00 | 20535.6626 | 739.487 | 24.28 | 24.28 | 27.69 | 30.07 | 5.82 | 1.9 | 2.31 | 5.2
2018-07-20 11:00 | 21256.2181 | 896.074 | 28.73 | 28.73 | 33.93 | 37.01 | 14.86 | 2.15 | 2 | 13.15
2018-07-20 12:00 | 21636.5519 | 1055.58 | 31.12 | 30.55 | 39.26 | 43.45 | 18.02 | 7.82 | 1.44 | 14.59
2018-07-20 13:00 | 21169.4116 | 649.793 | 34.15 | 34.15 | 41.91 | 55.99 | 22.75 | 12.21 | 0.99 | 19.26
2018-07-20 14:00 | 18536.6992 | 765.315 | 35.73 | 35.73 | 44.04 | 70 | 40.19 | 20.58 | 1 | 37.46
2018-07-20 15:00 | 19019.5569 | 548.016 | 37.42 | 37.42 | 47.73 | 91.39 | 108.6041 | 73.3073 | 1.52 | 86.2962
2018-07-20 16:00 | 16521.5374 | 446.092 | 39.21 | 39.21 | 50.71 | 71 | 444.1178 | 74.5773 | 2 | 101.0162
2018-07-20 17:00 | 17277.7877 | 153.05 | 44.69 | 44.69 | 44.37 | 52.07 | 45 | 26.83 | 2.11 | 38.29
2018-07-20 18:00 | 15147.1545 | 69.3732 | 35.08 | 35.08 | 41.39 | 41.39 | 24.23 | 10 | 2.11 | 18.23
2018-07-20 19:00 | 16968.3308 | 1.7259 | 40.51 | 40.51 | 34.9 | 37.16 | 16.45 | 2.14 | 2.11 | 12.26
2018-07-20 20:00 | 15096.4042 | -0.048233 | 31.94 | 31.94 | 33.45 | 35.92 | 11.64 | 1.32 | 2.31 | 7.42
2018-07-20 21:00 | 15082.1542 | -0.048233 | 31.61 | 31.61 | 22.67 | 32.74 | 8.6 | 1.25 | 7.97 | 7.6
2018-07-20 22:00 | 14525.4542 | -0.048233 | 28.91 | 26.13 | 19.33 | 27.6 | 5 | 0.45 | 1.99 | 2.4
2018-07-20 23:00 | 15577.0241 | -0.048233 | 20.41 | 24.61 | 16.48 | 24.57 | 2.5 | 0.45 | 2.09 | 1
2018-07-21 | 13841.4542 | -0.048233 | 19.52 | 22.03 | 13.41 | 22.01 | 1.51 | 0.25 | 2.61 | 0.95
2018-07-21 01:00 | 13670.4542 | -0.048233 | 18.46 | 20.4 | 9.58 | 20.63 | 1.15 | 0.25 | 2.73 | 0.95
2018-07-21 02:00 | 15110.7141 | -0.048233 | 17.53 | 19.3 | 9.06 | 20.04 | 1 | 0.82 | 2.99 | 0.95
2018-07-21 03:00 | 13371.2042 | -0.048233 | 16.78 | 18.93 | 7.67 | 19.13 | 1 | 0.82 | 2.61 | 0.95
2018-07-21 04:00 | 14207.2042 | -0.048233 | 16.56 | 18.4 | 9.01 | 19.13 | 1 | 0.7 | 2.11 | 0.95
2018-07-21 05:00 | 15194.2542 | -0.048233 | 16.86 | 18.36 | 9.49 | 19.74 | 1 | 0.7 | 2.11 | 0.95
2018-07-21 06:00 | 16834.4525 | 27.4763 | 17.46 | 19.33 | 15.78 | 20.46 | 1 | 0.99 | 2.31 | 1.5
2018-07-21 07:00 | 19413.7584 | 95.6667 | 16.94 | 19.1 | 17.79 | 20.58 | 1.01 | 1 | 1.97 | 1.5
2018-07-21 08:00 | 20095.2644 | 237.644 | 18.45 | 21.18 | 19.45 | 22.42 | 1.63 | 1.13 | 0.56 | 1.67
2018-07-21 09:00 | 18924.6517 | 345.686 | 19.87 | 21.14 | 22.33 | 24.91 | 3 | 1.15 | 0.25 | 3
2018-07-21 10:00 | 20057.0051 | 876.637 | 21.62 | 24.43 | 24.21 | 28.44 | 5.44 | 1.6 | 0.25 | 5.44
2018-07-21 11:00 | 19718.5705 | 922.39 | 29.01 | 29.01 | 31.23 | 33.75 | 17.3 | 8.11 | 1.06 | 16.3
2018-07-21 12:00 | 22696.4798 | 824.251 | 32.53 | 32.53 | 34.76 | 38.11 | 18.81 | 8.15 | 1.18 | 16.12
2018-07-21 13:00 | 23617.2089 | 1046.98 | 36.12 | 36.12 | 36.21 | 49.99 | 28.73 | 18.17 | 1 | 22.89
2018-07-21 14:00 | 20752.925 | 891.019 | 45.5 | 34.78 | 38.45 | 61.95 | 30.08 | 16.83 | 2.11 | 24.05
2018-07-21 15:00 | 17711.3335 | 870.509 | 60.71 | 33.7 | 40.38 | 72.41 | 51.19 | 55.7073 | 2.31 | 41.66
2018-07-21 16:00 | 18389.6639 | 385.961 | 33.99 | 33.99 | 40.42 | 58.73 | 104.3241 | 62.4273 | 2.11 | 96.2362
2018-07-21 17:00 | 16002.0593 | 292.273 | 33.94 | 33.94 | 37.94 | 41.19 | 28.54 | 18.17 | 3 | 25.75
2018-07-21 18:00 | 17193.551 | 78.2047 | 31.91 | 31.91 | 34.36 | 35.92 | 18.96 | 9.06 | 2.18 | 13.26
2018-07-21 19:00 | 15164.5896 | 1.7259 | 30.14 | 29.86 | 31.29 | 34.51 | 13.78 | 9.61 | 2.11 | 4.3
2018-07-21 20:00 | 16851.4641 | -0.048233 | 28.72 | 28.04 | 28.6 | 31.9 | 12.33 | 1 | 2.11 | 5.73
2018-07-21 21:00 | 16640.4641 | -0.048233 | 31.36 | 31.36 | 22.66 | 27.88 | 6.19 | 1.2 | 3.5 | 3.87
2018-07-21 22:00 | 15948.3841 | -0.048233 | 28.17 | 26.1 | 20.25 | 26.06 | 4.96 | 0.25 | 1.99 | 3
2018-07-21 23:00 | 13959.2542 | -0.048233 | 20.33 | 24.43 | 18.82 | 24.08 | 2.61 | 0.25 | 2.3 | 1
2018-07-22 | 15229.9291 | -0.048233 | 18.94 | 23.57 | 18.42 | 22.79 | 1.75 | 0.25 | 1.93 | 1.01
2018-07-22 01:00 | 13496.6042 | -0.048233 | 17.81 | 24.32 | 17.17 | 21.52 | 1.61 | 0.12 | 3.5 | 1
2018-07-22 02:00 | 13298.0542 | -0.048233 | 17.32 | 22.89 | 16.03 | 20.25 | 1.01 | 0.76 | 3.44 | 0.95
2018-07-22 03:00 | 13179.3042 | -0.048233 | 16.82 | 21.48 | 13.05 | 19.7 | 1.01 | 0.76 | 2.61 | 0.95
2018-07-22 04:00 | 14958.7941 | -0.048233 | 16.61 | 21.22 | 15.39 | 19.12 | 1.01 | 0.7 | 2 | 0.95
2018-07-22 05:00 | 13993.4542 | -0.048233 | 16.76 | 21.18 | 15.48 | 19.22 | 1.15 | 0.7 | 2.61 | 1
2018-07-22 06:00 | 15780.6311 | 45.9442 | 17.54 | 21.1 | 16.91 | 19.9 | 1.01 | 0.99 | 2.13 | 2
2018-07-22 07:00 | 14309.0339 | 188.141 | 16.96 | 20.89 | 19.08 | 19.87 | 1 | 0.99 | 0.88 | 1.85
2018-07-22 08:00 | 16472.7383 | 382.97 | 18.95 | 22.06 | 19.91 | 21.78 | 1.44 | 0.99 | 0.25 | 2
2018-07-22 09:00 | 16814.8168 | 481.215 | 20.19 | 21.29 | 21.06 | 22.76 | 1.97 | 1.26 | 2.61 | 2.83
2018-07-22 10:00 | 17013.965 | 635.981 | 22.52 | 22.52 | 20.5 | 25.99 | 4 | 1.22 | 2.28 | 4
2018-07-22 11:00 | 17342.1354 | 929.043 | 30.39 | 30.39 | 30.45 | 31.81 | 15.46 | 1.35 | 1.9 | 15
2018-07-22 12:00 | 15271.7364 | 548.512 | 40.83 | 40.83 | 31.64 | 37.59 | 19.11 | 9.61 | 1.16 | 15.31
2018-07-22 13:00 | 15240.051 | 838.159 | 34.03 | 34.03 | 32.09 | 43.63 | 20.01 | 12.83 | 1 | 15.25
2018-07-22 14:00 | 16419.3659 | 543.38 | 39.11 | 39.11 | 32.19 | 50.82 | 26.4 | 16.73 | 2 | 22.91
2018-07-22 15:00 | 16553.1262 | 599.167 | 41.37 | 37.37 | 35.03 | 68.71 | 45.6 | 22.16 | 2.31 | 38.26
2018-07-22 16:00 | 16552.7548 | 530.815 | 38.87 | 35.81 | 34.65 | 68.84 | 93.9941 | 25.23 | 2.11 | 83.5562
2018-07-22 17:00 | 14313.1532 | 261.477 | 38.75 | 31.32 | 32.39 | 46.64 | 27.29 | 19.06 | 2.11 | 26.28
2018-07-22 18:00 | 15629.2707 | 74.4746 | 34.85 | 30.57 | 30.54 | 37.1 | 17.98 | 8.09 | 2.11 | 13.12
2018-07-22 19:00 | 14091.1024 | 1.7394 | 36.82 | 29.41 | 29.25 | 32.87 | 14.04 | 0.99 | 2 | 4
2018-07-22 20:00 | 13985.8542 | -0.048233 | 31.14 | 26.87 | 22.76 | 30.48 | 10 | 0.99 | 2.5 | 5.69
2018-07-22 21:00 | 15511.6141 | -0.048233 | 29.3 | 29.3 | 19.54 | 28.86 | 6.33 | 1.25 | 1.26 | 5.38
2018-07-22 22:00 | 13717.9542 | -0.048233 | 29.45 | 27.49 | 18.84 | 25.43 | 4.66 | 0.12 | 2.5 | 2.62
2018-07-22 23:00 | 13388.3042 | -0.048233 | 20.66 | 25.17 | 17.2 | 22.87 | 2.27 | 0.12 | 2.5 | 1
2018-07-23 | 14670.7791 | -0.048233 | 20.2 | 23.7 | 15.84 | 21.48 | 1.46 | 0.17 | 3.46 | 1
2018-07-23 01:00 | 14467.1641 | -0.048233 | 18.98 | 22.75 | 11.35 | 20.43 | 1.15 | 0.17 | 2.61 | 0.95
2018-07-23 02:00 | 12996.9042 | -0.048233 | 18.26 | 21.73 | 10.33 | 19.9 | 1 | 0.82 | 2.99 | 0.95
2018-07-23 03:00 | 14568.4441 | -0.048233 | 18.02 | 21.38 | 6.69 | 19.11 | 1 | 0.76 | 2.36 | 0.95
2018-07-23 04:00 | 13048.2042 | -0.048233 | 17.67 | 21.4 | 6.76 | 18.63 | 1 | 0.75 | 1 | 0.95
2018-07-23 05:00 | 12920.9042 | -0.048233 | 17.14 | 21.2 | 10.92 | 18.7 | 1 | 0.76 | 2.11 | 1
2018-07-23 06:00 | 12999.4641 | 46.6464 | 17.11 | 21.18 | 15.36 | 19.18 | 1 | 1 | 2 | 1.5
2018-07-23 07:00 | 13009.2686 | 200.967 | 16.89 | 21.11 | 16.28 | 19.53 | 1 | 0.99 | 2.61 | 1.5
2018-07-23 08:00 | 14472.5723 | 353.078 | 19.04 | 21.55 | 16.23 | 20.72 | 1.01 | 1 | 3.42 | 1.5
2018-07-23 09:00 | 13261.1231 | 354.077 | 19.94 | 21.74 | 18.33 | 23.27 | 2.3 | 1.15 | 3.01 | 2.72
2018-07-23 10:00 | 15477.3395 | 909.464 | 21.58 | 23.88 | 18.94 | 26.86 | 4.68 | 1.31 | 2.61 | 4.62
2018-07-23 11:00 | 13982.6111 | 987.538 | 28.1 | 28.1 | 20.02 | 31.39 | 13.25 | 7.6 | 2 | 12.4
2018-07-23 12:00 | 15736.2724 | 945.898 | 31.34 | 31.34 | 20.38 | 37.36 | 18.09 | 14.36 | 1.17 | 15.56
2018-07-23 13:00 | 14324.4439 | 892.362 | 42.99 | 33.97 | 23.06 | 43.15 | 21.33 | 15.58 | 1 | 18.58
2018-07-23 14:00 | 14324.4116 | 914.328 | 43.07 | 42.92 | 24.88 | 54.02 | 32.4 | 19.9 | 2 | 28.31
2018-07-23 15:00 | 14095.8805 | 654.769 | 47.94 | 46.54 | 30.48 | 72.99 | 46.47 | 27.97 | 2.11 | 41.66
2018-07-23 16:00 | 15805.8095 | 527.81 | 50.18 | 43.21 | 31.21 | 62.8 | 89.8041 | 57.1573 | 2 | 87.1062
2018-07-23 17:00 | 13964.5943 | 243.573 | 46.6 | 33.69 | 29.33 | 43.62 | 37.29 | 20.48 | 2 | 34.24
2018-07-23 18:00 | 13746.1575 | 66.6395 | 40.27 | 32.05 | 24.2 | 36.08 | 21.57 | 10.65 | 2.11 | 16.97
2018-07-23 19:00 | 13714.3227 | 1.1291 | 36.91 | 30.1 | 20.3 | 36.28 | 17.3 | 0.99 | 2.11 | 12.01
2018-07-23 20:00 | 13782.5542 | -0.048233 | 49.38 | 27.46 | 20.75 | 32.57 | 11.89 | 0.99 | 2.21 | 5.63
2018-07-23 21:00 | 13757.8542 | -0.048233 | 29.09 | 27.8 | 19.97 | 31.66 | 8.87 | 1.25 | 7.5 | 7.87
2018-07-23 22:00 | 13653.3542 | -0.048233 | 23.23 | 23.23 | 16.56 | 25.94 | 5.08 | 0.17 | 2 | 2.21
2018-07-23 23:00 | 15162.4091 | -0.048233 | 20.22 | 24.93 | 16.45 | 23.32 | 2.46 | 0.17 | 3.46 | 1
2018-07-24 | 15172.9591 | -0.048233 | 19.67 | 22.01 | 15 | 21.04 | 1.11 | 0.12 | 3.01 | 0.95
2018-07-24 01:00 | 13529.8542 | -0.048233 | 18.7 | 21.99 | 13.71 | 20.24 | 1 | 0.12 | 3.11 | 0.95
2018-07-24 02:00 | 13299.9542 | -0.048233 | 18.34 | 21.21 | 12.34 | 19.87 | 1 | 0.76 | 2.82 | 0.95
2018-07-24 03:00 | 14731.9691 | -0.048233 | 17.62 | 20.39 | 11.15 | 19.71 | 1 | 0.75 | 2.37 | 0.95
2018-07-24 04:00 | 13793.0042 | -0.048233 | 17.11 | 20.81 | 11.05 | 19.26 | 1 | 0.7 | 2 | 0.95
2018-07-24 05:00 | 14841.8042 | -0.048233 | 17.29 | 21.79 | 11.56 | 19.91 | 1 | 0.7 | 1.99 | 0.95
2018-07-24 06:00 | 18062.1696 | 47.5399 | 17.5 | 22.12 | 12.56 | 21.17 | 1 | 0.99 | 2.18 | 1.5
2018-07-24 07:00 | 17024.9538 | 173.004 | 17.37 | 22.01 | 14.58 | 21.11 | 1.65 | 1 | 0.82 | 1.5
2018-07-24 08:00 | 19862.2307 | 282.759 | 19.49 | 21.83 | 16.26 | 22.99 | 2 | 1 | 0.71 | 2
2018-07-24 09:00 | 20489.1698 | 298.014 | 20.1 | 21.51 | 18.5 | 26.44 | 2.49 | 0.99 | 0.81 | 3.09
2018-07-24 10:00 | 18880.7873 | 532.513 | 20.82 | 21.68 | 20.12 | 31.2 | 4.49 | 1.45 | 2 | 5
2018-07-24 11:00 | 20294.2775 | 627.282 | 28.91 | 26.57 | 20.29 | 36.41 | 8.99 | 10.25 | 1.22 | 11.6
2018-07-24 12:00 | 19431.6069 | 931.323 | 32.28 | 28.94 | 20.31 | 41.52 | 16.84 | 13.1 | 1 | 15.84
2018-07-24 13:00 | 22274.1939 | 1084.98 | 42.88 | 31.14 | 20.72 | 55.39 | 24.61 | 17.63 | 1 | 20.63
2018-07-24 14:00 | 20400.1963 | 857.679 | 55.42 | 33.93 | 20.31 | 67.25 | 36.72 | 21.71 | 1.32 | 31.14
2018-07-24 15:00 | 19097.2661 | 766.674 | 140.12 | 33.43 | 22.91 | 72.9 | 459.1078 | 418.5316 | 1 | 99.6262
2018-07-24 16:00 | 18260.8262 | 542.84 | 352.6457 | 34.71 | 22.96 | 59.46 | 470.3478 | 434.0216 | 2 | 451.4006
2018-07-24 17:00 | 17551.5212 | 262.513 | 80.07 | 31.9 | 22.92 | 44.7 | 89.3241 | 76.7473 | 2.11 | 82.7562
2018-07-24 18:00 | 15495.4586 | 66.0091 | 35.61 | 30.3 | 23.31 | 36.35 | 27.69 | 14.26 | 2.11 | 21.47
2018-07-24 19:00 | 15322.6727 | 1.1291 | 33.77 | 26.67 | 18.93 | 33.7 | 15.67 | 10.88 | 2.11 | 4
2018-07-24 20:00 | 15327.2542 | -0.048233 | 29.86 | 24.54 | 19.66 | 32.94 | 13.18 | 1.14 | 2.11 | 5.3
2018-07-24 21:00 | 16865.1791 | -0.048233 | 30.83 | 25.71 | 18.08 | 29.23 | 6.75 | 1.15 | 8.61 | 5.79
2018-07-24 22:00 | 14648.9542 | -0.048233 | 23.6 | 23.6 | 13.87 | 26.24 | 4.54 | 0.17 | 2 | 2.21
2018-07-24 23:00 | 14287.9542 | -0.048233 | 21.79 | 22.28 | 14.51 | 23.36 | 1.81 | 0.12 | 4 | 1
2018-07-25 | 14111.2542 | -0.048233 | 20.3 | 21.18 | 15.6 | 21.29 | 1.49 | 0.12 | 4 | 1
2018-07-25 01:00 | 14019.1042 | -0.048233 | 19.5 | 21.13 | 13.35 | 20.5 | 1.01 | 0.12 | 2.61 | 0.95
2018-07-25 02:00 | 13794.9042 | -0.048233 | 18.9 | 19.98 | 11.1 | 19.75 | 1 | 0.75 | 2.61 | 0.95
2018-07-25 03:00 | 13745.5042 | -0.048233 | 18.2 | 18.79 | 10.39 | 19.05 | 1 | 0.7 | 2.11 | 0.95
2018-07-25 04:00 | 16258.5541 | -0.048233 | 17.44 | 18.41 | 10.38 | 18.76 | 1 | 0.7 | 1 | 0.95
2018-07-25 05:00 | 15727.2042 | -0.048233 | 16.96 | 19 | 9.08 | 19.42 | 1 | 0.75 | 1 | 0.95
2018-07-25 06:00 | 17322.4266 | 41.1333 | 17.75 | 20.57 | 9.99 | 20.1 | 1.01 | 1 | 1 | 1.5
2018-07-25 07:00 | 20287.9865 | 225.319 | 17.7 | 20.6 | 11.19 | 20.09 | 1.01 | 1 | 1.25 | 1.64
2018-07-25 08:00 | 19004.3234 | 470.551 | 19.33 | 21.16 | 14.39 | 21.89 | 2.01 | 1.15 | 3.01 | 2.11
2018-07-25 09:00 | 20468.776 | 765.08 | 20.39 | 21.35 | 16.41 | 24.11 | 3.28 | 1.23 | 2.24 | 2.97
2018-07-25 10:00 | 20238.7136 | 952.909 | 22.93 | 22.93 | 17.95 | 28.15 | 5.97 | 1.21 | 2.11 | 5.04
2018-07-25 11:00 | 21939.0942 | 1003.35 | 29.53 | 26.04 | 34.44 | 33.86 | 15.15 | 9.86 | 1.09 | 12.26
2018-07-25 12:00 | 23964.5321 | 1105.13 | 39.71 | 28.57 | 35.71 | 38.99 | 20.5 | 9.96 | 1.36 | 15.99
2018-07-25 13:00 | 20020.5755 | 1006.29 | 67.26 | 32.71 | 41.82 | 47.31 | 31.04 | 20.45 | 1 | 27.26
2018-07-25 14:00 | 21156.6693 | 978.715 | 170.31 | 33.46 | 45.55 | 52.24 | 34.68 | 23.71 | 1.56 | 26.11
2018-07-25 15:00 | 20008.2797 | 832.194 | 66.94 | 36.8 | 45.08 | 64.02 | 120.1341 | 82.5273 | 1.63 | 88.5362
2018-07-25 16:00 | 19089.7186 | 576.52 | 84.55 | 38.04 | 42.66 | 59.61 | 460.3478 | 90.8073 | 1.37 | 100.1162
2018-07-25 17:00 | 16405.2992 | 297.736 | 58.33 | 31.98 | 40.48 | 43.25 | 86.4141 | 68.2473 | 2.14 | 81.7162
2018-07-25 18:00 | 15887.3395 | 54.5153 | 55.09 | 30.9 | 38.14 | 35.04 | 22.55 | 14.04 | 2.61 | 18.55
2018-07-25 19:00 | 17507.8613 | 1.1292 | 31.28 | 27.01 | 36.37 | 33.61 | 9.18 | 1.24 | 2.31 | 4.69
2018-07-25 20:00 | 17498.1791 | -0.048233 | 28.17 | 27.38 | 34.88 | 31.36 | 8.55 | 1.23 | 2.31 | 5
2018-07-25 21:00 | 17256.5841 | -0.048233 | 29.15 | 29.15 | 18.19 | 28.63 | 6.56 | 1.3 | 4 | 4.62
2018-07-25 22:00 | 15103.0542 | -0.048233 | 21.83 | 23.16 | 13.9 | 25.61 | 5 | 0.12 | 2.11 | 2.21
2018-07-25 23:00 | 14471.3042 | -0.048233 | 20.11 | 23.01 | 15.6 | 23.45 | 2.2 | 0.12 | 3.15 | 1
2018-07-26 | 13966.8542 | -0.048233 | 19.18 | 20.66 | 14.09 | 19.87 | 1.2 | 0.12 | 3.98 | 1
2018-07-26 01:00 | 15169.7941 | -0.048233 | 18.25 | 20.71 | 11 | 18.9 | 1.05 | 0.12 | 3.95 | 0.95
2018-07-26 02:00 | 13695.1542 | -0.048233 | 18.17 | 19.18 | 10.16 | 18.17 | 1 | 0.7 | 3.11 | 0.95
2018-07-26 03:00 | 14786.8291 | -0.048233 | 18.19 | 18.19 | 9.69 | 18.1 | 1 | 0.7 | 2.61 | 0.95
2018-07-26 04:00 | 15573.8591 | -0.048233 | 18.04 | 18.13 | 9.66 | 18.2 | 1 | 0.7 | 2 | 0.95
2018-07-26 05:00 | 17048.7491 | -0.048233 | 17.71 | 18.79 | 11.94 | 19.38 | 1.15 | 0.7 | 14.9 | 1
2018-07-26 06:00 | 18951.3608 | 47.3752 | 17.96 | 20.25 | 12.06 | 20.45 | 1.05 | 0.99 | 2.24 | 2.1
2018-07-26 07:00 | 19698.5454 | 193.607 | 17.81 | 20.44 | 13.14 | 20.93 | 1.65 | 0.99 | 2.61 | 2
2018-07-26 08:00 | 18132.8181 | 484.177 | 19.44 | 21.4 | 15.05 | 21.49 | 2.11 | 0.99 | 3.5 | 2.19
2018-07-26 09:00 | 20725.5214 | 573.044 | 19.4 | 19.4 | 16.39 | 22.62 | 3 | 1.09 | 2.89 | 3
2018-07-26 10:00 | 19286.6521 | 915.739 | 21.02 | 21.02 | 17.32 | 25.67 | 3.99 | 1.3 | 0.71 | 3.44
2018-07-26 11:00 | 19270.7272 | 853.976 | 29.53 | 22.3 | 32.58 | 32.25 | 7.82 | 7.36 | 2.11 | 11.38
2018-07-26 12:00 | 19591.3655 | 1072.49 | 33.75 | 26.1 | 38.04 | 34.61 | 13.35 | 9.37 | 1 | 12.83
2018-07-26 13:00 | 21632.0914 | 730.352 | 36.3 | 29.14 | 38.89 | 40.5 | 23 | 19 | 1 | 20.8
2018-07-26 14:00 | 18362.8141 | 491.278 | 52.26 | 31.72 | 39.06 | 49.65 | 45 | 28.72 | 1.7 | 31.12
2018-07-26 15:00 | 17426.7686 | 657.967 | 139.5 | 33.37 | 41.32 | 55.55 | 471.9278 | 428.1016 | 2 | 108.3962
2018-07-26 16:00 | 18308.4763 | 433.006 | 136.68 | 37.97 | 44.22 | 48.82 | 496.3778 | 441.7416 | 2 | 449.5506
2018-07-26 17:00 | 17302.3017 | 233.286 | 98.18 | 35.45 | 40.13 | 37.58 | 104.9141 | 73.9673 | 2.11 | 82.2162
2018-07-26 18:00 | 14942.5736 | 68.0248 | 54.05 | 30.63 | 38.25 | 33.5 | 25 | 18.64 | 2 | 18.64
2018-07-26 19:00 | 16501.3816 | 1.12 | 32.06 | 29.53 | 35.67 | 31.67 | 14.3 | 10.89 | 1.5 | 4.66
2018-07-26 20:00 | 16530.7441 | -0.048233 | 29.72 | 27.17 | 31.89 | 29.71 | 8.29 | 1.03 | 2.61 | 5.53
2018-07-26 21:00 | 16298.6441 | -0.048233 | 28.78 | 27.4 | 18.8 | 27.35 | 6.3 | 1.14 | 2.11 | 3.24
2018-07-26 22:00 | 15870.3141 | -0.048233 | 21.67 | 22.08 | 17.05 | 25.27 | 3.92 | 0.12 | 2.64 | 2.29
2018-07-26 23:00 | 15590.7391 | -0.048233 | 20.27 | 21.53 | 16.48 | 22.81 | 1.79 | 0.12 | 3.58 | 1.95
2018-07-27 | 15482.0741 | -0.048233 | 19.23 | 19.23 | 13.23 | 20.01 | 1 | 0.12 | 11.79 | 1.61
2018-07-27 01:00 | 15214.1041 | -0.048233 | 18.89 | 18.89 | 12.39 | 18.88 | 1 | 0.12 | 1.54 | 1.11
2018-07-27 02:00 | 13496.6042 | -0.048233 | 18.2 | 18.2 | 11.27 | 18.08 | 1 | 0.7 | 3.44 | 1
2018-07-27 03:00 | 13261.9542 | -0.048233 | 16.98 | 16.98 | 11.16 | 17.99 | 1 | 0.7 | 2.21 | 1
2018-07-27 04:00 | 15601.2891 | -0.048233 | 16.93 | 16.93 | 12.14 | 18.04 | 1 | 0.7 | 1 | 1.25
2018-07-27 05:00 | 16989.6691 | -0.048233 | 17.45 | 17.45 | 12.16 | 18.84 | 1 | 0.7 | 2.61 | 2.09
2018-07-27 06:00 | 18769.2162 | 40.7263 | 18.53 | 18.53 | 15.44 | 21.33 | 1 | 0.99 | 1.6 | 2.15
2018-07-27 07:00 | 19356.8488 | 190.724 | 18.96 | 19.04 | 17.05 | 21.35 | 1.01 | 0.99 | 0.61 | 2
2018-07-27 08:00 | 20376.9779 | 388.671 | 20.41 | 20.7 | 16.65 | 22.65 | 1.51 | 0.99 | 0.51 | 2.11
2018-07-27 09:00 | 19455.3226 | 750.287 | 20.65 | 21.8 | 17.96 | 26.01 | 3.69 | 0.99 | 3.01 | 3.79
2018-07-27 10:00 | 20317.4239 | 725.762 | 21.72 | 26.77 | 19.09 | 31.93 | 7.34 | 0.99 | 2.61 | 6.34
2018-07-27 11:00 | 18730.6731 | 905.498 | 28.25 | 27.63 | 24.25 | 36.19 | 9.51 | 7.11 | 2 | 11.31
2018-07-27 12:00 | 20593.1738 | 915.025 | 31.47 | 31.47 | 32.14 | 40.48 | 16.64 | 14.59 | 1 | 14.94
2018-07-27 13:00 | 22591.4039 | 985.653 | 34.11 | 34.11 | 33.67 | 48.87 | 29.8 | 23.89 | 1 | 24.49
2018-07-27 14:00 | 20841.736 | 1013.2 | 37.43 | 37.43 | 35.29 | 65.38 | 41.2 | 54.0273 | 1.41 | 34.92
2018-07-27 15:00 | 18890.6464 | 830.826 | 42.18 | 42.18 | 35.51 | 83.44 | 488.3478 | 429.6916 | 1.98 | 100.4962
2018-07-27 16:00 | 16081.4879 | 522.882 | 42.41 | 42.41 | 34.37 | 73.02 | 510.9078 | 437.4116 | 2 | 107.2362
2018-07-27 17:00 | 15219.7077 | 193.745 | 36.97 | 36.97 | 33.62 | 49.62 | 117.7641 | 67.7573 | 2.11 | 46.74
2018-07-27 18:00 | 14835.0068 | 74.7966 | 33.37 | 33.37 | 31.55 | 41.15 | 35.57 | 19.91 | 2.21 | 20.26
2018-07-27 19:00 | 16400.1017 | 1.12 | 31.43 | 31.43 | 23.48 | 37.94 | 13.62 | 12.66 | 2.11 | 11.86
2018-07-27 20:00 | 16484.3241 | -0.048233 | 29.06 | 29.06 | 22.91 | 34.24 | 8.24 | 1.18 | 2.21 | 5.24
2018-07-27 21:00 | 14816.1542 | -0.048233 | 30.44 | 30.44 | 19.78 | 34.3 | 6.72 | 0.99 | 8.61 | 4.7
2018-07-27 22:00 | 14409.5542 | -0.048233 | 21.07 | 26.44 | 17.54 | 26.74 | 3.92 | 0.12 | 3.85 | 5
2018-07-27 23:00 | 13882.3042 | -0.048233 | 19.39 | 21.74 | 17.34 | 23.28 | 1.39 | 0.12 | 8.61 | 2.61
2018-07-28 | 13569.7542 | -0.048233 | 18.47 | 20.95 | 15.79 | 20.91 | 1.01 | 0.12 | 2.99 | 2.11
2018-07-28 01:00 | 15004.1591 | -0.048233 | 18.26 | 19.27 | 14.02 | 20.14 | 1 | 0.12 | 1.95 | 1.25
2018-07-28 02:00 | 13294.2542 | -0.048233 | 17.74 | 18.41 | 13.62 | 19.09 | 1 | 0.7 | 2.61 | 1
2018-07-28 03:00 | 13183.1042 | -0.048233 | 17.06 | 17.48 | 13.11 | 18.32 | 1 | 0.7 | 2.11 | 1
2018-07-28 04:00 | 15804.9041 | -0.048233 | 17.25 | 17.26 | 13.1 | 18.54 | 1 | 0.7 | 1 | 1
2018-07-28 05:00 | 15408.0042 | -0.048233 | 17.44 | 17.44 | 13.51 | 19.28 | 1 | 0.7 | 1 | 1.35
2018-07-28 06:00 | 18867.0534 | 44.4629 | 18.17 | 18.45 | 15.97 | 20.09 | 1 | 0.97 | 1 | 2
2018-07-28 07:00 | 17504.5033 | 214.793 | 18.48 | 18.77 | 16.56 | 20.64 | 1.05 | 0.97 | 0.73 | 2
2018-07-28 08:00 | 18007.572 | 429.339 | 20.02 | 20.57 | 16.8 | 22.25 | 2 | 0.97 | 0.51 | 2.11
2018-07-28 09:00 | 20969.2053 | 528.024 | 21.22 | 21.27 | 17.51 | 27.08 | 3 | 0.97 | 0.71 | 3
2018-07-28 10:00 | 21824.3714 | 928.608 | 22.44 | 25.05 | 22.14 | 34.1 | 6 | 0.99 | 2 | 5.12
2018-07-28 11:00 | 19106.267 | 1012.86 | 29.58 | 29.58 | 25.15 | 42.83 | 15.66 | 3 | 1.01 | 16.55
2018-07-28 12:00 | 20426.9238 | 959.025 | 33.81 | 33.81 | 32.37 | 50.19 | 23.35 | 8.1 | 1 | 20.3
2018-07-28 13:00 | 18973.4257 | 915.027 | 35.63 | 35.63 | 35.05 | 90.41 | 80.2341 | 11.72 | 0.92 | 45.06
2018-07-28 14:00 | 17960.0597 | 860.326 | 59.56 | 59.56 | 36.89 | 172.6 | 470.1478 | 437.2116 | 1 | 440.4906
2018-07-28 15:00 | 18249.0429 | 431.671 | 137.65 | 72.12 | 34.8 | 276.3 | 574.6578 | 504.0216 | 2 | 540.8306
2018-07-28 16:00 | 17696.1427 | 326.595 | 80.91 | 80.91 | 34.63 | 217.91 | 525.8778 | 494.0716 | 1.85 | 508.1506
2018-07-28 17:00 | 15453.6861 | 206.038 | 64.02 | 64.02 | 32.71 | 66.47 | 96.5741 | 56.9073 | 2 | 40.8
2018-07-28 18:00 | 15096.4139 | 58.962 | 43.71 | 43.71 | 31.62 | 45.16 | 21.47 | 12.4 | 2.11 | 15.21
2018-07-28 19:00 | 15011.064 | 1.12 | 35.87 | 35.87 | 25.33 | 43.53 | 17.08 | 7 | 1.84 | 11.92
2018-07-28 20:00 | 14994.7542 | -0.048233 | 33.49 | 33.49 | 24.42 | 36.37 | 8.77 | 0.97 | 2.21 | 3.9
2018-07-28 21:00 | 14838.0042 | -0.048233 | 31.87 | 31.87 | 22.52 | 32.37 | 6.7 | 0.97 | 8 | 5.7
2018-07-28 22:00 | 15739.4941 | -0.048233 | 20.28 | 26.95 | 16.54 | 30.07 | 5.63 | 0.17 | 10.63 | 5.63
2018-07-28 23:00 | 15105.4391 | -0.048233 | 18.78 | 24.66 | 16.89 | 24.88 | 3 | 0.12 | 7.58 | 3
2018-07-29 | 14705.5941 | -0.048233 | 17.62 | 21.47 | 17.37 | 23.32 | 2 | 0.12 | 2.99 | 1.8
2018-07-29 01:00 | 14489.3191 | -0.048233 | 16.63 | 21.6 | 16.44 | 20.82 | 1.15 | 0.12 | 2.01 | 1.11
2018-07-29 02:00 | 12996.9042 | -0.048233 | 16.4 | 20.69 | 15.18 | 20.08 | 1 | 0.71 | 2.11 | 1
2018-07-29 03:00 | 12943.7042 | -0.048233 | 15.95 | 19.45 | 14.13 | 19.38 | 1 | 0.61 | 2 | 1
2018-07-29 04:00 | 14787.8841 | -0.048233 | 15.76 | 18.79 | 13.29 | 18.7 | 1 | 0.61 | 1 | 1
2018-07-29 05:00 | 15367.0791 | -0.048233 | 16.58 | 18.75 | 13.35 | 19 | 1 | 0.61 | 1 | 2
2018-07-29 06:00 | 16011.5267 | 39.8026 | 17.92 | 19.45 | 13.23 | 19.29 | 1 | 0.99 | 1 | 2
2018-07-29 07:00 | 16137.4625 | 124.173 | 18.16 | 19.6 | 13.2 | 19.77 | 1 | 0.99 | 0.98 | 1.84
2018-07-29 08:00 | 15037.1871 | 458.618 | 19.12 | 20.99 | 14.83 | 20.38 | 1 | 0.99 | 0.25 | 2.21
2018-07-29 09:00 | 15357.0445 | 594.31 | 20.11 | 22.8 | 18.13 | 23.68 | 2.64 | 1.15 | 0.73 | 3.4
2018-07-29 10:00 | 17451.1348 | 878.36 | 20.82 | 27.2 | 29.52 | 26.68 | 4.59 | 2.31 | 1 | 6.21
2018-07-29 11:00 | 15804.0641 | 972.857 | 30.98 | 30.12 | 33.07 | 36.67 | 12.11 | 2 | 0.61 | 12.11
2018-07-29 12:00 | 15950.5009 | 958.001 | 35.33 | 34.5 | 34.3 | 46.5 | 20.32 | 8.38 | 1 | 20.17
2018-07-29 13:00 | 15637.3705 | 1032.39 | 54.56 | 54.56 | 37.54 | 67.84 | 31.61 | 16.36 | 1 | 30.07
2018-07-29 14:00 | 15204.6455 | 1014.89 | 54.89 | 54.89 | 40.67 | 103.48 | 53.93 | 53.3073 | 1.44 | 38.54
2018-07-29 15:00 | 16397.06 | 644.237 | 89.1 | 69.73 | 43.98 | 126.47 | 100.7541 | 81.0673 | 2 | 96.0562
2018-07-29 16:00 | 14479.2521 | 506.318 | 85.32 | 55.22 | 49.02 | 104.59 | 452.3778 | 92.1473 | 2.11 | 443.5406
2018-07-29 17:00 | 14138.9545 | 283.11 | 51.42 | 45 | 45 | 59.97 | 40.24 | 55.1873 | 2.11 | 37.58
2018-07-29 18:00 | 14043.583 | 57.719 | 37.02 | 34.31 | 36.75 | 41.43 | 21.48 | 11.86 | 2.11 | 15.48
2018-07-29 19:00 | 13918.4042 | -0.048233 | 35.1 | 32.55 | 33.78 | 35.19 | 14.21 | 8.26 | 2.11 | 6.02
2018-07-29 20:00 | 13750.2542 | -0.048233 | 35.06 | 29.57 | 16.06 | 31.67 | 8.87 | 1.25 | 2.11 | 5.82
2018-07-29 21:00 | 13552.6542 | -0.048233 | 32.12 | 30.97 | 16.01 | 29.86 | 6.08 | 0.97 | 1 | 5.5
2018-07-29 22:00 | 14693.9891 | -0.048233 | 29.98 | 26.69 | 14.37 | 28.84 | 3.93 | 0.12 | 8.61 | 4.07
2018-07-29 23:00 | 14319.4641 | -0.048233 | 20.33 | 25.37 | 14.39 | 24.61 | 2.5 | 0.12 | 2.61 | 2.7
2018-07-30 | 14172.8191 | -0.048233 | 20.29 | 22.61 | 15.49 | 23.26 | 2 | 0.17 | 3.11 | 2
2018-07-30 01:00 | 12691.0042 | -0.048233 | 19.45 | 21.69 | 15.3 | 21.34 | 1.47 | 0.17 | 2.94 | 1.76
2018-07-30 02:00 | 13944.9391 | -0.048233 | 18.26 | 21.18 | 13.24 | 20.3 | 1 | 0.75 | 2.11 | 1.11
2018-07-30 03:00 | 13519.7741 | -0.048233 | 17.11 | 21.1 | 13.05 | 19.6 | 1 | 0.75 | 1 | 1
2018-07-30 04:00 | 12048.8042 | -0.048233 | 16.79 | 20.91 | 13.06 | 18.85 | 1 | 0.75 | 1 | 1.11
2018-07-30 05:00 | 11882.5542 | -0.048233 | 17.48 | 20.62 | 12.12 | 18.89 | 1 | 0.75 | 1 | 2
2018-07-30 06:00 | 11820.8649 | 47.0157 | 18.24 | 20.45 | 12.23 | 19.55 | 1 | 0.99 | 1 | 2
2018-07-30 07:00 | 11814.6759 | 214.501 | 18.21 | 20.09 | 12.92 | 20.1 | 1 | 1 | 0.61 | 2
2018-07-30 08:00 | 13445.3736 | 392.43 | 19.86 | 21.28 | 13.66 | 21.42 | 1.15 | 1.15 | 0.25 | 2.41
2018-07-30 09:00 | 13749.5903 | 522.787 | 20.38 | 21.6 | 15.05 | 24.39 | 2.55 | 1.4 | 1 | 3
2018-07-30 10:00 | 14233.753 | 796.709 | 21.89 | 23.05 | 15.3 | 26 | 3.97 | 1.72 | 2 | 5.31
2018-07-30 11:00 | 13145.5575 | 869.429 | 33.02 | 27.94 | 30.07 | 33.32 | 8.1 | 1 | 2 | 14.02
2018-07-30 12:00 | 13020.6354 | 517.932 | 57.1 | 28.92 | 32.87 | 39.72 | 21.58 | 12 | 1.1 | 18.65
2018-07-30 13:00 | 14966.6583 | 881.406 | 59.35 | 30.21 | 35.51 | 50.42 | 44.89 | 22.25 | 1 | 42.89
2018-07-30 14:00 | 14572.1305 | 531.446 | 74.46 | 31.99 | 36.55 | 73.4 | 111.9641 | 425.0216 | 1.35 | 106.8062
2018-07-30 15:00 | 13322.3934 | 659.572 | 329.6957 | 30.67 | 36.29 | 84.86 | 478.9678 | 473.5616 | 2 | 478.8706
2018-07-30 16:00 | 12989.8373 | 266.513 | 415.0857 | 30.28 | 36.82 | 85.66 | 532.9578 | 484.0216 | 2.11 | 532.9406
2018-07-30 17:00 | 14286.2086 | 192.43 | 164.38 | 31.01 | 34.74 | 46.28 | 451.7178 | 439.0216 | 2.11 | 451.7006
2018-07-30 18:00 | 12743.8614 | 66.5909 | 74.64 | 34.13 | 30.67 | 35.99 | 36.25 | 28.87 | 2.11 | 32.05
2018-07-30 19:00 | 12531.4042 | -0.048233 | 31.13 | 30.65 | 23.61 | 31.74 | 19.48 | 9.44 | 2 | 13.34
2018-07-30 20:00 | 12711.9042 | -0.048233 | 32.38 | 30.35 | 22.62 | 30.46 | 7.31 | 1.25 | 2.11 | 5.41
2018-07-30 21:00 | 12754.6542 | -0.048233 | 30.18 | 29.33 | 16.85 | 28.03 | 5.03 | 1.24 | 3.5 | 5.02
2018-07-30 22:00 | 13935.4441 | -0.048233 | 30.16 | 26.22 | 15.47 | 26.41 | 3.28 | 0.17 | 12.07 | 4.21
2018-07-30 23:00 | 13709.6741 | -0.048233 | 19.93 | 23.96 | 16 | 23.22 | 2.25 | 0.17 | 3.01 | 3
2018-07-31 | 12353.7542 | -0.048233 | 19.4 | 21.74 | 15.2 | 21.73 | 1.36 | 0.17 | 2.39 | 2.01
2018-07-31 01:00 | 12294.8542 | -0.048233 | 19.2 | 21.15 | 13.02 | 20.47 | 1.01 | 0.17 | 1.32 | 1.25
2018-07-31 02:00 | 13386.8441 | -0.048233 | 17.79 | 20.41 | 12.9 | 19.65 | 1 | 0.75 | 0.71 | 1.03
2018-07-31 03:00 | 12141.9042 | -0.048233 | 17.09 | 19.9 | 11.99 | 19.04 | 1 | 0.75 | 2.11 | 1
2018-07-31 04:00 | 14392.2591 | -0.048233 | 16.56 | 19.86 | 12.3 | 19.32 | 1 | 0.75 | 1 | 1
2018-07-31 05:00 | 15495.7891 | -0.048233 | 16.22 | 20.49 | 12.98 | 19.65 | 1 | 0.75 | 1 | 2
2018-07-31 06:00 | 17857.6897 | 43.7201 | 15.24 | 21.07 | 14 | 21.56 | 1 | 0.99 | 1.07 | 2
2018-07-31 07:00 | 19619.0997 | 134.303 | 15.25 | 21 | 14.17 | 21.96 | 1.17 | 0.99 | 2 | 1.7
2018-07-31 08:00 | 18169.5575 | 228.85 | 17.58 | 21.33 | 15.55 | 24.37 | 2 | 1.26 | 0.51 | 2
2018-07-31 09:00 | 20502.7044 | 278.843 | 38.13 | 22.35 | 18.44 | 25.62 | 2.67 | 1.19 | 2 | 3
2018-07-31 10:00 | 20518.4597 | 345.777 | 18.75 | 27.26 | 19.06 | 30.49 | 3.93 | 1.59 | 2 | 5
2018-07-31 11:00 | 18666.2688 | 314.704 | 30.73 | 28.93 | 19.55 | 34.65 | 7.21 | 1 | 1 | 10.3
2018-07-31 12:00 | 21885.7503 | 327.787 | 42.5 | 31.54 | 20.03 | 43.29 | 17.39 | 9.83 | 1 | 15.39
2018-07-31 13:00 | 20117.9942 | 315.836 | 43.59 | 33.36 | 19.8 | 55.05 | 35 | 27.14 | 1 | 30.4
2018-07-31 14:00 | 17554.3717 | 522.286 | 58.76 | 40.73 | 19.38 | 78.21 | 47.39 | 59.8773 | 1 | 40.77
2018-07-31 15:00 | 16391.3617 | 511.065 | 115.37 | 48.08 | 20.02 | 83.08 | 116.3541 | 426.6816 | 1.7 | 107.7762
2018-07-31 16:00 | 15788.9535 | 247.951 | 86.93 | 86.93 | 22.33 | 83.7 | 457.9178 | 444.3016 | 2.09 | 446.5906
2018-07-31 17:00 | 17004.7675 | 147.263 | 45.2 | 45.2 | 21.96 | 49.89 | 42.81 | 58.3573 | 1.86 | 38.55
2018-07-31 18:00 | 14754.0313 | 60.5593 | 38.26 | 38.26 | 20.74 | 37.49 | 23.18 | 17.58 | 2 | 18.33
2018-07-31 19:00 | 14687.9042 | -0.048233 | 37.19 | 37.19 | 20.05 | 33.8 | 13.19 | 1.14 | 2.11 | 5.11
2018-07-31 20:00 | 14674.6042 | -0.048233 | 35.49 | 35.49 | 21.42 | 32.5 | 7.98 | 1.23 | 2.21 | 5.45
2018-07-31 21:00 | 16271.2141 | -0.048233 | 30.6 | 30.6 | 19.54 | 30.65 | 5.47 | 1.2 | 3.98 | 4.88
2018-07-31 22:00 | 15815.4541 | -0.048233 | 22.5 | 27.86 | 18.03 | 25.78 | 3.45 | 0.17 | 9.2 | 4
2018-07-31 23:00 | 13768.3042 | -0.048233 | 19.49 | 24.66 | 17.42 | 23.35 | 2.21 | 0.17 | 2.11 | 2.61
2018-08-01 | 13382.6042 | -0.048233 | 18.58 | 21.49 | 16.94 | 21.22 | 1.65 | 0.01 | 3.27 | 2.5
2018-08-01 01:00 | 14543.1241 | -0.048233 | 17.18 | 20.83 | 15.18 | 19.88 | 1 | 0.01 | 1.4 | 1.3
2018-08-01 02:00 | 14362.7191 | -0.048233 | 15.88 | 20.02 | 15 | 18.82 | 1 | 0.5 | 1.87 | 1
2018-08-01 03:00 | 14194.9741 | -0.048233 | 15 | 19.41 | 13.99 | 18.21 | 1 | 0.5 | 1 | 1
2018-08-01 04:00 | 14760.4541 | -0.048233 | 15.43 | 18.78 | 13.4 | 18.02 | 1 | 0.5 | 1 | 1
2018-08-01 05:00 | 14111.2542 | -0.048233 | 16.21 | 19.67 | 13.33 | 18.88 | 1 | 0.5 | 1 | 1.25
2018-08-01 06:00 | 15605.1965 | 29.5226 | 17.52 | 21.08 | 14.5 | 20.81 | 1 | 1 | 2.11 | 1.85
2018-08-01 07:00 | 16555.3023 | 244.634 | 17.92 | 21.34 | 16 | 21.43 | 1 | 1 | 2.61 | 1.61
2018-08-01 08:00 | 18916.0276 | 388.884 | 19.13 | 23.98 | 16.41 | 23.06 | 2 | 1 | 2.11 | 2
2018-08-01 09:00 | 17762.6659 | 724.543 | 39.38 | 39.38 | 17.97 | 25.23 | 3.11 | 1.1 | 2.59 | 3.11
2018-08-01 10:00 | 20099.803 | 886.946 | 20.41 | 31.68 | 18.27 | 29.02 | 4.82 | 2 | 1 | 5.87
2018-08-01 11:00 | 20094.5639 | 1096.98 | 29.23 | 29.23 | 20.11 | 33.8 | 7.36 | 1.56 | 1 | 9.97
2018-08-01 12:00 | 18520.8599 | 969.642 | 30.09 | 30.09 | 20.39 | 37.9 | 13.61 | 9.53 | 1 | 12.54
2018-08-01 13:00 | 20799.1752 | 933.858 | 31.45 | 31.45 | 21.89 | 44.8 | 24.51 | 14.3 | 1.53 | 18.61
2018-08-01 14:00 | 17691.3009 | 851.422 | 33.44 | 33.44 | 22.3 | 57.71 | 33.88 | 17.63 | 1.65 | 25.57
2018-08-01 15:00 | 16434.3663 | 346.333 | 40.04 | 40.04 | 22.33 | 62.21 | 53.15 | 59.9473 | 1.6 | 43.31
2018-08-01 16:00 | 17631.812 | 469.618 | 33.28 | 32.61 | 28.85 | 53.63 | 89.0141 | 69.8573 | 2 | 78.8962
2018-08-01 17:00 | 16815.5078 | 114.87 | 32.45 | 32.45 | 24.98 | 39.8 | 37.02 | 28.54 | 2.31 | 31.84
2018-08-01 18:00 | 16512.8229 | 40.9648 | 31.17 | 31.17 | 20.36 | 33.27 | 20.95 | 10 | 2.21 | 13.98
2018-08-01 19:00 | 16334.5141 | -0.048233 | 30.95 | 30.95 | 20.25 | 31.71 | 7.86 | 1.36 | 2.31 | 7.86
2018-08-01 20:00 | 16347.1741 | -0.048233 | 31.63 | 31.63 | 19.74 | 30.22 | 7.12 | 0.97 | 2.11 | 6.61
2018-08-01 21:00 | 14626.1542 | -0.048233 | 30.09 | 30.09 | 20.24 | 28.25 | 5.22 | 0.97 | 4 | 5.24
2018-08-01 22:00 | 14112.2042 | -0.048233 | 41.43 | 41.43 | 18.01 | 25.46 | 3.75 | 0.01 | 9.11 | 4.36
2018-08-01 23:00 | 13588.7542 | -0.048233 | 22.96 | 26.35 | 16.47 | 23.16 | 1.64 | 0.01 | 3.11 | 1.64
2018-08-02 | 13335.1042 | -0.048233 | 19.02 | 22.59 | 15.82 | 21.77 | 1.75 | 0.12 | 2.61 | 2
2018-08-02 01:00 | 13225.8542 | -0.048233 | 17.87 | 21.3 | 13.45 | 20.21 | 1.01 | 0.01 | 2.61 | 1.11
2018-08-02 02:00 | 13057.7042 | -0.048233 | 17.81 | 20.51 | 12.39 | 19.66 | 1 | 0.5 | 2.11 | 1
2018-08-02 03:00 | 13011.1542 | -0.048233 | 16.5 | 20.13 | 10.67 | 19.17 | 1 | 0.5 | 2 | 1.2
2018-08-02 04:00 | 13642.9042 | -0.048233 | 16.41 | 20.13 | 9.81 | 19.03 | 1 | 0.5 | 1 | 1
2018-08-02 05:00 | 14544.4542 | -0.048233 | 16.82 | 20.55 | 9.76 | 19.44 | 1 | 0.5 | 1 | 1.25
2018-08-02 06:00 | 16802.1956 | 29.5217 | 16.4 | 21.18 | 10.68 | 23.09 | 1 | 0.99 | 2 | 2
2018-08-02 07:00 | 17388.4751 | 209.658 | 15.96 | 21.01 | 10.56 | 23.57 | 1 | 0.99 | 2.09 | 1.98
2018-08-02 08:00 | 20438.7492 | 502.222 | 18.15 | 21.12 | 14.86 | 25.24 | 2 | 1 | 2.11 | 2
2018-08-02 09:00 | 21963.9026 | 490.865 | 19.89 | 22.62 | 16.43 | 27.41 | 2.75 | 1 | 2.17 | 3
2018-08-02 10:00 | 18694.2615 | 667.17 | 20.74 | 25.05 | 17.08 | 29.95 | 3.74 | 2.5 | 0.51 | 3.74
2018-08-02 11:00 | 19221.8345 | 1045.51 | 316.8957 | 272.57 | 18.44 | 34.75 | 6.5 | 1.22 | 1 | 6.3
2018-08-02 12:00 | 19990.5175 | 1158.65 | 32.14 | 25.89 | 29.83 | 38.64 | 14.23 | 9.28 | 1 | 13.96
2018-08-02 13:00 | 19818.0925 | 1094.15 | 151.68 | 151.68 | 30.64 | 46.2 | 20 | 11.78 | 1.02 | 19.04
2018-08-02 14:00 | 21765.1174 | 973.443 | 754.7911 | 26.99 | 32.05 | 52.39 | 29.49 | 18.34 | 1.69 | 23.72
2018-08-02 15:00 | 17014.7346 | 861.247 | 831.8011 | 27.45 | 34.05 | 58.69 | 81.2541 | 64.4473 | 1.8 | 50
2018-08-02 16:00 | 16113.1694 | 597.231 | 334.1857 | 26.75 | 34.32 | 56.61 | 94.7841 | 77.6173 | 2.11 | 85.7162
2018-08-02 17:00 | 15529.4894 | 284.831 | 107.67 | 24.5 | 34.14 | 36.94 | 36.73 | 29.15 | 2.27 | 32.73
2018-08-02 18:00 | 16909.8221 | 48.2674 | 32.94 | 23.77 | 29.96 | 31.9 | 18.92 | 10 | 2.11 | 14.37
2018-08-02 19:00 | 16585.6041 | -0.048233 | 41.75 | 21.69 | 20.84 | 30.69 | 7.31 | 1.32 | 2.11 | 10.42
2018-08-02 20:00 | 16521.2491 | -0.048233 | 29.03 | 22.79 | 21.03 | 30.23 | 6.62 | 1.22 | 2 | 5.78
2018-08-02 21:00 | 14726.8542 | -0.048233 | 30.92 | 21.71 | 20.2 | 29.51 | 6.25 | 1.21 | 4.63 | 5.8
2018-08-02 22:00 | 15781.6941 | -0.048233 | 21.79 | 21.79 | 19.03 | 24.42 | 3.63 | 0.01 | 21.4 | 4
2018-08-02 23:00 | 15188.7841 | -0.048233 | 20.72 | 20.72 | 17.2 | 22.55 | 2 | 0.01 | 3.01 | 2
2018-08-03 | 14931.3641 | -0.048233 | 19.56 | 19.63 | 16.87 | 19.5 | 1 | 0.01 | 3.5 | 1.6
2018-08-03 01:00 | 14769.9491 | -0.048233 | 18.55 | 19 | 16.62 | 18.49 | 1 | 0.01 | 2.61 | 1.11
2018-08-03 02:00 | 13247.7042 | -0.048233 | 17.82 | 18.56 | 16.43 | 17.87 | 1 | 0.5 | 2.11 | 1
2018-08-03 03:00 | 14861.7341 | -0.048233 | 17.06 | 18.21 | 13.34 | 17.48 | 1 | 0.5 | 1.02 | 1
2018-08-03 04:00 | 15870.3141 | -0.048233 | 16.95 | 18.19 | 13.53 | 17.46 | 1 | 0.5 | 1 | 1
2018-08-03 05:00 | 15270.2542 | -0.048233 | 17.29 | 18.45 | 16.26 | 18.1 | 1 | 0.5 | 1 | 1.64
2018-08-03 06:00 | 17084.594 | 29.7832 | 18.72 | 19.2 | 16.6 | 19.86 | 1 | 1 | 1 | 2
2018-08-03 07:00 | 19803.4472 | 177.04 | 19.31 | 20.17 | 19.04 | 20.48 | 1.15 | 1.33 | 2.11 | 2
2018-08-03 08:00 | 18439.9294 | 528.452 | 20.45 | 21.05 | 19.95 | 22.29 | 2.2 | 1.11 | 2.61 | 2.8
2018-08-03 09:00 | 18879.7728 | 746.445 | 21.16 | 21.16 | 20.33 | 25.57 | 4 | 1.18 | 2.11 | 4.18
2018-08-03 10:00 | 19056.3825 | 1006.35 | 21.59 | 21.59 | 21.42 | 27.26 | 4.23 | 6.71 | 2 | 7.55
2018-08-03 11:00 | 21392.5409 | 1147.29 | 30.82 | 25.89 | 21.72 | 32.92 | 7.12 | 1.5 | 1 | 14.18
2018-08-03 12:00 | 19455.6675 | 1158.65 | 31.64 | 27.65 | 21.87 | 37.06 | 18.55 | 11.06 | 1 | 15.66
2018-08-03 13:00 | 19116.5175 | 1158.65 | 78.21 | 30.32 | 22.38 | 40.57 | 29.24 | 24.24 | 1 | 25.24
2018-08-03 14:00 | 19721.8324 | 1053.68 | 59 | 48.5 | 23.23 | 50.7 | 95.3441 | 26.98 | 1.41 | 86.8162
2018-08-03 15:00 | 16545.4251 | 757.237 | 187.83 | 79.65 | 30.3 | 58.2 | 104.6041 | 85.5573 | 2 | 95.0162
2018-08-03 16:00 | 17491.8029 | 576.908 | 109.66 | 42.79 | 32.56 | 66.67 | 117.8141 | 426.4916 | 2.11 | 434.8006
2018-08-03 17:00 | 15128.3206 | 287.548 | 50.64 | 50.64 | 29.82 | 39.58 | 40.74 | 54.6473 | 2.11 | 35.54
2018-08-03 18:00 | 14396.2372 | 62.9339 | 43.4 | 43.4 | 22.51 | 33.74 | 23.37 | 10 | 2.11 | 17.82
2018-08-03 19:00 | 14323.1042 | -0.048233 | 105.03 | 105.03 | 21.83 | 30.86 | 15.04 | 1.12 | 2 | 11.62
2018-08-03 20:00 | 14310.7542 | -0.048233 | 32.72 | 32.72 | 21.85 | 31.44 | 7.29 | 1.02 | 2 | 6.19
2018-08-03 21:00 | 14383.9042 | -0.048233 | 30.57 | 29.95 | 20.81 | 29.82 | 7.34 | 1.02 | 3.5 | 6.83
2018-08-03 22:00 | 14153.0542 | -0.048233 | 26.58 | 26.54 | 19.94 | 23.26 | 4 | 0.12 | 14.03 | 4
2018-08-03 23:00 | 15408.2241 | -0.048233 | 20.88 | 21.64 | 18.26 | 22.17 | 1.98 | 0.01 | 11.28 | 2.85
2018-08-04 | 13722.7042 | -0.048233 | 18.81 | 21.09 | 18.06 | 20.13 | 1 | 0.12 | 3.5 | 1.85
2018-08-04 01:00 | 13666.6542 | -0.048233 | 18.81 | 20.2 | 16.16 | 19.42 | 1 | 0.12 | 2.99 | 1
2018-08-04 02:00 | 15129.7041 | -0.048233 | 17.34 | 19.68 | 16.36 | 18.63 | 1 | 0.5 | 2.11 | 1
2018-08-04 03:00 | 13552.6542 | -0.048233 | 15.63 | 19.16 | 15.55 | 17.93 | 1 | 0.5 | 2 | 1
2018-08-04 04:00 | 14233.8042 | -0.048233 | 15.38 | 19.43 | 16 | 17.86 | 1 | 0.5 | 1 | 1
2018-08-04 05:00 | 16846.1891 | -0.048233 | 15.83 | 18.93 | 16.91 | 18.65 | 1 | 0.5 | 1 | 1.65
2018-08-04 06:00 | 18688.1143 | 40.8524 | 16.64 | 21.08 | 18.18 | 20.36 | 1 | 0.97 | 2.11 | 2
2018-08-04 07:00 | 19889.4128 | 204.524 | 17.11 | 21.16 | 19.43 | 20.7 | 1 | 1 | 2.5 | 2
2018-08-04 08:00 | 20393.1447 | 404.995 | 18.17 | 21.83 | 19.51 | 22.09 | 1.78 | 0.99 | 2.61 | 2.11
2018-08-04 09:00 | 21207.9065 | 585.281 | 19.17 | 26.62 | 20.58 | 25.02 | 3.97 | 1.15 | 2 | 3.8
2018-08-04 10:00 | 18366.5438 | 653.204 | 28.49 | 28.49 | 21.11 | 31.03 | 4.81 | 2 | 2 | 6.82
2018-08-04 11:00 | 19684.4506 | 676.247 | 30.4 | 30.4 | 21.26 | 33.91 | 7.21 | 1.25 | 1 | 13.02
2018-08-04 12:00 | 20827.6939 | 1131.89 | 32.25 | 32.25 | 22.19 | 37.48 | 20.51 | 17.04 | 1 | 19.21
2018-08-04 13:00 | 20647.4577 | 1090.05 | 33.78 | 33.1 | 22.21 | 44.92 | 39.01 | 59.6473 | 1 | 37.34
2018-08-04 14:00 | 19694.5512 | 977.821 | 47.23 | 47.23 | 23.62 | 53.11 | 496.2478 | 449.0216 | 2.11 | 493.5006
2018-08-04 15:00 | 17062.721 | 794.759 | 49.51 | 49.51 | 23.56 | 68.37 | 554.3478 | 449.0216 | 2.11 | 550.7006
2018-08-04 16:00 | 18172.4562 | 509.077 | 38.94 | 33.83 | 23.56 | 48.3 | 516.4778 | 449.0216 | 2.21 | 511.0106
2018-08-04 17:00 | 17449.2769 | 269.599 | 55.92 | 55.92 | 22.34 | 35.06 | 89.6541 | 72.6973 | 2.73 | 79.9662
2018-08-04 18:00 | 14982.1009 | 56.6325 | 33.79 | 31.61 | 21.85 | 31.34 | 24.32 | 10 | 2.21 | 18.02
2018-08-04 19:00 | 16506.4791 | -0.048233 | 36.38 | 29.51 | 20.81 | 28.95 | 15.91 | 0.97 | 1 | 11.91
2018-08-04 20:00 | 16443.1791 | -0.048233 | 29.66 | 29.58 | 21.06 | 25.66 | 5.89 | 0.97 | 2.14 | 5.95
2018-08-04 21:00 | 16409.4191 | -0.048233 | 29.05 | 29.05 | 20.77 | 26.23 | 5 | 0.97 | 3.5 | 6.51
2018-08-04 22:00 | 14458.9542 | -0.048233 | 23.19 | 23.32 | 19.14 | 23.31 | 3.61 | 0.12 | 11.81 | 4
2018-08-04 23:00 | 14077.0542 | -0.048233 | 20.76 | 21.6 | 18.19 | 21.62 | 1.51 | 0.12 | 3.98 | 2.61
2018-08-05 | 13746.4542 | -0.048233 | 18.64 | 20.31 | 17.63 | 20.97 | 1.55 | 0.12 | 10 | 1.61
2018-08-05 01:00 | 13416.8042 | -0.048233 | 18.37 | 20.2 | 16.99 | 19.97 | 1 | 0.12 | 2.11 | 1
2018-08-05 02:00 | 13411.1042 | -0.048233 | 16.96 | 18.57 | 15.05 | 18.72 | 1 | 0.5 | 2.46 | 1
2018-08-05 03:00 | 13293.3042 | -0.048233 | 16.58 | 17.68 | 14.21 | 17.67 | 1 | 0.5 | 2.61 | 1.11
2018-08-05 04:00 | 13408.2542 | -0.048233 | 16.85 | 17.22 | 13.96 | 17.32 | 1 | 0.5 | 2.21 | 1
2018-08-05 05:00 | 15396.6191 | -0.048233 | 17.1 | 17.1 | 13.94 | 17.12 | 1 | 0.5 | 2.61 | 1.25
2018-08-05 06:00 | 14394.7626 | 27.3817 | 17.49 | 17.49 | 15.02 | 19.58 | 1 | 1 | 2.11 | 2
2018-08-05 07:00 | 15929.9135 | 78.4441 | 17.4 | 17.4 | 16.34 | 19.42 | 1 | 1 | 1.77 | 2
2018-08-05 08:00 | 16833.4692 | 553.895 | 19.18 | 19.18 | 17.63 | 20.71 | 1.34 | 1.1 | 1.73 | 2
2018-08-05 09:00 | 15552.8917 | 686.465 | 20.18 | 20.18 | 20.25 | 26.63 | 1.77 | 1.08 | 2.31 | 3.6
2018-08-05 10:00 | 15771.9978 | 877.103 | 20.09 | 20.09 | 20.84 | 25.34 | 3.11 | 2 | 1 | 6
2018-08-05 11:00 | 16173.617 | 1073.86 | 29.94 | 21.33 | 21.08 | 28.64 | 4.07 | 6.57 | 1 | 14.42
2018-08-05 12:00 | 16242.644 | 1107.52 | 34.51 | 23.02 | 20.09 | 33.98 | 21.48 | 16.39 | 1 | 16.48
2018-08-05 13:00 | 15623.6468 | 603.944 | 54.21 | 25.61 | 21.02 | 39.81 | 81.9141 | 66.0773 | 1 | 49.37
2018-08-05 14:00 | 15753.4424 | 996.571 | 81.98 | 25.26 | 22.46 | 42.88 | 470.3178 | 449.0216 | 1.41 | 462.9406
2018-08-05 15:00 | 17061.3608 | 733.906 | 400.3157 | 27.51 | 22.79 | 52.14 | 536.3778 | 452.6816 | 2 | 531.8606
2018-08-05 16:00 | 14983.7876 | 527.408 | 1095.9611 | 30.07 | 23.06 | 42.55 | 500.3578 | 451.6316 | 2.11 | 493.6606
2018-08-05 17:00 | 14820.5301 | 287.558 | 244.2557 | 41.32 | 22.79 | 34.12 | 45.83 | 60.8873 | 2.32 | 38.58
2018-08-05 18:00 | 15967.5688 | 41.1363 | 127.26 | 127.26 | 21 | 29.79 | 19.91 | 8.99 | 2.21 | 12.7
2018-08-05 19:00 | 15796.4641 | -0.048233 | 38.78 | 31.01 | 20.49 | 27.96 | 15.31 | 0.97 | 2.14 | 11.51
2018-08-05 20:00 | 14126.4542 | -0.048233 | 36.51 | 31.55 | 20.6 | 27 | 4 | 0.97 | 2.09 | 4
2018-08-05 21:00 | 15554.8691 | -0.048233 | 30.72 | 25.47 | 17.66 | 25.42 | 3.07 | 0.97 | 3.5 | 5.07
2018-08-05 22:00 | 13482.3542 | -0.048233 | 27.16 | 25.99 | 16.73 | 22.77 | 3 | 0.12 | 30.82 | 4.07
2018-08-05 23:00 | 14684.4941 | -0.048233 | 21.15 | 21.15 | 15.42 | 21.62 | 1.15 | 0.12 | 30 | 2.2
2018-08-06 | 13255.3042 | -0.048233 | 19.51 | 21.68 | 15.99 | 20.12 | 1.01 | 0.01 | 15 | 2
2018-08-06 01:00 | 14692.9341 | -0.048233 | 18.61 | 22.04 | 14.64 | 18.67 | 1 | 0.01 | 3.47 | 1.11
2018-08-06 02:00 | 14721.4191 | -0.048233 | 18.01 | 19.65 | 13.21 | 17.56 | 1 | 0.45 | 3.11 | 1
2018-08-06 03:00 | 13240.1042 | -0.048233 | 17.33 | 19.05 | 12.44 | 16.86 | 1 | 0.45 | 2.56 | 1.11
2018-08-06 04:00 | 13175.5042 | -0.048233 | 17.31 | 19.75 | 11.52 | 16.71 | 1 | 0.45 | 2.21 | 1
2018-08-06 05:00 | 14739.3541 | -0.048233 | 17.07 | 20.24 | 11.43 | 16.66 | 1 | 0.45 | 2.61 | 1.41
2018-08-06 06:00 | 14985.8203 | 39.569 | 17.09 | 20.85 | 11.43 | 18.38 | 1 | 1 | 2.11 | 2
2018-08-06 07:00 | 13468.0436 | 193.888 | 17.25 | 20.27 | 13.03 | 18.39 | 1 | 1 | 2 | 2
2018-08-06 08:00 | 13891.6552 | 387.795 | 19.29 | 20.26 | 12.76 | 20.13 | 1.01 | 1.05 | 1.86 | 2
2018-08-06 09:00 | 15979.9088 | 675.833 | 19.97 | 19.97 | 14.58 | 24.68 | 2.72 | 1.18 | 2 | 3.31
2018-08-06 10:00 | 16415.3105 | 946.536 | 20.49 | 20.49 | 15.26 | 24.63 | 3 | 0.99 | 2.01 | 6
2018-08-06 11:00 | 16145.7094 | 1063.99 | 31.18 | 21.54 | 16.32 | 26.7 | 4.36 | 7.23 | 1 | 12.88
2018-08-06 12:00 | 14261.457 | 1079.06 | 40.21 | 24.26 | 16.32 | 30.18 | 23.75 | 16.64 | 1 | 21.17
2018-08-06 13:00 | 16013.4757 | 1059.65 | 39.9 | 29.28 | 16.79 | 35.92 | 45.12 | 66.3473 | 1 | 43.04
2018-08-06 14:00 | 15972.5344 | 881.843 | 197.07 | 32.84 | 17.87 | 46.92 | 453.3278 | 442.3016 | 1 | 449.3706
2018-08-06 15:00 | 14980.3809 | 791.822 | 263.3357 | 32.27 | 19.06 | 60 | 579.2078 | 574.0216 | 1.8 | 579.1906
2018-08-06 16:00 | 16241.6701 | 306.948 | 274.4657 | 42.82 | 19.34 | 62.21 | 660.0478 | 651.5116 | 2 | 660.0406
2018-08-06 17:00 | 14419.9882 | 173.935 | 101.38 | 35.62 | 21.31 | 36.99 | 449.2978 | 449.0216 | 2 | 450.6906
2018-08-06 18:00 | 15968.9265 | 54.4232 | 31.58 | 28.2 | 21.09 | 30.59 | 38.96 | 28.76 | 2.11 | 33.47
2018-08-06 19:00 | 15839.7191 | -0.048233 | 52.12 | 52.12 | 19.39 | 29.17 | 22.11 | 17.11 | 2 | 18.11
2018-08-06 20:00 | 14250.9042 | -0.048233 | 37.27 | 37.27 | 21.09 | 29.48 | 16.21 | 0.97 | 1.17 | 5.24
2018-08-06 21:00 | 15850.2691 | -0.048233 | 37.64 | 37.64 | 18.27 | 29.49 | 6 | 0.97 | 3.5 | 4.65
2018-08-06 22:00 | 15484.1841 | -0.048233 | 26.13 | 26.13 | 15.97 | 23.8 | 3.74 | 0.01 | 13.43 | 4
2018-08-06 23:00 | 15501.0641 | -0.048233 | 20.5 | 23.13 | 15.51 | 22.66 | 2.21 | 0.01 | 20 | 2.34
2018-08-07 | 15447.2591 | -0.048233 | 18.77 | 21.24 | 14.1 | 22.94 | 1.99 | 0.01 | 10 | 2
2018-08-07 01:00 | 15422.9941 | -0.048233 | 17.34 | 20.74 | 12.5 | 21.49 | 1.45 | 0.01 | 3.36 | 1.25
2018-08-07 02:00 | 15357.5841 | -0.048233 | 16.58 | 20.26 | 12.51 | 20.88 | 1.25 | 0.58 | 3.11 | 1.05
2018-08-07 03:00 | 15234.1491 | -0.048233 | 15.68 | 20.33 | 11.56 | 20.54 | 1.31 | 0.5 | 2.61 | 1.11
2018-08-07 04:00 | 14455.1542 | -0.048233 | 15.2 | 20.8 | 11.77 | 20.5 | 1.21 | 0.5 | 2.11 | 1.01
2018-08-07 05:00 | 17010.7691 | -0.048233 | 15.9 | 21.47 | 12.44 | 21.25 | 1.61 | 0.61 | 2.61 | 1.41
2018-08-07 06:00 | 19009.3472 | 30.3386 | 16.48 | 21.65 | 13.76 | 21.51 | 1.2 | 0.99 | 2.5 | 2
2018-08-07 07:00 | 18291.9773 | 236.713 | 16.46 | 21.69 | 15.46 | 22.16 | 1.2 | 0.99 | 2.61 | 2
2018-08-07 08:00 | 21034.6649 | 533.071 | 18.24 | 21.33 | 16.82 | 23.81 | 1.99 | 0.99 | 2.11 | 2
2018-08-07 09:00 | 19402.7069 | 628.902 | 18.98 | 21.05 | 18.72 | 26.62 | 2.11 | 1.25 | 2.56 | 3
2018-08-07 10:00 | 19909.6098 | 955.484 | 20.27 | 21.13 | 19.07 | 28.8 | 5.43 | 6.55 | 1.02 | 5.63
2018-08-07 11:00 | 21680.7965 | 919.518 | 22.14 | 22.14 | 19.95 | 33.12 | 7.89 | 8.21 | 1 | 10.89
2018-08-07 12:00 | 19275.8705 | 1117.39 | 29.76 | 24.16 | 20.47 | 36.2 | 19.4 | 15.75 | 1.07 | 16.37
2018-08-07 13:00 | 20804.5599 | 911.962 | 35.7 | 24.57 | 20.67 | 49.15 | 34.7 | 55.6773 | 1.6 | 29.9
2018-08-07 14:00 | 18619.7226 | 910.708 | 53.54 | 24.34 | 20.69 | 46.92 | 517.5578 | 514.4316 | 1.59 | 514.7406
2018-08-07 15:00 | 17764.3141 | 728.278 | 71.76 | 24.21 | 20.65 | 48.09 | 1006.8278 | 968.3716 | 2.11 | 972.1106
2018-08-07 16:00 | 16900.7147 | 501.226 | 122.49 | 25.64 | 21.22 | 42.1 | 1315.3878 | 1276.5716 | 2.18 | 1280.8306
2018-08-07 17:00 | 16183.4514 | 248.212 | 55.46 | 24.89 | 21.25 | 34.81 | 592.8178 | 559.9116 | 2.31 | 560.2206
2018-08-07 18:00 | 17255.1683 | 39.6098 | 63.34 | 63.34 | 20.54 | 36.44 | 43.35 | 59.2573 | 2.11 | 38.35
2018-08-07 19:00 | 17039.2541 | -0.048233 | 30.73 | 30.73 | 19.85 | 30.89 | 17.4 | 10.54 | 2 | 14.79
2018-08-07 20:00 | 15184.7542 | -0.048233 | 30.07 | 22.92 | 19.62 | 27.88 | 5.33 | 1.21 | 2 | 5.55
2018-08-07 21:00 | 16710.0941 | -0.048233 | 28.96 | 24.8 | 17.67 | 27.68 | 5.52 | 0.97 | 3.18 | 5.61
2018-08-07 22:00 | 14646.1042 | -0.048233 | 21.57 | 21.57 | 15.71 | 24.46 | 3.81 | 0.01 | 12 | 4
2018-08-07 23:00 | 14272.7542 | -0.048233 | 20.2 | 21.12 | 15.03 | 22.35 | 1.86 | 0.01 | 20 | 2.31
2018-08-08 | 14054.2542 | -0.048233 | 18.62 | 20.1 | 14.31 | 19.65 | 1 | 0.12 | 3.5 | 1.45
2018-08-08 01:00 | 15297.4491 | -0.048233 | 17.35 | 19.34 | 12.09 | 19.14 | 1 | 0.12 | 2.61 | 1
2018-08-08 02:00 | 13558.3542 | -0.048233 | 16.16 | 18.69 | 10.99 | 18.71 | 1 | 0.45 | 1 | 1
2018-08-08 03:00 | 13533.6542 | -0.048233 | 14.95 | 19.1 | 9.97 | 18.34 | 1 | 0.45 | 1 | 1
2018-08-08 04:00 | 14328.8042 | -0.048233 | 4.89 | 19.13 | 10.09 | 18.47 | 1 | 0.45 | 0.17 | 1
2018-08-08 05:00 | 16940.0841 | -0.048233 | 4.1 | 19.34 | 12.5 | 19.11 | 1 | 0.5 | 0.53 | 1.01
2018-08-08 06:00 | 17058.3162 | 43.1223 | 15.17 | 20.64 | 14.21 | 20.35 | 1.15 | 1 | 1 | 2
2018-08-08 07:00 | 19911.8452 | 99.7869 | 15.1 | 19.99 | 12.39 | 20.73 | 1.61 | 1 | 2.11 | 1.61
2018-08-08 08:00 | 20732.8083 | 435.951 | 17.6 | 20.8 | 14.32 | 21.89 | 1.69 | 1.34 | 2.11 | 2
2018-08-08 09:00 | 19453.3305 | 721.19 | 19.39 | 21.09 | 16 | 24.42 | 2 | 1.4 | 2.42 | 2.11
2018-08-08 10:00 | 21555.0268 | 883.305 | 20.6 | 22.9 | 17.36 | 28.79 | 2.78 | 2.24 | 2.12 | 3.32
2018-08-08 11:00 | 21391.1272 | 1005.95 | 23.27 | 23.27 | 18.9 | 31.1 | 5.54 | 10 | 0.73 | 12.2
2018-08-08 12:00 | 19618.754 | 1017.32 | 31.38 | 24.12 | 19.44 | 37.28 | 21.44 | 19.17 | 1 | 19.74
2018-08-08 13:00 | 21407.6802 | 963.64 | 34.6 | 27.99 | 20 | 43.84 | 45.29 | 66.9073 | 1.05 | 43.6
2018-08-08 14:00 | 19549.9391 | 726.748 | 36.62 | 29.13 | 20.28 | 45.22 | 124.4441 | 429.5216 | 1.43 | 108.9662
2018-08-08 15:00 | 17335.5344 | 658.931 | 54.02 | 37.84 | 20.05 | 50.11 | 517.7678 | 489.0216 | 2.07 | 514.1506
2018-08-08 16:00 | 16618.6293 | 450.294 | 62.52 | 62.44 | 30.94 | 48.55 | 492.1278 | 483.1916 | 1.87 | 484.6506
2018-08-08 17:00 | 15693.4499 | 155.421 | 54.43 | 54.43 | 19.95 | 40.31 | 104.9941 | 420.7116 | 1.97 | 98.8562
2018-08-08 18:00 | 16961.3773 | 44.1349 | 35.72 | 29.34 | 20.07 | 34.63 | 20.99 | 14.59 | 3 | 16.99
2018-08-08 19:00 | 15134.4042 | -0.048233 | 29.94 | 28.38 | 19.06 | 28.19 | 7.26 | 1.34 | 2.31 | 9.74
2018-08-08 20:00 | 16802.9341 | -0.048233 | 26.97 | 25.65 | 18.89 | 26.87 | 5.39 | 1.37 | 2.26 | 4
2018-08-08 21:00 | 14978.6042 | -0.048233 | 41.5 | 41.5 | 17.22 | 28.23 | 4.84 | 1 | 3.5 | 4.18
2018-08-08 22:00 | 14766.7542 | -0.048233 | 22.06 | 22.43 | 15.64 | 23.45 | 3.4 | 0.12 | 20 | 3.92
2018-08-08 23:00 | 14483.6542 | -0.048233 | 19.97 | 21.03 | 15.48 | 22.03 | 1.81 | 0.12 | 8.11 | 2.11
2018-08-09 | 15378.6841 | -0.048233 | 18.43 | 19.68 | 14.43 | 19.74 | 1 | 0.12 | 3.5 | 1.25
2018-08-09 01:00 | 15211.9941 | -0.048233 | 17.37 | 18.83 | 12.64 | 19.02 | 1 | 0.04 | 2.99 | 1
2018-08-09 02:00 | 13527.9542 | -0.048233 | 16.69 | 18.28 | 11.81 | 18.28 | 1 | 0.45 | 1 | 1
2018-08-09 03:00 | 13470.0042 | -0.048233 | 15.61 | 17.81 | 9.4 | 17.96 | 1 | 0.45 | 1 | 1
2018-08-09 04:00 | 14110.3042 | -0.048233 | 10.39 | 17.71 | 9.35 | 17.88 | 1 | 0.45 | 0.08 | 1
2018-08-09 05:00 | 16979.1191 | -0.048233 | 15.37 | 18.06 | 7.55 | 19 | 1 | 0.5 | 0.48 | 1.01
2018-08-09 06:00 | 16840.4631 | 33.8033 | 15.91 | 19.05 | 10.03 | 21.7 | 1.01 | 0.99 | 1 | 2
2018-08-09 07:00 | 19181.9826 | 156.974 | 15.79 | 19.72 | 10.96 | 21.65 | 1.61 | 0.99 | 2 | 1.7
2018-08-09 08:00 | 17963.8701 | 305.337 | 17.44 | 20.12 | 14.67 | 22.64 | 1.61 | 1 | 2 | 2
2018-08-09 09:00 | 19251.9618 | 790.223 | 19.26 | 21.56 | 16.43 | 28.61 | 2 | 1.1 | 1 | 2.11
2018-08-09 10:00 | 19155.9378 | 764.145 | 20.36 | 21.89 | 17.11 | 32.24 | 2.46 | 2.14 | 1 | 3
2018-08-09 11:00 | 21578.2631 | 1119.33 | 30.55 | 26.13 | 18.21 | 32.79 | 4.45 | 10.64 | 0.68 | 11.82
2018-08-09 12:00 | 19476.3708 | 396.443 | 31.02 | 28.23 | 19.44 | 35.86 | 16.5 | 15.3 | 0.87 | 15.3
2018-08-09 13:00 | 21032.0939 | 303.634 | 39.57 | 39.57 | 20.99 | 42.91 | 32.72 | 55.1373 | 1 | 31.59
2018-08-09 14:00 | 18096.2982 | 343.735 | 101.32 | 101.32 | 29.84 | 51.36 | 90.8141 | 79.9273 | 1 | 81.7362
2018-08-09 15:00 | 19269.4294 | 281.862 | 721.8111 | 454.2 | 31.88 | 56.13 | 456.1478 | 452.8316 | 2 | 453.7606
2018-08-09 16:00 | 16479.1541 | 200.478 | 332.7557 | 288.43 | 34.54 | 61.14 | 607.1678 | 607.8016 | 2.11 | 608.1106
2018-08-09 17:00 | 15892.3857 | 106.827 | 85.29 | 85.29 | 33.96 | 47.26 | 118.2541 | 438.1316 | 2.11 | 438.4406
2018-08-09 18:00 | 17216.6525 | 44.1019 | 37.37 | 33.29 | 31.64 | 36.1 | 29.82 | 24.06 | 2.11 | 26.06
2018-08-09 19:00 | 15478.3042 | -0.048233 | 33.52 | 31.51 | 23.45 | 32.74 | 14.8 | 1.38 | 2.11 | 11.9
2018-08-09 20:00 | 15568.5542 | -0.048233 | 30.48 | 29.13 | 20.87 | 31.02 | 7.29 | 1.38 | 2.55 | 5.15
2018-08-09 21:00 | 15515.3542 | -0.048233 | 28.99 | 28.08 | 20.01 | 28.68 | 4.82 | 1.32 | 3.5 | 4.1
2018-08-09 22:00 | 16954.8541 | -0.048233 | 22.12 | 22.12 | 17 | 23.74 | 3.08 | 0.12 | 11.75 | 4
2018-08-09 23:00 | 16310.2491 | -0.048233 | 19.52 | 22.42 | 15.43 | 22.44 | 1.55 | 0.12 | 3.5 | 2
2018-08-10 | 14103.6542 | -0.048233 | 17.8 | 19.96 | 15.47 | 19.89 | 1 | 0.1 | 3.11 | 1.25
2018-08-10 01:00 | 15196.1691 | -0.048233 | 16.48 | 18.71 | 14 | 18.76 | 0.99 | 0.01 | 2.88 | 1
2018-08-10 02:00 | 15060.0741 | -0.048233 | 13.18 | 17.45 | 12.06 | 18.2 | 0.99 | 0.45 | 1.01 | 1
2018-08-10 03:00 | 15008.3791 | -0.048233 | 3.33 | 17.11 | 11.84 | 17.88 | 0.99 | 0.5 | 1 | 1
2018-08-10 04:00 | 15788.0241 | -0.048233 | 11.8 | 17.18 | 11.87 | 17.79 | 0.99 | 0.5 | 0.15 | 1
2018-08-10 05:00 | 15379.5042 | -0.048233 | 15.39 | 17.81 | 14.12 | 18.91 | 0.99 | 0.5 | 0.22 | 1.01
2018-08-10 06:00 | 19363.0207 | 37.5741 | 16.65 | 19.06 | 15.47 | 20.9 | 1.21 | 1 | 1 | 2
2018-08-10 07:00 | 17892.9507 | 203.685 | 17.47 | 19 | 17.23 | 21.31 | 1.21 | 1 | 1.73 | 1.34
2018-08-10 08:00 | 18627.8194 | 407.231 | 19.06 | 20.74 | 17.39 | 22.88 | 1.21 | 1 | 1 | 2
2018-08-10 09:00 | 21911.7434 | 662.425 | 21 | 22.53 | 20.17 | 28.65 | 2.86 | 1.4 | 1 | 2.86
2018-08-10 10:00 | 22077.543 | 860.581 | 22.23 | 26.43 | 20.58 | 28.76 | 5.4 | 5.81 | 1 | 5.4
2018-08-10 11:00 | 19124.982 | 1032.56 | 32.21 | 32.21 | 21.36 | 37.54 | 8.25 | 10.76 | 1 | 11.66
2018-08-10 12:00 | 20005.594 | 1062.52 | 33.99 | 31.09 | 22.33 | 37.93 | 21.72 | 19.54 | 1 | 19.54
2018-08-10 13:00 | 20893.16 | 1046.8 | 54.75 | 36.75 | 23.43 | 49.02 | 107.8141 | 428.6616 | 1 | 104.7562
2018-08-10 14:00 | 20852.8705 | 907.754 | 63.07 | 35.32 | 28.68 | 57.41 | 824.6578 | 821.5316 | 1 | 821.8406
2018-08-10 15:00 | 17457.1487 | 798.946 | 124.76 | 44.16 | 28.59 | 65.91 | 2039.2678 | 2034.9416 | 20 | 2035.2506
2018-08-10 16:00 | 18649.1538 | 464.923 | 140.85 | 32.49 | 31.23 | 62.97 | 2600.4078 | 2590.4916 | 17.23 | 2590.7906
2018-08-10 17:00 | 17778.4348 | 240.597 | 119.5 | 35.4 | 29.44 | 45.13 | 1137.2078 | 1134.8816 | 12.05 | 1135.1906
2018-08-10 18:00 | 16483.765 | 52.4218 | 70.31 | 41.15 | 23.71 | 38.03 | 567.7478 | 563.0816 | 2.11 | 565.7906
2018-08-10 19:00 | 12835.4042 | -0.048233 | 68.07 | 30.03 | 23 | 36 | 19.54 | 10.35 | 2.11 | 13.72
2018-08-10 20:00 | 14731.9691 | -0.048233 | 32.2 | 30.04 | 22.89 | 33.9 | 8.85 | 0.99 | 2.11 | 5.87
2018-08-10 21:00 | 15330.1541 | -0.048233 | 30.57 | 30.57 | 20.24 | 30.07 | 7.31 | 0.99 | 4.74 | 5.79
2018-08-10 22:00 | 15407.1691 | -0.048233 | 26.11 | 26.11 | 17.29 | 26.02 | 3.84 | 0.12 | 3.5 | 4.14
2018-08-10 23:00 | 13624.8542 | -0.048233 | 21.65 | 21.65 | 16.58 | 22.91 | 1.15 | 0.12 | 3.5 | 2.21
2018-08-11 | 14698.2091 | -0.048233 | 19.98 | 20.58 | 13.76 | 20.37 | 0.98 | 0.1 | 3.44 | 1
2018-08-11 01:00 | 14616.9741 | -0.048233 | 18.91 | 18.91 | 13.86 | 18.51 | 0.97 | 0.01 | 3.11 | 1
2018-08-11 02:00 | 14645.4591 | -0.048233 | 17.9 | 17.9 | 12.94 | 17.99 | 0.97 | 0.5 | 2.11 | 0.97
2018-08-11 03:00 | 14860.6791 | -0.048233 | 17.63 | 17.87 | 12.21 | 17.75 | 0.97 | 0.5 | 1.22 | 1
2018-08-11 04:00 | 14092.2542 | -0.048233 | 17.27 | 17.94 | 12.51 | 17.98 | 0.97 | 0.5 | 1 | 1
2018-08-11 05:00 | 14983.3542 | -0.048233 | 17.68 | 18.58 | 13.05 | 18.91 | 0.97 | 0.5 | 1 | 1.01
2018-08-11 06:00 | 16727.9139 | 23.3304 | 18.81 | 20.04 | 15.18 | 21.79 | 0.98 | 0.97 | 2 | 1.8
2018-08-11 07:00 | 17582.3853 | 218.774 | 19.42 | 20.08 | 15.5 | 21.3 | 0.97 | 0.97 | 2.07 | 1.01
2018-08-11 08:00 | 17989.8536 | 474.688 | 19.85 | 21.2 | 16.6 | 23.09 | 1 | 0.99 | 2.31 | 1.51
2018-08-11 09:00 | 21101.9264 | 779.826 | 21.34 | 21.34 | 18.32 | 27.83 | 2.41 | 0.99 | 2.11 | 2.41
2018-08-11 10:00 | 19738.1025 | 1017.95 | 23.09 | 26.11 | 32.08 | 35.76 | 6.39 | 6.31 | 2.11 | 6.19
2018-08-11 11:00 | 20101.3255 | 1102.29 | 29.71 | 28.04 | 36.19 | 38.42 | 8.77 | 8.52 | 1.31 | 12.69
2018-08-11 12:00 | 22621.3944 | 1110.08 | 56.73 | 32 | 36.68 | 43.42 | 18.25 | 16.71 | 1.38 | 16.71
2018-08-11 13:00 | 23215.9607 | 1158.65 | 57.27 | 34.2 | 40.88 | 59.2 | 38.77 | 55.0073 | 2 | 31.7
2018-08-11 14:00 | 18712.454 | 1035.32 | 265.4257 | 43.54 | 45.17 | 69.86 | 512.7378 | 516.4116 | 1 | 516.7206
2018-08-11 15:00 | 19146.7519 | 872.58 | 771.9011 | 41.16 | 47.75 | 99.27 | 1061.0178 | 1049.1016 | 15 | 1049.4106
2018-08-11 16:00 | 16518.6589 | 554.062 | 347.3657 | 33.26 | 48.49 | 77.99 | 1364.7478 | 1348.8216 | 33.29 | 1349.1306
2018-08-11 17:00 | 15891.1117 | 250.486 | 91.86 | 32.04 | 47.8 | 51.92 | 611.2978 | 599.3716 | 2.21 | 599.6806
2018-08-11 18:00 | 15481.9137 | 36.7513 | 37.02 | 32.32 | 45.04 | 39.71 | 86.9341 | 27.85 | 15.71 | 31.6
2018-08-11 19:00 | 15224.6542 | -0.048233 | 35.95 | 30.97 | 38.85 | 35.08 | 18.39 | 11.17 | 2 | 15.31
2018-08-11 20:00 | 15272.1542 | -0.048233 | 30.27 | 30.27 | 36.06 | 35.24 | 13.72 | 1.19 | 2.21 | 5.65
2018-08-11 21:00 | 16545.5141 | -0.048233 | 30.01 | 30.01 | 18.01 | 33.67 | 7.06 | 1.14 | 3.5 | 6.86
2018-08-11 22:00 | 14478.9042 | -0.048233 | 30.37 | 26.78 | 15.56 | 27.08 | 5.04 | 0.12 | 8.61 | 5.14
2018-08-11 23:00 | 15741.6041 | -0.048233 | 22.76 | 23.89 | 15.55 | 23.59 | 2.11 | 0.12 | 3.34 | 2.11
2018-08-12 | 15362.8591 | -0.048233 | 19.49 | 21.36 | 16.4 | 21.44 | 2 | 0.1 | 2.99 | 2
2018-08-12 01:00 | 13657.1542 | -0.048233 | 19.45 | 20.32 | 15.73 | 20.41 | 1.2 | 0.12 | 3.01 | 1.11
2018-08-12 02:00 | 14916.5941 | -0.048233 | 18.45 | 19.18 | 15.56 | 19.65 | 1.01 | 0.5 | 2.61 | 1
2018-08-12 03:00 | 14792.1041 | -0.048233 | 19.04 | 19.06 | 15.51 | 19.19 | 1.11 | 0.61 | 2.34 | 1
2018-08-12 04:00 | 13481.4042 | -0.048233 | 18.49 | 18.49 | 15.51 | 18.62 | 1.01 | 0.5 | 2 | 1
2018-08-12 05:00 | 14055.2042 | -0.048233 | 18.39 | 18.39 | 15.49 | 18.69 | 1.48 | 0.5 | 2.61 | 1.48
2018-08-12 06:00 | 14845.4709 | 34.8115 | 18.56 | 18.56 | 14.99 | 19.97 | 1.61 | 0.97 | 1.72 | 2
2018-08-12 07:00 | 14823.1977 | 160.366 | 19.32 | 19.32 | 15.11 | 20.19 | 1.71 | 0.97 | 1.02 | 2
2018-08-12 08:00 | 17060.6814 | 383.262 | 19.54 | 21.08 | 16.88 | 21.57 | 2.1 | 0.97 | 1 | 2.11
2018-08-12 09:00 | 17525.1557 | 669.522 | 21.19 | 21.26 | 18.02 | 24.34 | 3.27 | 0.97 | 1.87 | 3.52
2018-08-12 10:00 | 15686.7781 | 468.398 | 42.12 | 28.02 | 35.81 | 25.99 | 5.36 | 6.94 | 1 | 7
2018-08-12 11:00 | 17505.4304 | 448.825 | 35.97 | 28.98 | 41.41 | 33.01 | 21.91 | 10 | 1 | 21.06
2018-08-12 12:00 | 17751.9828 | 614.524 | 46.04 | 30.85 | 45.58 | 35.41 | 27 | 17.87 | 1 | 23
2018-08-12 13:00 | 17254.9027 | 569.358 | 60.52 | 41.52 | 47.96 | 43.78 | 98.2741 | 83.9573 | 1 | 90.5062
2018-08-12 14:00 | 16771.5639 | 508.217 | 390.0657 | 49.36 | 48.45 | 60.14 | 466.2978 | 444.0216 | 1 | 453.2806
2018-08-12 15:00 | 15000.8772 | 508.397 | 740.9711 | 50.14 | 51.43 | 67.24 | 621.1678 | 581.6116 | 2 | 590.3706
2018-08-12 16:00 | 16471.1221 | 258.438 | 339.7157 | 43.26 | 49.39 | 61.76 | 645.3878 | 614.7916 | 2.11 | 616.6006
2018-08-12 17:00 | 14688.747 | 163.839 | 105.28 | 31.3 | 49.02 | 44.23 | 105.3341 | 65.9173 | 2.38 | 45.32
2018-08-12 18:00 | 14405.4768 | 45.6598 | 45.53 | 32.5 | 45.15 | 34.69 | 40.88 | 23.91 | 2.11 | 26.18
2018-08-12 19:00 | 14215.7542 | -0.048233 | 38.6 | 29.2 | 38.57 | 32.28 | 22.54 | 11.45 | 1.8 | 18.54
2018-08-12 20:00 | 14179.6542 | -0.048233 | 32.1 | 26.46 | 36.53 | 29.29 | 7.78 | 0.97 | 1.49 | 6.07
2018-08-12 21:00 | 14005.8042 | -0.048233 | 30.44 | 25.27 | 29.94 | 28.66 | 8.1 | 0.97 | 3.11 | 7.9
2018-08-12 22:00 | 15263.6891 | -0.048233 | 23.14 | 24.43 | 17.07 | 26.5 | 5 | 0.12 | 12 | 5.83
2018-08-12 23:00 | 13528.9042 | -0.048233 | 21.92 | 24.44 | 16.56 | 24.56 | 2.83 | 0.12 | 3.11 | 3
2018-08-13 | 13280.9542 | -0.048233 | 22.01 | 22.01 | 16.07 | 21.05 | 1.5 | 0.01 | 3.5 | 1.94
2018-08-13 01:00 | 14442.8991 | -0.048233 | 21.34 | 21.35 | 15.42 | 20.1 | 0.98 | 0.01 | 2.61 | 1
2018-08-13 02:00 | 12855.3542 | -0.048233 | 20.21 | 21.04 | 14.45 | 18.8 | 0.98 | 0.5 | 2.61 | 1
2018-08-13 03:00 | 14089.4741 | -0.048233 | 19.97 | 20.37 | 14.22 | 18.38 | 0.98 | 0.5 | 2.26 | 1
2018-08-13 04:00 | 14089.4741 | -0.048233 | 19.73 | 20 | 14.21 | 17.67 | 0.98 | 0.5 | 2.11 | 0.98
2018-08-13 05:00 | 12774.6042 | -0.048233 | 19.35 | 19.99 | 12.91 | 17.88 | 0.98 | 0.5 | 2.31 | 1.01
2018-08-13 06:00 | 12820.0757 | 27.8165 | 19.4 | 20.02 | 12.54 | 18.84 | 1 | 0.85 | 2.2 | 2
2018-08-13 07:00 | 12608.513 | 168.119 | 19.13 | 19.35 | 13.03 | 19.06 | 1 | 0.97 | 2.11 | 1.51
2018-08-13 08:00 | 14270.0714 | 191.134 | 19.21 | 20.12 | 15.11 | 20.08 | 1.78 | 0.97 | 2 | 2
2018-08-13 09:00 | 14565.9714 | 273.608 | 19.4 | 20.9 | 16.74 | 22.26 | 2.42 | 0.97 | 2.21 | 3.52
2018-08-13 10:00 | 14813.6591 | 337.383 | 18.72 | 21.08 | 17.05 | 26.29 | 5.14 | 2 | 1 | 5.15
2018-08-13 11:00 | 14953.8137 | 377.231 | 39.03 | 21.56 | 30 | 28.6 | 13.86 | 11.06 | 1 | 12.92
2018-08-13 12:00 | 14454.8295 | 1122.61 | 91.94 | 24.71 | 35.69 | 32.77 | 20.9 | 18.12 | 1 | 19.37
2018-08-13 13:00 | 13939.6511 | 520.317 | 57.76 | 30.54 | 36.8 | 37.13 | 95.4541 | 87.9473 | 1.4 | 92.0562
2018-08-13 14:00 | 14462.0875 | 1036.25 | 81.34 | 30.54 | 36.29 | 49 | 507.4178 | 499.9516 | 1 | 506.6206
2018-08-13 15:00 | 13841.1647 | 358.647 | 1356.8411 | 31.67 | 37.2 | 57.62 | 790.4678 | 773.4216 | 1.29 | 776.9806
2018-08-13 16:00 | 15667.8124 | 410.007 | 914.2211 | 57.38 | 36.36 | 66.05 | 917.7378 | 903.8116 | 2.11 | 904.8606
2018-08-13 17:00 | 15253.6468 | 110.433 | 657.3211 | 30.78 | 35.89 | 43.11 | 487.2478 | 472.8316 | 2.11 | 476.3306
2018-08-13 18:00 | 15222.1387 | 34.5675 | 61.26 | 30.73 | 34.79 | 35.7 | 83.6341 | 57.3473 | 2.11 | 44.09
2018-08-13 19:00 | 15027.3691 | -0.048233 | 40.98 | 27.41 | 29.4 | 30.72 | 19.14 | 0.97 | 2.11 | 15.14
2018-08-13 20:00 | 13519.4042 | -0.048233 | 35.03 | 22.92 | 29.65 | 31.18 | 6.95 | 0.97 | 2.21 | 4.85
2018-08-13 21:00 | 13619.1542 | -0.048233 | 30.93 | 23.05 | 17.23 | 28.16 | 4.88 | 0.97 | 8.41 | 4
2018-08-13 22:00 | 13453.8542 | -0.048233 | 20.66 | 20.66 | 16.98 | 25.07 | 4 | 0.01 | 11.07 | 4.28
2018-08-13 23:00 | 13286.6542 | -0.048233 | 20.54 | 20.54 | 16.45 | 22.76 | 2.11 | 0.01 | 4 | 2.11
2018-08-14 | 13221.1042 | -0.048233 | 19.94 | 21.07 | 16.12 | 20.45 | 1 | 0.01 | 3.5 | 1.04
2018-08-14 01:00 | 14646.5141 | -0.048233 | 18.78 | 18.78 | 14.45 | 18.76 | 0.98 | 0.01 | 2.99 | 1
2018-08-14 02:00 | 13094.7542 | -0.048233 | 17.92 | 17.92 | 14.14 | 17.69 | 0.98 | 0.5 | 2.99 | 1
2018-08-14 03:00 | 14416.5241 | -0.048233 | 17.8 | 17.8 | 13.12 | 17.23 | 0.98 | 0.5 | 2.31 | 1
2018-08-14 04:00 | 13712.2542 | -0.048233 | 18.16 | 19.73 | 13.62 | 17.17 | 0.98 | 0.5 | 2.11 | 0.98
2018-08-14 05:00 | 14649.9042 | -0.048233 | 18.48 | 20.93 | 14.08 | 18.08 | 0.98 | 0.5 | 2.61 | 1
2018-08-14 06:00 | 16501.7586 | 33.2722 | 18.25 | 21.77 | 15.81 | 19.83 | 1.25 | 0.97 | 1.02 | 1.25
2018-08-14 07:00 | 19259.4386 | 190.392 | 17.81 | 21.28 | 17.38 | 20.07 | 1.25 | 0.97 | 1.56 | 1.25
2018-08-14 08:00 | 17999.4011 | 407.738 | 19.07 | 21.26 | 17.9 | 21.28 | 2 | 0.97 | 1 | 2
2018-08-14 09:00 | 21124.2333 | 670.97 | 20.29 | 21.18 | 18.79 | 23.73 | 2.11 | 0.97 | 1.42 | 3
2018-08-14 10:00 | 18892.3906 | 878.727 | 20.7 | 21.9 | 22.67 | 26.47 | 3 | 7.34 | 1 | 4
2018-08-14 11:00 | 18941.1855 | 1078.09 | 32.27 | 23.69 | 30.86 | 31.97 | 5.82 | 9.09 | 1 | 5.82
2018-08-14 12:00 | 21309.8901 | 866.948 | 36.69 | 28.44 | 39.43 | 36.1 | 17.3 | 15.43 | 1 | 16.23
2018-08-14 13:00 | 20841.9185 | 697.373 | 49.96 | 29.32 | 42.83 | 43.44 | 34.81 | 24.98 | 1.73 | 32.18
2018-08-14 14:00 | 18122.7576 | 632.587 | 40.91 | 31.95 | 42.52 | 57.4 | 462.2678 | 453.7316 | 1 | 455.4806
2018-08-14 15:00 | 17250.5398 | 633.463 | 58.06 | 32.74 | 42.41 | 67.84 | 853.7878 | 839.9816 | 2 | 845.4106
2018-08-14 16:00 | 18400.37 | 499.109 | 35.87 | 32.42 | 43.15 | 61.41 | 869.3978 | 855.4716 | 2.25 | 857.6206
2018-08-14 17:00 | 15699.0833 | 94.3508 | 33.28 | 32.45 | 42.45 | 45.63 | 106.1341 | 90.0273 | 2.31 | 95.7262
2018-08-14 18:00 | 16923.8229 | 43.5383 | 32.24 | 32.24 | 42.86 | 38.93 | 30.97 | 16.55 | 8.32 | 20.55
2018-08-14 19:00 | 15238.9042 | -0.048233 | 29.02 | 27.35 | 42.61 | 35.69 | 5.69 | 10.09 | 2.31 | 5.02
2018-08-14 20:00 | 17116.2691 | -0.048233 | 21.77 | 24.56 | 40.04 | 36.45 | 4.45 | 0.82 | 2.61 | 3.79
2018-08-14 21:00 | 15213.2542 | -0.048233 | 22.94 | 23.65 | 32.32 | 28.74 | 4.68 | 0.82 | 8.31 | 4
2018-08-14 22:00 | 14675.5542 | -0.048233 | 22.01 | 22.18 | 17.69 | 23.9 | 3.13 | 0.01 | 12 | 3.13
2018-08-14 23:00 | 14308.8542 | -0.048233 | 20.21 | 21.26 | 17.13 | 22.34 | 2 | 0.01 | 4 | 2.01
2018-08-15 | 14051.4042 | -0.048233 | 19.34 | 21.91 | 17.19 | 21.01 | 1 | 0.01 | 3.5 | 2.46
2018-08-15 01:00 | 13701.8042 | -0.048233 | 18.7 | 20.06 | 15.53 | 19.19 | 1 | 0.01 | 2.81 | 1.25
2018-08-15 02:00 | 13669.5042 | -0.048233 | 18.38 | 18.62 | 15.31 | 18.74 | 1 | 0.5 | 2.44 | 1
2018-08-15 03:00 | 15203.5541 | -0.048233 | 18.03 | 18.03 | 15.19 | 17.74 | 1 | 0.5 | 2.11 | 1
2018-08-15 04:00 | 16074.9841 | -0.048233 | 18.05 | 18.05 | 15.1 | 17.56 | 1 | 0.5 | 1 | 1
2018-08-15 05:00 | 16949.5791 | -0.048233 | 18.62 | 18.78 | 15.33 | 18.9 | 1 | 0.5 | 2.11 | 1.41
2018-08-15 06:00 | 19199.6001 | 27.6731 | 18.42 | 21.11 | 15.52 | 21.55 | 1 | 0.97 | 2.44 | 2
2018-08-15 07:00 | 18074.9688 | 195.283 | 18.4 | 21.37 | 16 | 21.15 | 1.16 | 0.97 | 2.31 | 2
2018-08-15 08:00 | 18635.5534 | 441.372 | 19.47 | 21.28 | 19 | 21.4 | 2 | 0.97 | 2.61 | 2
2018-08-15 09:00 | 19520.3511 | 721.738 | 20.06 | 20.06 | 24.4 | 26.12 | 2.81 | 0.97 | 2.61 | 2.81
2018-08-15 10:00 | 19844.6459 | 881.101 | 20.78 | 20.78 | 31.23 | 28.85 | 4.83 | 0.99 | 1.5 | 4.99
2018-08-15 11:00 | 19458.8443 | 846.994 | 21.13 | 21.26 | 38.19 | 31.2 | 6.94 | 1 | 0.69 | 7.31
2018-08-15 12:00 | 22015.2484 | 967.534 | 32.84 | 22.69 | 37.91 | 33.99 | 8.31 | 2.62 | 1 | 10.53
2018-08-15 13:00 | 19517.4764 | 846.712 | 33.96 | 25.37 | 42.65 | 38.77 | 16.62 | 3 | 1.26 | 15.03
2018-08-15 14:00 | 18613.4602 | 600.116 | 50.47 | 26.22 | 45.15 | 47.91 | 25.44 | 13.76 | 1 | 21.04
2018-08-15 15:00 | 17892.6154 | 738.332 | 36.25 | 27.37 | 49.81 | 56.38 | 51.95 | 58.2373 | 2 | 46.93
2018-08-15 16:00 | 16937.4911 | 468.938 | 37.25 | 28.06 | 47.04 | 52.42 | 99.0841 | 78.2273 | 2 | 92.3162
2018-08-15 17:00 | 16283.2308 | 197.243 | 38.47 | 29.53 | 45.46 | 41.7 | 36.44 | 24.29 | 2.11 | 29.89
2018-08-15 18:00 | 15858.573 | 53.2347 | 35.18 | 28.64 | 37.98 | 36.29 | 22.96 | 1 | 8.11 | 6.5
2018-08-15 19:00 | 17558.3141 | -0.048233 | 20.79 | 25.89 | 35 | 32.56 | 7.13 | 0.97 | 2.61 | 6.19
2018-08-15 20:00 | 17501.3441 | -0.048233 | 29.3 | 29.3 | 34.92 | 29.98 | 5 | 0.97 | 2.61 | 4.12
2018-08-15 21:00 | 15645.5042 | -0.048233 | 22.07 | 26.3 | 20.38 | 29.36 | 4.97 | 0.97 | 10.53 | 3.63
2018-08-15 22:00 | 15208.5042 | -0.048233 | 19.59 | 24.01 | 18.77 | 23.83 | 3 | 0.01 | 11.4 | 3.11
2018-08-15 23:00 | 14780.0542 | -0.048233 | 18.38 | 24.56 | 18.07 | 22.56 | 1.51 | 0.01 | 5 | 2.11
2018-08-16 | 14393.4042 | -0.048233 | 16.72 | 21.78 | 18.8 | 19.77 | 1 | 0.01 | 10 | 2
2018-08-16 01:00 | 15798.5741 | -0.048233 | 16.45 | 20.85 | 18.08 | 18.17 | 1 | 0.01 | 3.13 | 1
2018-08-16 02:00 | 14087.5042 | -0.048233 | 16.55 | 19.77 | 16.99 | 17.51 | 1 | 0.5 | 3.5 | 1.04
2018-08-16 03:00 | 13993.4542 | -0.048233 | 16.68 | 18.87 | 16.12 | 17.12 | 1 | 0.5 | 2.61 | 1
2018-08-16 04:00 | 16103.4691 | -0.048233 | 16.92 | 18.79 | 15.61 | 17.1 | 1 | 0.5 | 1 | 1
2018-08-16 05:00 | 15320.6042 | -0.048233 | 16.77 | 19.58 | 15.52 | 18.31 | 1 | 0.5 | 2.61 | 1.78
2018-08-16 06:00 | 17134.9996 | 33.8417 | 16.89 | 20.17 | 15.51 | 20.34 | 1.99 | 0.97 | 3.04 | 2
2018-08-16 07:00 | 18277.5896 | 199.568 | 16.48 | 20.21 | 16.71 | 20.18 | 2 | 0.97 | 2.99 | 1.8
2018-08-16 08:00 | 18396.7139 | 499.962 | 18.46 | 20.57 | 18.14 | 20.9 | 2 | 0.97 | 3.44 | 2
2018-08-16 09:00 | 22014.3115 | 649.646 | 20.25 | 21.19 | 35.2 | 23.81 | 2.72 | 0.97 | 2.11 | 3
2018-08-16 10:00 | 19713.2457 | 878.785 | 20.43 | 23.35 | 34.69 | 26.94 | 3.03 | 0.99 | 2.11 | 3.03
2018-08-16 11:00 | 22094.7152 | 924.858 | 21.49 | 27.93 | 39.27 | 30.62 | 5 | 1 | 0.69 | 5
2018-08-16 12:00 | 22557.3559 | 1155.38 | 31.07 | 27.49 | 43.41 | 32.54 | 7.25 | 0.99 | 1 | 7.25
2018-08-16 13:00 | 20043.518 | 1000.44 | 31.97 | 31.34 | 45.35 | 38.89 | 20.37 | 2.5 | 2.01 | 16.78
2018-08-16 14:00 | 18677.3201 | 732.337 | 32.42 | 32.42 | 50.7 | 49.19 | 24.21 | 1.15 | 1 | 17.31
2018-08-16 15:00 | 17779.6813 | 711.454 | 65.83 | 65.83 | 48.73 | 61.98 | 35.01 | 21.85 | 1.97 | 30.21
2018-08-16 16:00 | 17158.7518 | 419.844 | 73.67 | 73.67 | 49.71 | 54.93 | 36.87 | 16.67 | 2 | 35.87
2018-08-16 17:00 | 18508.7987 | 205.885 | 120.18 | 120.18 | 48.66 | 40.83 | 23.05 | 9.29 | 2.11 | 20.27
2018-08-16 18:00 | 18056.0246 | 41.7153 | 44.98 | 44.98 | 45.91 | 36.57 | 5 | 1.27 | 8.11 | 4.28
2018-08-16 19:00 | 16064.4542 | -0.048233 | 28.95 | 28.95 | 40.02 | 34.58 | 3.46 | 0.97 | 2.61 | 3
2018-08-16 20:00 | 16035.0042 | -0.048233 | 28.71 | 28.71 | 36.45 | 30.87 | 3.65 | 0.97 | 3.5 | 3
2018-08-16 21:00 | 17515.0591 | -0.048233 | 28.87 | 28.87 | 30.83 | 28.27 | 2.74 | 0.97 | 8 | 2.74
2018-08-16 22:00 | 16997.0541 | -0.048233 | 20.34 | 24.42 | 19.65 | 24.04 | 2.41 | 0.01 | 10.03 | 2.61
2018-08-16 23:00 | 14893.1042 | -0.048233 | 19.77 | 23.91 | 19.07 | 21.96 | 1.64 | 0.01 | 7.1 | 2.11
2018-08-17 | 16326.0741 | -0.048233 | 19.3 | 21.64 | 16.88 | 20.82 | 1.15 | 0.01 | 3.95 | 1.61
2018-08-17 01:00 | 14626.1542 | -0.048233 | 18.18 | 20.97 | 15.87 | 19.99 | 1 | 0.01 | 3.5 | 1.25
2018-08-17 02:00 | 14388.6542 | -0.048233 | 17.2 | 20.91 | 15.36 | 19.99 | 1 | 0.5 | 3.5 | 1
2018-08-17 03:00 | 14249.9542 | -0.048233 | 16.26 | 21.01 | 12.6 | 19.63 | 1 | 0.5 | 2.61 | 1
2018-08-17 04:00 | 14748.7042 | -0.048233 | 16.27 | 21.14 | 13.16 | 19.85 | 1 | 0.5 | 1 | 1
2018-08-17 05:00 | 15695.8542 | -0.048233 | 17.41 | 21.29 | 15.89 | 20.08 | 1 | 0.5 | 2.61 | 1.32
2018-08-17 06:00 | 19050.0682 | 33.9367 | 18.12 | 24.84 | 17.08 | 21.89 | 1.76 | 0.97 | 2.11 | 2.4
2018-08-17 07:00 | 18329.5698 | 182.284 | 18.3 | 21.6 | 18.82 | 21.52 | 1.92 | 0.97 | 2.11 | 2.01
2018-08-17 08:00 | 21125.6101 | 210.275 | 19.49 | 20.58 | 22.03 | 21.64 | 2.1 | 0.97 | 1.82 | 2.5
2018-08-17 09:00 | 22777.6325 | 808.173 | 20.64 | 21.42 | 23.71 | 24.17 | 2.98 | 0.97 | 1.58 | 2.61
2018-08-17 10:00 | 20060.6531 | 990.477 | 22.37 | 24.96 | 30.28 | 30.88 | 3.9 | 2.14 | 1 | 3.9
2018-08-17 11:00 | 19525.408 | 925.061 | 27.44 | 27.44 | 35.22 | 42.1 | 5.41 | 1.15 | 1 | 5.41
2018-08-17 12:00 | 22353.0551 | 1023.73 | 29.02 | 28.54 | 35.33 | 40.26 | 14.41 | 7.49 | 1 | 13.27
2018-08-17 13:00 | 19492.2615 | 1020.17 | 34.6 | 34.6 | 41.78 | 45.79 | 17.68 | 10.18 | 1 | 15.18
2018-08-17 14:00 | 18180.4274 | 898.292 | 34.94 | 31.1 | 42.52 | 58.64 | 27.25 | 13.73 | 1 | 22.25
2018-08-17 15:00 | 17308.2476 | 677.208 | 84.02 | 31.34 | 46.47 | 76.51 | 43.8 | 28.11 | 2 | 33.71
2018-08-17 16:00 | 17183.428 | 460.819 | 100.26 | 100.26 | 47.2 | 67.21 | 45.2 | 58.7773 | 2.11 | 43.28
2018-08-17 17:00 | 15817.5076 | 201.008 | 246.0357 | 201.71 | 45.21 | 45.36 | 21.64 | 13.52 | 3.06 | 18.92
2018-08-17 18:00 | 16141.9964 | 50.5752 | 68.42 | 68.42 | 40.34 | 36.45 | 6.42 | 1.26 | 10 | 5.7
2018-08-17 19:00 | 17592.0741 | -0.048233 | 31.56 | 25.17 | 34.45 | 32.27 | 4.31 | 0.97 | 2.31 | 3.54
2018-08-17 20:00 | 17476.0241 | -0.048233 | 20.27 | 24.3 | 32.66 | 31.11 | 4.3 | 0.97 | 3.5 | 3
2018-08-17 21:00 | 17099.3891 | -0.048233 | 67.61 | 67.61 | 30.88 | 29.29 | 3.68 | 0.97 | 4 | 3.15
2018-08-17 22:00 | 16720.6441 | -0.048233 | 18.84 | 22.13 | 18.53 | 25.32 | 2.38 | 0.01 | 16.31 | 2.61
2018-08-17 23:00 | 14670.8042 | -0.048233 | 18.97 | 20.14 | 17.66 | 22.37 | 1.54 | 0.01 | 8.61 | 2.11
2018-08-18 | 14180.6042 | -0.048233 | 17.32 | 18.69 | 16.72 | 20.4 | 1 | 0.01 | 2.61 | 1.61
2018-08-18 01:00 | 15550.6491 | -0.048233 | 17 | 17.54 | 14.22 | 19.51 | 1 | 0.01 | 2.89 | 1
2018-08-18 02:00 | 13878.5042 | -0.048233 | 16.83 | 16.94 | 11.34 | 18.77 | 1 | 0.5 | 2.61 | 1
2018-08-18 03:00 | 15358.6391 | -0.048233 | 16.56 | 16.78 | 9.49 | 18.15 | 1 | 0.5 | 2.61 | 1
2018-08-18 04:00 | 16129.8441 | -0.048233 | 16.66 | 16.9 | 9.45 | 18.28 | 1 | 0.5 | 1 | 1
2018-08-18 05:00 | 15478.3042 | -0.048233 | 17.58 | 17.58 | 14.8 | 19.02 | 1 | 0.5 | 2.61 | 1.41
2018-08-18 06:00 | 17334.8831 | 24.2454 | 18.35 | 18.35 | 17.33 | 21.18 | 1.51 | 0.85 | 2.61 | 2
2018-08-18 07:00 | 18324.513 | 223.961 | 18.72 | 18.72 | 18.15 | 21.29 | 1.88 | 0.85 | 2.98 | 2.35
2018-08-18 08:00 | 18943.9338 | 568.983 | 19.26 | 19.26 | 18.62 | 22.6 | 2.35 | 0.97 | 2.72 | 2.5
2018-08-18 09:00 | 22135.4382 | 784.458 | 20.41 | 20.41 | 19.69 | 29.02 | 3.11 | 0.97 | 2.61 | 3.11
2018-08-18 10:00 | 22184.7246 | 641.175 | 21.07 | 24.37 | 24.33 | 32.77 | 4 | 2.09 | 2.61 | 3.55
2018-08-18 11:00 | 19696.7395 | 1144.41 | 24.06 | 25 | 31.92 | 36.36 | 5.85 | 2 | 1 | 4.9
2018-08-18 12:00 | 21342.1119 | 721.381 | 27.4 | 27.4 | 33.99 | 42.79 | 6.89 | 5.6 | 1 | 11.35
2018-08-18 13:00 | 21752.6757 | 1158.65 | 31.26 | 31.26 | 34.25 | 53.41 | 22.13 | 9.55 | 1.32 | 18.06
2018-08-18 14:00 | 20537.5468 | 853.869 | 34.69 | 34.69 | 34.02 | 72.78 | 36.18 | 15 | 1 | 29.79
2018-08-18 15:00 | 19915.4734 | 836.226 | 39.63 | 39.63 | 34.52 | 102.38 | 86.2941 | 25 | 2 | 51.78
2018-08-18 16:00 | 17034.0444 | 445.573 | 81.18 | 37.51 | 35.25 | 83.83 | 46.3 | 24.59 | 2.11 | 35.81
2018-08-18 17:00 | 18164.4688 | 195.506 | 35.2 | 30.71 | 34.55 | 60.37 | 25.37 | 13.36 | 2.91 | 20.37
2018-08-18 18:00 | 17643.7476 | 34.9314 | 37.56 | 28 | 31.7 | 39.54 | 13.67 | 1.27 | 10 | 13.21
2018-08-18 19:00 | 17457.0341 | -0.048233 | 31.2 | 27.39 | 29.48 | 31.69 | 5 | 0.97 | 2.31 | 3.52
2018-08-18 20:00 | 17503.4541 | -0.048233 | 35.18 | 26.1 | 24.71 | 31.72 | 4.88 | 0.97 | 1.09 | 3.58
2018-08-18 21:00 | 17151.0841 | -0.048233 | 19.74 | 25.58 | 21.93 | 27.53 | 3.39 | 0.97 | 4 | 3
2018-08-18 22:00 | 16449.5091 | -0.048233 | 18.13 | 24.09 | 18.72 | 27.31 | 3.25 | 0.01 | 14.01 | 3
2018-08-18 23:00 | 15804.9041 | -0.048233 | 16.76 | 21.23 | 18.01 | 23.28 | 1.96 | 0.01 | 8.11 | 2.17
2018-08-19 | 15261.5791 | -0.048233 | 16.85 | 23.23 | 18.85 | 20.78 | 1 | 0.01 | 3.5 | 2
2018-08-19 01:00 | 13696.1042 | -0.048233 | 17.18 | 20.3 | 18.2 | 19.47 | 0.99 | 0.01 | 3.5 | 0.99
2018-08-19 02:00 | 15060.0741 | -0.048233 | 16.14 | 19.06 | 17.39 | 19 | 0.99 | 0.5 | 2.99 | 0.5
2018-08-19 03:00 | 13425.3542 | -0.048233 | 16.36 | 18.3 | 15.52 | 18.02 | 0.97 | 0.5 | 2.61 | 0.5
2018-08-19 04:00 | 14836.4141 | -0.048233 | 16.97 | 17.89 | 15.54 | 17.56 | 0.97 | 0.5 | 1.67 | 0.5
2018-08-19 05:00 | 15421.9391 | -0.048233 | 17.97 | 17.97 | 16.76 | 17.92 | 0.99 | 0.5 | 2.61 | 1
2018-08-19 06:00 | 15866.8619 | 31.6795 | 18.36 | 18.36 | 17.36 | 19.9 | 1.51 | 0.82 | 2.61 | 2.31
2018-08-19 07:00 | 14382.5326 | 146.508 | 18.38 | 18.38 | 18.42 | 20.01 | 1.51 | 0.85 | 2.61 | 2
2018-08-19 08:00 | 14885.2735 | 354.709 | 18.85 | 18.85 | 18.52 | 21.41 | 2.01 | 0.97 | 3.11 | 2.37
2018-08-19 09:00 | 15241.4912 | 561.675 | 20.38 | 20.53 | 19.43 | 27.56 | 2.24 | 0.82 | 3 | 2.5
2018-08-19 10:00 | 15635.4458 | 726.364 | 20.43 | 22.65 | 20.9 | 29.63 | 3.94 | 2 | 1.64 | 4.26
2018-08-19 11:00 | 17255.2825 | 553.718 | 21.89 | 26.3 | 22.28 | 38.04 | 5.16 | 1.43 | 1 | 5.09
2018-08-19 12:00 | 17326.4528 | 531.178 | 30.63 | 30.63 | 23.39 | 45.15 | 8.64 | 6.21 | 1 | 12.5
2018-08-19 13:00 | 17083.0295 | 666.445 | 38.42 | 38.42 | 22.81 | 49.02 | 19.96 | 7.09 | 1.37 | 15.17
2018-08-19 14:00 | 14999.3856 | 527.827 | 45.48 | 45.48 | 29.03 | 63.74 | 30 | 14.95 | 1 | 25
2018-08-19 15:00 | 14600.9756 | 246.448 | 49.79 | 49.79 | 29.14 | 79.55 | 44.21 | 20.94 | 2.08 | 33.55
2018-08-19 16:00 | 16271.1152 | 245.858 | 34.52 | 34.52 | 30.49 | 79.03 | 44.67 | 18 | 2.11 | 34.02
2018-08-19 17:00 | 14698.0409 | 140.622 | 21.89 | 31.27 | 30.19 | 51.23 | 17.82 | 9.74 | 2.11 | 13.34
2018-08-19 18:00 | 14431.6248 | 40.184 | 21.89 | 30.98 | 22.62 | 38.92 | 7.61 | 1.37 | 10 | 5.11
2018-08-19 19:00 | 14284.1542 | -0.048233 | 20.71 | 29.19 | 22.06 | 31.29 | 5 | 0.82 | 2.06 | 4.57
2018-08-19 20:00 | 14172.0542 | -0.048233 | 20.56 | 26.72 | 21.97 | 30.42 | 5 | 0.82 | 3.01 | 4
2018-08-19 21:00 | 15673.0291 | -0.048233 | 19.92 | 25.7 | 21.12 | 26.37 | 3.45 | 0.82 | 10 | 3
2018-08-19 22:00 | 15428.2691 | -0.048233 | 19.72 | 24.42 | 20 | 24.15 | 3 | 0.01 | 11.12 | 3.06
2018-08-19 23:00 | 13656.2042 | -0.048233 | 76.8 | 21.18 | 19.54 | 22.59 | 2 | 0.01 | 7.53 | 2.18
2018-08-20 | 15124.4291 | -0.048233 | 16.63 | 21.12 | 19.4 | 21.68 | 1 | 0.01 | 3.98 | 2.11
2018-08-20 01:00 | 13422.5042 | -0.048233 | 16.36 | 18.74 | 18.32 | 19.84 | 1 | 0.01 | 3.5 | 1
2018-08-20 02:00 | 14614.8641 | -0.048233 | 16.69 | 17.64 | 18.01 | 18.26 | 1 | 0.5 | 3.46 | 0.5
2018-08-20 03:00 | 12953.2042 | -0.048233 | 16.01 | 17.01 | 16.92 | 17.63 | 0.99 | 0.5 | 2.11 | 0.5
2018-08-20 04:00 | 14407.0291 | -0.048233 | 16.58 | 16.58 | 16.58 | 17.53 | 0.97 | 0.5 | 1 | 0.5
2018-08-20 05:00 | 12939.9042 | -0.048233 | 16.34 | 16.34 | 16.72 | 17.54 | 0.99 | 0.5 | 2.11 | 1.48
2018-08-20 06:00 | 12887.097 | 22.3653 | 16.36 | 16.36 | 15.27 | 19.14 | 1.75 | 0.85 | 2.62 | 2.5
2018-08-20 07:00 | 12802.5268 | 210.344 | 16.54 | 16.54 | 16.91 | 19.71 | 2 | 0.85 | 2.61 | 2.11
2018-08-20 08:00 | 13099.797 | 239.26 | 17.78 | 17.78 | 18.17 | 21.11 | 2.01 | 0.97 | 3 | 2.5
2018-08-20 09:00 | 13336.9103 | 299.853 | 18.39 | 18.8 | 19.48 | 23.31 | 2.11 | 0.97 | 3.01 | 2.31
2018-08-20 10:00 | 15487.3356 | 811.939 | 18.76 | 20.22 | 20.04 | 26.26 | 3.13 | 0.99 | 1 | 2.5
2018-08-20 11:00 | 15476.3077 | 666.486 | 19.63 | 21.69 | 20.49 | 30.12 | 5.35 | 0.99 | 1 | 5.53
2018-08-20 12:00 | 15635.406 | 565.29 | 20.8 | 24.77 | 23.29 | 32.72 | 5.98 | 2.28 | 1 | 5.98
2018-08-20 13:00 | 15615.1647 | 483.104 | 20.55 | 28.72 | 25.77 | 41.53 | 16.01 | 6.73 | 1.88 | 15.16
2018-08-20 14:00 | 15778.6844 | 619.099 | 20.57 | 29.75 | 24.22 | 49.11 | 21.6 | 0.99 | 1 | 19.22
2018-08-20 15:00 | 16054.2272 | 690.277 | 31.24 | 31.24 | 25.07 | 66.77 | 35.98 | 14.57 | 1.9 | 30.93
2018-08-20 16:00 | 15891.3648 | 342.905 | 19.88 | 30.17 | 23.26 | 65.73 | 35.11 | 15.24 | 2.11 | 29.51
2018-08-20 17:00 | 14190.814 | 244.699 | 19.64 | 29.24 | 23.01 | 41 | 16.52 | 0.99 | 2.11 | 15.72
2018-08-20 18:00 | 13929.5192 | 25.6518 | 19.51 | 25.88 | 21.81 | 34.21 | 9.73 | 0.99 | 15.11 | 6.49
2018-08-20 19:00 | 15420.8841 | -0.048233 | 19.14 | 27.41 | 21.66 | 28.81 | 5.39 | 0.97 | 2.31 | 5.16
2018-08-20 20:00 | 13888.9542 | -0.048233 | 18.98 | 25.43 | 21.63 | 29.62 | 5.39 | 0.82 | 2.61 | 4
2018-08-20 21:00 | 13892.7542 | -0.048233 | 19.38 | 25.15 | 20.51 | 26.44 | 3.94 | 0.82 | 4 | 3.22
2018-08-20 22:00 | 13628.6542 | -0.048233 | 18.41 | 21.64 | 19.6 | 22.81 | 2.48 | 0.01 | 13.3 | 2.41
2018-08-20 23:00 | 13413.0042 | -0.048233 | 17.11 | 22.9 | 18.87 | 22.86 | 1.51 | 0.01 | 8.61 | 2.21
2018-08-21 | 14786.8291 | -0.048233 | 15.63 | 20.77 | 17.96 | 19.87 | 0.99 | 0.01 | 8.61 | 1.31
2018-08-21 01:00 | 13177.4042 | -0.048233 | 14.73 | 19.41 | 16.77 | 18.47 | 0.97 | 0.01 | 3.5 | 0.5
2018-08-21 02:00 | 13091.9042 | -0.048233 | 15.11 | 18.92 | 15.82 | 17.6 | 0.97 | 0.5 | 3.44 | 0.5
2018-08-21 03:00 | 13075.7542 | -0.048233 | 9.93 | 18.45 | 12.94 | 17.06 | 0.97 | 0.5 | 2.61 | 0.5
2018-08-21 04:00 | 13580.2042 | -0.048233 | 15.16 | 18.09 | 10.91 | 17.54 | 0.97 | 0.5 | 1.05 | 0.5
2018-08-21 05:00 | 16365.1091 | -0.048233 | 16.21 | 18.44 | 10.89 | 19.14 | 0.97 | 0.5 | 2.61 | 1.31
2018-08-21 06:00 | 18507.0451 | 26.2228 | 16.88 | 19.35 | 10.9 | 21.58 | 1.91 | 0.85 | 2.61 | 2.5
2018-08-21 07:00 | 17709.1726 | 90.2343 | 16.42 | 28.43 | 12.28 | 21.17 | 1.91 | 0.85 | 3 | 2.1
2018-08-21 08:00 | 20304.8708 | 185.323 | 16.22 | 27.54 | 15.1 | 23.04 | 2 | 0.97 | 3.01 | 2.5
2018-08-21 09:00 | 21351.6101 | 270.493 | 17.63 | 24.94 | 18.12 | 28.02 | 2.28 | 0.97 | 3.11 | 2.59
2018-08-21 10:00 | 20799.1931 | 334.875 | 18.24 | 24.38 | 20 | 27.68 | 2.82 | 2 | 1.56 | 4.01
2018-08-21 11:00 | 18899.8054 | 376.532 | 19.5 | 26.84 | 21.98 | 30.4 | 4.72 | 3 | 0.65 | 4.79
2018-08-21 12:00 | 19701.8619 | 391.802 | 20.44 | 28.63 | 22.34 | 35.07 | 5.6 | 0.99 | 1 | 4.81
2018-08-21 13:00 | 21879.4815 | 384.845 | 28.38 | 28.38 | 23.05 | 42.31 | 15.45 | 7.18 | 1.25 | 14.25
2018-08-21 14:00 | 17944.511 | 343.959 | 28.2 | 27.67 | 24.38 | 49.02 | 21.22 | 0.99 | 1.86 | 15.67
2018-08-21 15:00 | 18614.9538 | 279.506 | 30.71 | 30.71 | 33.8 | 56.82 | 28.29 | 20.29 | 1 | 24.29
2018-08-21 16:00 | 16111.8451 | 192.837 | 40.82 | 40.82 | 36.19 | 52.26 | 37.12 | 22.76 | 1.9 | 32.64
2018-08-21 17:00 | 15591.9954 | 77.6267 | 31.04 | 31.04 | 32.91 | 42.83 | 21.21 | 12.41 | 2.11 | 17.21
2018-08-21 18:00 | 15294.8444 | 30.8362 | 29.97 | 29.97 | 23.8 | 35.05 | 13.77 | 0.99 | 2.61 | 4.04
2018-08-21 19:00 | 15271.2042 | -0.048233 | 28.51 | 28.51 | 21.88 | 30.99 | 6.61 | 0.97 | 2.61 | 3.54
2018-08-21 20:00 | 16992.8341 | -0.048233 | 22.78 | 28.21 | 22.01 | 29.98 | 5.77 | 0.82 | 2 | 4.24
2018-08-21 21:00 | 16583.4941 | -0.048233 | 21.64 | 24.93 | 21 | 31.98 | 4.57 | 0.82 | 4 | 3.71
2018-08-21 22:00 | 14560.6042 | -0.048233 | 19.75 | 21.55 | 20.16 | 24.59 | 2.84 | 0.01 | 10.34 | 2.6
2018-08-21 23:00 | 15606.5641 | -0.048233 | 17.82 | 21.78 | 19 | 21.84 | 2.16 | 0.01 | 8.11 | 2.16
2018-08-22 | 15391.3441 | -0.048233 | 16.49 | 18.84 | 19.23 | 19.82 | 0.97 | 0.01 | 3.51 | 1.41
2018-08-22 01:00 | 13596.3542 | -0.048233 | 15.59 | 19.07 | 18.13 | 18.87 | 0.95 | 0.01 | 3.5 | 0.5
2018-08-22 02:00 | 14977.7841 | -0.048233 | 15.17 | 18.3 | 16.95 | 18.19 | 0.95 | 0.5 | 3.01 | 0.5
2018-08-22 03:00 | 14736.1891 | -0.048233 | 14.7 | 17.32 | 16.53 | 18.02 | 0.95 | 0.5 | 2.11 | 0.44
2018-08-22 04:00 | 13726.5042 | -0.048233 | 14.98 | 17.3 | 16.94 | 18.28 | 0.95 | 0.5 | 1 | 0.5
2018-08-22 05:00 | 14754.4042 | -0.048233 | 16.09 | 17.84 | 17.87 | 19.19 | 0.97 | 0.5 | 2.11 | 1.11
2018-08-22 06:00 | 16902.7407 | 28.3586 | 16.95 | 20.23 | 17.91 | 21.95 | 1.51 | 0.97 | 2.61 | 2.22
2018-08-22 07:00 | 18356.926 | 233.08 | 16.99 | 19.52 | 17.91 | 22.18 | 2 | 0.97 | 2.61 | 2.2
2018-08-22 08:00 | 20988.0909 | 297.925 | 18.5 | 20.82 | 19.01 | 23.46 | 2 | 0.97 | 2.86 | 2.13
2018-08-22 09:00 | 20228.5753 | 299.005 | 19.18 | 21.95 | 21.04 | 25.48 | 3 | 0.97 | 2.61 | 3
2018-08-22 10:00 | 19701.4593 | 730.369 | 19.68 | 27.24 | 21.28 | 28.64 | 3.67 | 2.53 | 2 | 4.03
2018-08-22 11:00 | 18162.3936 | 547.309 | 20.35 | 28.6 | 22.29 | 35.42 | 6.61 | 2.5 | 1 | 5.82
2018-08-22 12:00 | 21692.488 | 799.6 | 31.94 | 31.94 | 22.41 | 40.64 | 6.9 | 6.53 | 1 | 11.64
2018-08-22 13:00 | 21748.3502 | 559.55 | 38.44 | 38.44 | 24.46 | 50.44 | 20.51 | 8.72 | 1.11 | 17.63
2018-08-22 14:00 | 21423.309 | 649.454 | 35.12 | 35.12 | 31.65 | 57.68 | 27.25 | 14.19 | 1 | 21.05
2018-08-22 15:00 | 19991.6761 | 415.456 | 35.73 | 35.73 | 36.01 | 76.63 | 41.76 | 21.33 | 1.55 | 36.65
2018-08-22 16:00 | 18155.0751 | 359.602 | 33.43 | 33.43 | 37.39 | 63.72 | 31 | 23.8 | 1.9 | 30.8
2018-08-22 17:00 | 17477.4708 | 135.323 | 32.39 | 32.38 | 35.93 | 50.7 | 19.98 | 15.77 | 2.7 | 19.77
2018-08-22 18:00 | 17053.1887 | 44.1599 | 40.37 | 40.37 | 29.87 | 39.36 | 14.82 | 0.99 | 2.11 | 5.48
2018-08-22 19:00 | 15209.4542 | -0.048233 | 37.3 | 37.3 | 22.28 | 33.26 | 6.11 | 0.97 | 2.21 | 4.09
2018-08-22 20:00 | 16889.4441 | -0.048233 | 32.24 | 32.24 | 22.34 | 31.26 | 5.52 | 0.97 | 2 | 4.45
2018-08-22 21:00 | 16509.6441 | -0.048233 | 20.23 | 28.7 | 20.21 | 30.49 | 4 | 0.97 | 4 | 3.83
2018-08-22 22:00 | 15885.0841 | -0.048233 | 19.35 | 25.63 | 18.39 | 25.94 | 2.53 | 0.01 | 9.64 | 3
2018-08-22 23:00 | 15520.0541 | -0.048233 | 18.18 | 22.29 | 16.98 | 23.18 | 1.05 | 0.01 | 6.85 | 1.61
2018-08-23 | 13961.1542 | -0.048233 | 17.14 | 21.69 | 16.75 | 21.87 | 1 | 0.01 | 10.53 | 2.11
2018-08-23 01:00 | 15312.2191 | -0.048233 | 18.22 | 21.2 | 11.15 | 20.68 | 0.95 | 0.01 | 2.7 | 1
2018-08-23 02:00 | 15022.0941 | -0.048233 | 16.79 | 20.96 | 9.18 | 20.27 | 0.95 | 0.61 | 2.07 | 0.61
2018-08-23 03:00 | 13497.5542 | -0.048233 | 16.81 | 20.23 | 9 | 19.74 | 0.95 | 0.61 | 1.68 | 0.61
2018-08-23 04:00 | 14175.8542 | -0.048233 | 16.41 | 19.95 | 9.32 | 19.52 | 0.95 | 0.61 | 0.25 | 1
2018-08-23 05:00 | 15296.8542 | -0.048233 | 16.19 | 20.38 | 9.34 | 19.99 | 0.95 | 0.61 | 1 | 1.53
2018-08-23 06:00 | 19067.1566 | 24.1342 | 16.57 | 21.36 | 15.2 | 22.04 | 1.99 | 1 | 2.11 | 2.5
2018-08-23 07:00 | 20051.3684 | 73.0364 | 16.54 | 21.21 | 15.17 | 22.44 | 2 | 1.05 | 2.61 | 2.11
2018-08-23 08:00 | 20752.8902 | 149.986 | 18.1 | 21.52 | 15.43 | 24.23 | 2 | 1.1 | 2.5 | 2.25
2018-08-23 09:00 | 21222.6068 | 221.215 | 56.07 | 56.07 | 17.89 | 28.21 | 3 | 1.14 | 2.11 | 3
2018-08-23 10:00 | 20614.8551 | 271.147 | 20.39 | 27.89 | 18.43 | 32.56 | 3.42 | 2.17 | 2.11 | 4.01
2018-08-23 11:00 | 18271.2179 | 303.861 | 19.98 | 28.13 | 19.21 | 33.75 | 6.25 | 3 | 1 | 6.18
2018-08-23 12:00 | 22031.4131 | 316.856 | 29.63 | 29.63 | 19.9 | 39.33 | 7.27 | 5.71 | 1 | 6.96
2018-08-23 13:00 | 22768.5595 | 306.573 | 37.77 | 37.77 | 20.96 | 47.95 | 16.15 | 5.7 | 2 | 14.04
2018-08-23 14:00 | 20230.6642 | 271.985 | 32.83 | 32.83 | 20.93 | 57.41 | 22.83 | 10.21 | 1.67 | 17.83
2018-08-23 15:00 | 16535.4074 | 221.692 | 33.2 | 33.2 | 21.63 | 68.62 | 39.48 | 29.7 | 1.71 | 35
2018-08-23 16:00 | 17992.4564 | 152.461 | 44.17 | 32.84 | 21.65 | 61.07 | 42.69 | 55.4873 | 2.21 | 39.18
2018-08-23 17:00 | 15425.7804 | 96.6636 | 31.26 | 31.26 | 21.63 | 47.47 | 23.66 | 15.98 | 2.47 | 20.78
2018-08-23 18:00 | 15029.3714 | 26.391 | 33.66 | 31.16 | 21.5 | 37.6 | 20.14 | 1 | 2 | 16.14
2018-08-23 19:00 | 15068.8542 | -0.048233 | 29.38 | 29.38 | 21.1 | 32.65 | 8.3 | 0.99 | 2.31 | 12.55
2018-08-23 20:00 | 16704.8191 | -0.048233 | 31.54 | 28.87 | 21.29 | 30.64 | 7.11 | 0.97 | 2.11 | 4.2
2018-08-23 21:00 | 14767.7042 | -0.048233 | 62.42 | 62.42 | 19.9 | 29.98 | 5.99 | 1 | 3.5 | 4.15
2018-08-23 22:00 | 14317.4042 | -0.048233 | 26.95 | 26.95 | 18.64 | 26.09 | 3 | 0.01 | 57.6962 | 3.14
2018-08-23 23:00 | 13980.1542 | -0.048233 | 28.38 | 27.02 | 17.01 | 23.38 | 1.15 | 0.01 | 22.29 | 2.61
2018-08-24 | 13697.0542 | -0.048233 | 18.95 | 21.03 | 11.95 | 21.28 | 0.99 | 0.01 | 12 | 2.11
2018-08-24 01:00 | 13374.0542 | -0.048233 | 16.73 | 20.11 | 9.21 | 20.38 | 0.95 | 0.01 | 3.42 | 0.95
2018-08-24 02:00 | 13258.1542 | -0.048233 | 16.36 | 19.31 | 7.55 | 19.5 | 0.95 | 0.5 | 2.61 | 0.5
2018-08-24 03:00 | 14645.4591 | -0.048233 | 15.34 | 19.01 | 7.49 | 19.21 | 0.95 | 0.5 | 2.11 | 0.5
2018-08-24 04:00 | 13886.1042 | -0.048233 | 15.34 | 18.94 | 8.85 | 19.07 | 0.95 | 0.5 | 0.25 | 0.5
2018-08-24 05:00 | 15241.7542 | -0.048233 | 16.93 | 19.66 | 10.53 | 19.58 | 0.95 | 0.5 | 1 | 1.64
2018-08-24 06:00 | 19274.9022 | 25.0495 | 19.9 | 21.05 | 17.49 | 22.7 | 1.5 | 0.97 | 2.11 | 2.5
2018-08-24 07:00 | 17079.1705 | 87.0742 | 19.84 | 21.17 | 18.15 | 23.19 | 1.5 | 0.97 | 2.61 | 2.21
2018-08-24 08:00 | 16950.0168 | 184.123 | 19.15 | 21.27 | 18.86 | 25.91 | 2.05 | 0.97 | 2.35 | 2.5
2018-08-24 09:00 | 17300.0149 | 214.542 | 20.33 | 22.55 | 19.37 | 28.36 | 3.07 | 0.97 | 2.61 | 2.61
2018-08-24 10:00 | 18742.9422 | 333.822 | 26.21 | 26.21 | 18.96 | 28.7 | 4.94 | 2.4 | 1 | 4
2018-08-24 11:00 | 17745.714 | 300.582 | 20.61 | 27.82 | 19.52 | 32.46 | 6.11 | 2.9 | 1 | 5
2018-08-24 12:00 | 15083.1035 | 308.951 | 29.79 | 29.79 | 22.72 | 37 | 8.44 | 8.79 | 1 | 10.92
2018-08-24 13:00 | 14221.1371 | 300.618 | 33.18 | 33.18 | 23.16 | 45.43 | 16.56 | 12.5 | 1.28 | 15
2018-08-24 14:00 | 13122.5343 | 339.194 | 77.51 | 77.51 | 22.85 | 49.02 | 27.52 | 18.86 | 1.87 | 20.3
2018-08-24 15:00 | 12086.2506 | 271.369 | 52.57 | 52.57 | 30.43 | 49.9 | 44.11 | 57.6173 | 2 | 35
2018-08-24 16:00 | 13041.2158 | 186.342 | 39.6 | 29.37 | 23.75 | 46.92 | 50.33 | 58.4573 | 2.11 | 42.15
2018-08-24 17:00 | 12777.2487 | 90.1362 | 32.24 | 31.58 | 23.94 | 38.11 | 27.39 | 15.63 | 2.41 | 19.63
2018-08-24 18:00 | 11465.7871 | 28.2496 | 31.43 | 29.55 | 22.99 | 30.83 | 16.86 | 1 | 1 | 12.51
2018-08-24 19:00 | 11414.2042 | -0.048233 | 30.23 | 27.32 | 22.5 | 28.73 | 5.93 | 0.97 | 2.11 | 3.78
2018-08-24 20:00 | 11462.6542 | -0.048233 | 32.66 | 28.04 | 22.46 | 29.04 | 5.8 | 0.97 | 2 | 3.2
2018-08-24 21:00 | 11371.4542 | -0.048233 | 69.48 | 27.21 | 18.78 | 27.92 | 3.58 | 0.97 | 3.11 | 2.52
2018-08-24 22:00 | 12671.5541 | -0.048233 | 63.36 | 24.31 | 17.96 | 23.67 | 3.42 | 0.01 | 27.44 | 3.42
2018-08-24 23:00 | 12405.6941 | -0.048233 | 19.5 | 21.23 | 17.76 | 22.04 | 2.5 | 0.01 | 14.54 | 2.61
2018-08-25 | 11067.4542 | -0.048233 | 19.06 | 21.14 | 15.58 | 21.61 | 2 | 0.01 | 3.5 | 2.21
2018-08-25 01:00 | 10966.7542 | -0.048233 | 17.64 | 21.13 | 14.96 | 20.51 | 1.85 | 0.01 | 3.28 | 1.01
2018-08-25 02:00 | 10772.9542 | -0.048233 | 16.25 | 20.79 | 14.09 | 19.84 | 1.78 | 0.5 | 2.72 | 1
2018-08-25 03:00 | 10591.5042 | -0.048233 | 15.69 | 20.01 | 12.78 | 19.39 | 1.51 | 0.5 | 2.61 | 0.72
2018-08-25 04:00 | 12255.8841 | -0.048233 | 16.24 | 20.13 | 12.76 | 19.44 | 1.51 | 0.5 | 1 | 1
2018-08-25 05:00 | 12403.5841 | -0.048233 | 17.22 | 20.76 | 14.92 | 20.17 | 1.85 | 0.5 | 2.11 | 2
2018-08-25 06:00 | 12346.1696 | 33.5304 | 19.58 | 21.29 | 16.76 | 23.12 | 2.01 | 0.97 | 2.6 | 2.8
2018-08-25 07:00 | 11024.5448 | 186.784 | 18.76 | 21.16 | 17.85 | 23.07 | 2.01 | 0.97 | 2.11 | 2.3
2018-08-25 08:00 | 11197.1142 | 436.436 | 18.73 | 20.57 | 18.2 | 23.9 | 2.21 | 1.09 | 2.11 | 3
2018-08-25 09:00 | 12611.9353 | 627.441 | 20.59 | 20.8 | 18.33 | 26.53 | 3.75 | 1.08 | 2.06 | 3.75
2018-08-25 10:00 | 12816.6612 | 851.494 | 21.22 | 21.22 | 19.15 | 29.23 | 6.31 | 0.99 | 1 | 4.6
2018-08-25 11:00 | 13075.1847 | 1132.54 | 21.81 | 21.81 | 18.92 | 31.64 | 9.59 | 0.99 | 1 | 10.7
2018-08-25 12:00 | 12790.3843 | 805.587 | 29.25 | 23.38 | 19.18 | 37.47 | 15 | 8.74 | 1 | 12.62
2018-08-25 13:00 | 11449.2594 | 739.852 | 30.26 | 25.25 | 23 | 40.78 | 18.85 | 10.18 | 1.25 | 14.25
2018-08-25 14:00 | 11709.0872 | 944.355 | 67.96 | 26.06 | 23.05 | 41.61 | 24.44 | 16.01 | 2.11 | 19.43
2018-08-25 15:00 | 12514.9765 | 652.537 | 38.33 | 28.5 | 23.22 | 38.37 | 38.22 | 56.7273 | 1.99 | 33.42
2018-08-25 16:00 | 7864.8552 | 447.795 | 37.18 | 22.81 | 24.06 | 33.64 | 36.72 | 29.35 | 3 | 31.62
2018-08-25 17:00 | 7777.0897 | 185.649 | 21.45 | 21.45 | 22.74 | 29.61 | 17.66 | 13.66 | 2.2 | 13.79
2018-08-25 18:00 | 5581.5591 | 26.3254 | 21.37 | 21.37 | 22.69 | 26.75 | 6.56 | 1.19 | 20 | 3.66
2018-08-25 19:00 | 5574.5542 | -0.048233 | 21.13 | 21.19 | 18.32 | 26.33 | 6.46 | 0.97 | 20 | 4
2018-08-25 20:00 | 5605.9042 | -0.048233 | 22.36 | 22.52 | 18.34 | 26.77 | 6.82 | 0.97 | 20 | 4
2018-08-25 21:00 | 5498.5542 | -0.048233 | 20.21 | 24.76 | 17.28 | 24.25 | 4.53 | 0.97 | 30.19 | 3.13
2018-08-25 22:00 | 5970.1941 | -0.048233 | 19.2 | 21.65 | 16.75 | 23.25 | 3.25 | 0.01 | 37.56 | 3.25
2018-08-25 23:00 | 5987.0741 | -0.048233 | 18.52 | 22.52 | 16.45 | 22.44 | 2.71 | 0.01 | 22.31 | 2.93
2018-08-26 | 5300.0042 | -0.048233 | 18.51 | 20.77 | 15.3 | 22.22 | 1.8 | 0.01 | 8.61 | 2.25
2018-08-26 01:00 | 5262.0042 | -0.048233 | 17.95 | 20.76 | 14.55 | 20.38 | 1.51 | 0.01 | 3.5 | 1.31
2018-08-26 02:00 | 5217.3542 | -0.048233 | 17.48 | 20.05 | 12.57 | 19.52 | 1.5 | 0.61 | 3 | 1.3
2018-08-26 03:00 | 5728.5991 | -0.048233 | 17.05 | 20.23 | 12.22 | 19.19 | 1.61 | 0.5 | 2.55 | 1.41
2018-08-26 04:00 | 5720.1591 | -0.048233 | 16.85 | 20.55 | 11.78 | 18.83 | 1.47 | 0.5 | 1.19 | 1.25
2018-08-26 05:00 | 5718.0491 | -0.048233 | 17.3 | 19.84 | 12.22 | 18.89 | 1.61 | 0.5 | 2.61 | 1.5
2018-08-26 06:00 | 5709.771 | 41.1052 | 18.05 | 18.05 | 12.26 | 20.24 | 1.75 | 0.82 | 2.99 | 3
2018-08-26 07:00 | 5183.6769 | 172.502 | 18.83 | 20.97 | 12.32 | 20.33 | 1.8 | 0.85 | 2.94 | 2.47
2018-08-26 08:00 | 5986.6197 | 433.521 | 18.36 | 21.36 | 14.57 | 21.72 | 2.83 | 0.97 | 3.11 | 3
2018-08-26 09:00 | 6175.8677 | 690.903 | 19.78 | 21.72 | 16.02 | 23.45 | 3.55 | 0.97 | 2.1 | 3.55
2018-08-26 10:00 | 6335.3003 | 806.024 | 21.8 | 22.26 | 15.08 | 23.7 | 3.41 | 0.99 | 1 | 4
2018-08-26 11:00 | 6991.8765 | 1007.87 | 51.33 | 22.22 | 23.4 | 26.49 | 5.01 | 0.99 | 0.71 | 5.01
2018-08-26 12:00 | 8161.3112 | 1106.84 | 31.02 | 20.75 | 33.17 | 27.89 | 5.87 | 2.01 | 1 | 5.01
2018-08-26 13:00 | 6975.6714 | 732.812 | 32.46 | 21.09 | 33.5 | 33.45 | 16.45 | 11.08 | 1.1 | 15.13
2018-08-26 14:00 | 7744.2212 | 875.494 | 59.32 | 21.12 | 38.96 | 33.56 | 23.27 | 14.46 | 1.8 | 16.06
2018-08-26 15:00 | 7446.7745 | 611.554 | 35.26 | 21.02 | 42.21 | 30.93 | 28.01 | 21.23 | 2 | 25.23
2018-08-26 16:00 | 5055.1939 | 425.653 | 52.97 | 21.4 | 42.97 | 29.71 | 34.24 | 24.76 | 2 | 31.75
2018-08-26 17:00 | 4843.6016 | 179.528 | 32.99 | 20.75 | 38.47 | 26.46 | 25.01 | 21.01 | 2 | 23.25
2018-08-26 18:00 | 6958.7767 | 29.9969 | 29.62 | 24.04 | 33.66 | 27.03 | 6.59 | 1 | 32 | 4.19
2018-08-26 19:00 | 6428.6042 | -0.048233 | 29.24 | 25.03 | 23.6 | 25.41 | 5.06 | 0.97 | 32.85 | 3.59
2018-08-26 20:00 | 6368.7542 | -0.048233 | 26.05 | 24.97 | 22.99 | 26.96 | 6.16 | 0.97 | 20 | 3
2018-08-26 21:00 | 7082.1641 | -0.048233 | 22.18 | 22.18 | 15.28 | 25.17 | 4.39 | 0.97 | 36.63 | 3.86
2018-08-26 22:00 | 6388.7042 | -0.048233 | 20.06 | 21.49 | 14 | 22.37 | 3.55 | 0.01 | 111.2334 | 3.55
2018-08-26 23:00 | 6401.0542 | -0.048233 | 18.88 | 21.1 | 12.83 | 21.14 | 2.39 | 0.01 | 30 | 2.58
2018-08-27 | 6344.0542 | -0.048233 | 17.99 | 21.26 | 12.31 | 25.29 | 1.61 | 0.01 | 4 | 1.75
2018-08-27 01:00 | 6335.5042 | -0.048233 | 16.99 | 20.74 | 10 | 20.68 | 1.47 | 0.01 | 3.44 | 1.25
2018-08-27 02:00 | 6975.6091 | -0.048233 | 16.1 | 19.77 | 10.18 | 19.38 | 1.47 | 0.5 | 2.65 | 1.25
2018-08-27 03:00 | 6268.0542 | -0.048233 | 12.5 | 19.36 | 9.47 | 19.06 | 1.47 | 0.5 | 2.11 | 1
2018-08-27 04:00 | 6285.1542 | -0.048233 | 14.7 | 19.03 | 9.78 | 18.74 | 1.47 | 0.5 | 1.39 | 1.11
2018-08-27 05:00 | 6327.9042 | -0.048233 | 16.1 | 18.98 | 7.7 | 19.02 | 1.47 | 0.5 | 2.61 | 1.27
2018-08-27 06:00 | 6326.8846 | 23.8785 | 17.41 | 18.76 | 7.17 | 20.98 | 1.5 | 0.85 | 3.5 | 2.31
2018-08-27 07:00 | 7005.2179 | 152.017 | 17.89 | 18.37 | 9.77 | 20.65 | 1.5 | 0.85 | 3.44 | 2.11
2018-08-27 08:00 | 6409.7174 | 373.071 | 18.03 | 18.85 | 11.19 | 22.95 | 2 | 0.97 | 3.46 | 2.5
2018-08-27 09:00 | 6320.5248 | 294.184 | 19.43 | 19.76 | 13.55 | 26.38 | 3.46 | 0.97 | 3.46 | 3.26
2018-08-27 10:00 | 7269.6663 | 443.679 | 19.68 | 21.08 | 13.46 | 27.75 | 3 | 2.5 | 1.3 | 5.38
2018-08-27 11:00 | 7293.4255 | 1139.29 | 21.17 | 21.17 | 14.19 | 42.8 | 5.46 | 1 | 0.71 | 6.66
2018-08-27 12:00 | 7091.7709 | 679.022 | 31.18 | 20.77 | 14.62 | 49.68 | 4.11 | 2.32 | 1 | 4.47
2018-08-27 13:00 | 7444.5192 | 633.336 | 31.69 | 20.86 | 14.79 | 55.66 | 19.44 | 10 | 1 | 15
2018-08-27 14:00 | 7559.7589 | 518.641 | 68.39 | 21.02 | 15.23 | 59.49 | 25.5 | 16.51 | 1.07 | 17.92
2018-08-27 15:00 | 8668.7694 | 428.843 | 352.6657 | 21 | 16.88 | 54.95 | 33.52 | 21.69 | 1 | 25
2018-08-27 16:00 | 8897.6421 | 346.784 | 39.1 | 21.06 | 22.74 | 50.34 | 34.32 | 53.3273 | 1.57 | 33.22
2018-08-27 17:00 | 8569.2565 | 86.518 | 46.92 | 21.14 | 21.85 | 40 | 19.86 | 15.86 | 2 | 18.84
2018-08-27 18:00 | 7763.3439 | 25.941 | 30.72 | 21.74 | 19.06 | 32.33 | 5 | 1 | 30 | 3.94
2018-08-27 19:00 | 8646.7291 | -0.048233 | 21.94 | 21.94 | 19.07 | 36.78 | 7.32 | 0.97 | 30 | 7.27
2018-08-27 20:00 | 8687.8741 | -0.048233 | 32.72 | 26.5 | 18.9 | 44.69 | 6.46 | 0.97 | 20 | 5.74
2018-08-27 21:00 | 7903.0042 | -0.048233 | 22.36 | 27.06 | 15.12 | 44.38 | 3.37 | 0.97 | 32 | 3.17
2018-08-27 22:00 | 8670.9941 | -0.048233 | 19.33 | 23.91 | 13.13 | 27.96 | 3 | 0.12 | 57.6962 | 3
2018-08-27 23:00 | 8618.2441 | -0.048233 | 18.4 | 21.26 | 12.37 | 21.73 | 2.04 | 0.12 | 29.71 | 2.5
2018-08-28 | 8588.7041 | -0.048233 | 17.25 | 20.84 | 12.06 | 24.31 | 1.61 | 0.01 | 7.41 | 2
2018-08-28 01:00 | 7726.3042 | -0.048233 | 14.54 | 18.78 | 11.06 | 21.24 | 1.47 | 0.01 | 3.5 | 1.25
2018-08-28 02:00 | 7659.8042 | -0.048233 | -0.7 | 18.2 | 11.15 | 19.54 | 1.5 | 0.5 | 3.47 | 1.01
2018-08-28 03:00 | 8360.8241 | -0.048233 | -0.35 | 17.36 | 10.22 | 19.44 | 1.5 | 0.5 | 2.61 | 1
2018-08-28 04:00 | 8381.9241 | -0.048233 | -0.37 | 16.13 | 10.2 | 19.17 | 1.52 | 0.5 | 1.43 | 1.01
2018-08-28 05:00 | 8439.9491 | -0.048233 | 15.5 | 16.47 | 11.18 | 20.45 | 1.75 | 0.5 | 2.6 | 2
2018-08-28 06:00 | 7572.119 | 24.6516 | 16.65 | 18.77 | 9.34 | 44.78 | 1.75 | 0.85 | 3.5 | 2.61
2018-08-28 07:00 | 8590.6097 | 208.758 | 16.86 | 20.17 | 7.36 | 45.04 | 1.9 | 0.85 | 3.5 | 2.28
2018-08-28 08:00 | 8951.9271 | 528.239 | 17 | 19 | 14.6 | 45.26 | 2.11 | 0.97 | 3.32 | 3.11
2018-08-28 09:00 | 9268.9884 | 791.771 | 18.26 | 18.97 | 14.96 | 50.71 | 2.75 | 0.97 | 3.43 | 3.11
2018-08-28 10:00 | 8838.896 | 996.101 | 19.31 | 19.39 | 15.64 | 73.04 | 3.62 | 2.19 | 1.63 | 5.01
2018-08-28 11:00 | 9092.7046 | 993.268 | 19.69 | 19.69 | 16.26 | 84.08 | 5.73 | 2.43 | 1 | 5.01
2018-08-28 12:00 | 9172.2215 | 1115.97 | 19.37 | 19.37 | 17.47 | 126.59 | 6.61 | 1.86 | 1 | 6.21
2018-08-28 13:00 | 9030.5974 | 945.892 | 30.76 | 19.92 | 18.37 | 129.08 | 16.34 | 7.41 | 1 | 13.51
2018-08-28 14:00 | 9525.7005 | 506.1 | 105.74 | 21.1 | 20.02 | 131.24 | 23.73 | 17.76 | 1.17 | 18
2018-08-28 15:00 | 8615.9613 | 676.433 | 30.03 | 20.42 | 19.89 | 139.11 | 29.11 | 19.46 | 1 | 24.26
2018-08-28 16:00 | 8432.4622 | 389.276 | 30.71 | 20.97 | 20.14 | 132.73 | 38.26 | 27.63 | 1 | 33.9
2018-08-28 17:00 | 8068.0232 | 217.656 | 31.32 | 20.96 | 20.15 | 127.45 | 23.83 | 18.06 | 2.09 | 19.92
2018-08-28 18:00 | 8595.8308 | 25.7069 | 20.51 | 20.51 | 18.27 | 124.55 | 6.03 | 11.06 | 40 | 2.61
2018-08-28 19:00 | 8495.8641 | -0.048233 | 21.09 | 21.09 | 18.03 | 125.94 | 5.89 | 1.28 | 40 | 3.01
2018-08-28 20:00 | 7746.2542 | -0.048233 | 48.37 | 22.82 | 17.99 | 129.12 | 7.11 | 1.1 | 20 | 3
2018-08-28 21:00 | 7702.5542 | -0.048233 | 44.31 | 21.66 | 16.02 | 125.31 | 3.6 | 1.04 | 20 | 3.6
2018-08-28 22:00 | 7678.8042 | -0.048233 | 19.36 | 20.01 | 14.77 | 45.94 | 3.25 | 0.01 | 59.6462 | 3.25
2018-08-28 23:00 | 7658.8542 | -0.048233 | 18.22 | 18.22 | 13.95 | 30.84 | 2 | 0.01 | 30 | 2.77
2018-08-29 | 8512.7441 | -0.048233 | 17.17 | 17.17 | 15.66 | 22.75 | 1.72 | 0.01 | 20 | 2.21
2018-08-29 01:00 | 8464.2141 | -0.048233 | 14.7 | 14.7 | 14.1 | 19.2 | 1.61 | 0.01 | 3.5 | 1.41
2018-08-29 02:00 | 7542.0042 | -0.048233 | 13.97 | 13.97 | 12.44 | 17.9 | 1.61 | 0.91 | 3.5 | 1.2
2018-08-29 03:00 | 8310.1841 | -0.048233 | 13.26 | 13.26 | 12.48 | 17.82 | 1.61 | 0.5 | 2 | 1.01
2018-08-29 04:00 | 7768.1042 | -0.048233 | 16 | 16 | 12.33 | 17.81 | 1.5 | 0.5 | 1.3 | 1.11
2018-08-29 05:00 | 8674.1591 | -0.048233 | 17.03 | 17.03 | 15.01 | 19.2 | 1.61 | 0.5 | 2.99 | 1.41
2018-08-29 06:00 | 8782.848 | 19.9744 | 17.85 | 18.59 | 15.77 | 25.23 | 1.99 | 1.12 | 3.06 | 2
2018-08-29 07:00 | 8064.4673 | 154.913 | 17.9 | 19.74 | 15.05 | 24.75 | 2 | 1.15 | 3.01 | 2.1
2018-08-29 08:00 | 9747.1534 | 285.008 | 18.86 | 19.63 | 15.71 | 26.24 | 2 | 1.06 | 3.46 | 2.38
2018-08-29 09:00 | 9661.9303 | 578.453 | 20.16 | 20.86 | 17.44 | 28.72 | 2.5 | 1.05 | 3.01 | 3
2018-08-29 10:00 | 10152.0952 | 860.416 | 21.02 | 21.51 | 18.58 | 32.65 | 3.56 | 1.22 | 3.01 | 4.85
2018-08-29 11:00 | 11602.0407 | 909.195 | 22.96 | 22.96 | 20.27 | 38.34 | 5.14 | 2.62 | 1 | 5.01
2018-08-29 12:00 | 11840.7851 | 886.493 | 21.24 | 21.24 | 19.14 | 117.75 | 6.67 | 5.95 | 0.56 | 5.58
2018-08-29 13:00 | 10816.6183 | 811.914 | 21.73 | 21.73 | 30.58 | 128.89 | 20.59 | 12.67 | 1 | 17.65
2018-08-29 14:00 | 11003.9991 | 886.157 | 29.29 | 23.26 | 35.26 | 59.26 | 23.87 | 9.34 | 1.15 | 19.29
2018-08-29 15:00 | 10851.2762 | 551.396 | 34.78 | 27.03 | 39.54 | 89.81 | 24.54 | 14.16 | 1 | 18.96
2018-08-29 16:00 | 10991.7251 | 419.237 | 30.7 | 27.04 | 39.59 | 103.94 | 30.55 | 19.31 | 1.24 | 27.71
2018-08-29 17:00 | 10683.9375 | 144.25 | 34.07 | 29.35 | 35.26 | 94.94 | 18.42 | 13.11 | 2.11 | 17.11
2018-08-29 18:00 | 10322.3096 | 25.5891 | 29.71 | 27.4 | 33.92 | 74.79 | 5.94 | 1 | 32 | 2.95
2018-08-29 19:00 | 11292.6691 | -0.048233 | 32.13 | 32.13 | 20.08 | 75 | 5.42 | 1.06 | 25.3 | 3.86
2018-08-29 20:00 | 11283.1741 | -0.048233 | 286.6357 | 242.31 | 23.16 | 86.77 | 6.76 | 1.22 | 20 | 6.37
2018-08-29 21:00 | 9924.6042 | -0.048233 | 1248.9811 | 981.37 | 18.16 | 80.17 | 3.75 | 1.22 | 29.84 | 3.72
2018-08-29 22:00 | 9731.7542 | -0.048233 | 19.74 | 26.53 | 15.77 | 34.9 | 2.94 | 0.01 | 40 | 3
2018-08-29 23:00 | 10563.6641 | -0.048233 | 19.14 | 24.62 | 15.48 | 27.36 | 2.09 | 0.01 | 40 | 2.37
2018-08-30 | 9414.4542 | -0.048233 | 1602.3511 | 1334.74 | 14.79 | 22.08 | 1.89 | 0.01 | 20 | 1.2
2018-08-30 01:00 | 10294.6391 | -0.048233 | 18.63 | 28.97 | 14.03 | 20.24 | 1.5 | 0.01 | 3.4 | 1
2018-08-30 02:00 | 9209.2542 | -0.048233 | 17.74 | 18.19 | 12.49 | 19.56 | 1.47 | 0.61 | 2.61 | 1
2018-08-30 03:00 | 9095.2542 | -0.048233 | 17.29 | 17.77 | 8.17 | 18.96 | 1.5 | 0.5 | 2.05 | 1
2018-08-30 04:00 | 9442.0042 | -0.048233 | 17.13 | 17.95 | 7.12 | 18.48 | 1.47 | 0.5 | 1 | 1
2018-08-30 05:00 | 9521.8042 | -0.048233 | 991.4911 | 723.88 | 7.25 | 19.69 | 1.5 | 0.5 | 2.17 | 1.3
2018-08-30 06:00 | 10726.4561 | 24.257 | 17.37 | 20.2 | 10.03 | 23.41 | 1.89 | 0.97 | 2.61 | 2
2018-08-30 07:00 | 10840.2537 | 179.122 | 17.15 | 20.23 | 11.71 | 24.68 | 1.89 | 0.97 | 2.21 | 1.2
2018-08-30 08:00 | 12077.5735 | 488.937 | 17.89 | 20.13 | 16.53 | 24.05 | 1.89 | 1 | 1.97 | 2.01
2018-08-30 09:00 | 11622.4986 | 497.209 | 18.61 | 21.45 | 17.3 | 26.44 | 2.27 | 1.05 | 2 | 3
2018-08-30 10:00 | 12118.0233 | 743.814 | 19.63 | 21.86 | 18.45 | 30.53 | 3.75 | 0.99 | 1 | 3.89
2018-08-30 11:00 | 13782.2742 | 907.767 | 21.99 | 23.08 | 19.73 | 32.73 | 4.69 | 2.75 | 1 | 4.49
2018-08-30 12:00 | 12611.8039 | 946.583 | 23.32 | 23.32 | 19.76 | 37.5 | 5 | 2.99 | 0.71 | 3.5
2018-08-30 13:00 | 14319.4306 | 1003.92 | 28.76 | 26.13 | 20.55 | 43.44 | 17.33 | 7.59 | 2 | 17.33
2018-08-30 14:00 | 14567.0148 | 874.597 | 29.57 | 29.36 | 21.89 | 56.47 | 20.64 | 1.7 | 1 | 18.2
2018-08-30 15:00 | 14209.0048 | 599.251 | 36.41 | 28.67 | 22.55 | 64.48 | 24.52 | 13.12 | 1 | 21.72
2018-08-30 16:00 | 12282.6326 | 317.087 | 72.47 | 31.66 | 22.92 | 72.87 | 35.6 | 18.62 | 1.64 | 28.77
2018-08-30 17:00 | 13288.2536 | 89.501 | 37.24 | 31.07 | 22.56 | 60.74 | 28.43 | 12.12 | 2 | 22.08
2018-08-30 18:00 | 13031.9021 | 23.5138 | 31.75 | 28.6 | 22.33 | 44.12 | 15.22 | 1.27 | 2.11 | 11.65
2018-08-30 19:00 | 12805.5391 | -0.048233 | 30.54 | 27.2 | 21.26 | 42.48 | 8.4 | 1.23 | 2 | 9.56
2018-08-30 20:00 | 12978.5591 | -0.048233 | 28.84 | 28.84 | 21.25 | 40.65 | 7.82 | 0.99 | 1 | 6.75
2018-08-30 21:00 | 12747.5141 | -0.048233 | 27.84 | 27.84 | 17.73 | 35.47 | 3.75 | 0.99 | 20 | 3.75
2018-08-30 22:00 | 11316.3542 | -0.048233 | 19.39 | 21.47 | 16.95 | 28.04 | 2.66 | 0.01 | 34.88 | 2.4
2018-08-30 23:00 | 12339.2291 | -0.048233 | 18.69 | 20.23 | 16.92 | 22.97 | 2 | 0.01 | 38.34 | 1.2
2018-08-31 | 10900.2542 | -0.048233 | 18.43 | 18.5 | 12.92 | 30.45 | 1.61 | 0.01 | 11.22 | 2.2
2018-08-31 01:00 | 11817.0041 | -0.048233 | 17.24 | 18 | 12.26 | 28.37 | 1.61 | 0.01 | 3.5 | 1.41
2018-08-31 02:00 | 11583.8491 | -0.048233 | 16.58 | 17.16 | 10.47 | 23.91 | 1.61 | 0.5 | 3.5 | 1
2018-08-31 03:00 | 10229.5542 | -0.048233 | 16.11 | 16.53 | 10.54 | 23.31 | 1.61 | 0.5 | 3.4 | 1
2018-08-31 04:00 | 11591.2341 | -0.048233 | 15.83 | 16.58 | 12.18 | 23.5 | 1.52 | 0.5 | 1 | 1
2018-08-31 05:00 | 10838.5042 | -0.048233 | 16.73 | 17.27 | 12.09 | 24.83 | 1.61 | 0.5 | 3.5 | 1.41
2018-08-31 06:00 | 13477.7404 | 23.1094 | 18.74 | 18.74 | 16.6 | 28.03 | 2 | 0.97 | 2.61 | 2.3
2018-08-31 07:00 | 13465.273 | 98.9716 | 18.39 | 19.01 | 17.41 | 27.07 | 2 | 0.97 | 2.61 | 1
2018-08-31 08:00 | 13929.2363 | 285.354 | 18.18 | 19.35 | 17.4 | 29.57 | 2 | 0.99 | 3.01 | 2.5
2018-08-31 09:00 | 14773.2229 | 766.761 | 20.48 | 20.95 | 18.02 | 32.32 | 3.11 | 0.99 | 2 | 3
2018-08-31 10:00 | 15275.4006 | 901.369 | 21.48 | 21.48 | 17.86 | 37.37 | 4 | 2.53 | 1.46 | 4.03
2018-08-31 11:00 | 16796.6845 | 660.028 | 30.05 | 25.28 | 29.98 | 42.37 | 5.26 | 2.76 | 1 | 5.26
2018-08-31 12:00 | 17219.1266 | 387.447 | 32.63 | 28.44 | 31.68 | 52.43 | 14.44 | 1 | 0.71 | 14.44
2018-08-31 13:00 | 17767.8215 | 461.537 | 34.75 | 34.75 | 33.11 | 64.04 | 20 | 9.94 | 1.02 | 16.9
2018-08-31 14:00 | 15353.3243 | 579.394 | 59.93 | 59.93 | 33.72 | 82.53 | 30.52 | 7.32 | 1 | 23.8
2018-08-31 15:00 | 14456.6582 | 436.535 | 39.93 | 29.95 | 42.36 | 91.9 | 39.12 | 9.97 | 1 | 28.2
2018-08-31 16:00 | 14008.756 | 161.059 | 46.03 | 46.03 | 42.32 | 99.87 | 49.07 | 18.38 | 1.96 | 39.63
2018-08-31 17:00 | 13846.7801 | 95.558 | 48.5 | 48.5 | 40.94 | 73.69 | 32 | 11.58 | 2 | 20.54
2018-08-31 18:00 | 13533.8093 | 20.1151 | 37.8 | 37.8 | 32.7 | 51.91 | 14 | 1.49 | 3.11 | 10.78
2018-08-31 19:00 | 13503.2542 | -0.048233 | 30.57 | 27.59 | 31.46 | 49.44 | 12.34 | 1.4 | 3.11 | 11.49
2018-08-31 20:00 | 13404.4542 | -0.048233 | 30.6 | 26.63 | 29.42 | 49.39 | 7.62 | 1.09 | 1 | 6.3
2018-08-31 21:00 | 13121.3542 | -0.048233 | 23 | 24.29 | 17.36 | 44.63 | 4.49 | 1 | 20 | 4.49
2018-08-31 22:00 | 14278.3191 | -0.048233 | 19.81 | 21.65 | 16.83 | 32.74 | 3 | 0.01 | 30 | 2.61
2018-08-31 23:00 | 9477.1542 | -0.048233 | 18.98 | 19.91 | 16.61 | 30.66 | 2.23 | 0.01 | 27.74 | 2.21
2018-09-01 | 15714.1741 | -0.048233 | 18.53 | 18.53 | 13.07 | 23.79 | 2.05 | 0.5 | 10.43 | 2.61
2018-09-01 01:00 | 15690.9641 | -0.048233 | 18.22 | 18.22 | 11.39 | 22.28 | 1.61 | 0.5 | 3.15 | 1.2
2018-09-01 02:00 | 15536.9341 | -0.048233 | 17.46 | 17.46 | 10.08 | 21.29 | 1.59 | 0.97 | 2.11 | 1
2018-09-01 03:00 | 13838.6042 | -0.048233 | 16.63 | 16.63 | 7 | 21.36 | 1.5 | 0.97 | 2 | 1
2018-09-01 04:00 | 14337.3542 | -0.048233 | 16.15 | 16.15 | 9.73 | 21.12 | 1.53 | 0.97 | 1.85 | 1.01
2018-09-01 05:00 | 15441.2542 | -0.048233 | 16.66 | 16.66 | 11.93 | 21.56 | 1.97 | 0.97 | 9.11 | 2.11
2018-09-01 06:00 | 17210.1542 | -0.048233 | 17.46 | 17.46 | 15.08 | 26.13 | 2 | 1 | 3.05 | 3.75
2018-09-01 07:00 | 17704.8441 | 238.678 | 18.23 | 18.23 | 15.87 | 26.38 | 2 | 1 | 3.5 | 1
2018-09-01 08:00 | 20302.3388 | 540.923 | 18.07 | 18.07 | 16.56 | 27.04 | 2.61 | 0.97 | 8.61 | 2.11
2018-09-01 09:00 | 21857.5607 | 818.067 | 19.75 | 21.42 | 17.23 | 33.53 | 2.65 | 0.97 | 3.5 | 2.21
2018-09-01 10:00 | 19970.7613 | 976.854 | 19.68 | 21.67 | 16.05 | 43.65 | 4.55 | 6.55 | 1.08 | 4.55
2018-09-01 11:00 | 19587.1494 | 858.052 | 26.7 | 26.7 | 15.69 | 58.02 | 7.15 | 7 | 1 | 7.06
2018-09-01 12:00 | 23433.0692 | 1106.44 | 29.6 | 29.6 | 32.21 | 52.78 | 15 | 9.2 | 0.61 | 13.54
2018-09-01 13:00 | 21499.1935 | 1081.73 | 57.36 | 57.36 | 35.34 | 60.16 | 22.24 | 16.92 | 1.11 | 17.92
2018-09-01 14:00 | 21904.0197 | 956.104 | 33.74 | 33.74 | 35.33 | 70.26 | 30.91 | 7.67 | 1.79 | 24.21
2018-09-01 15:00 | 20445.458 | 625.581 | 38.58 | 38.58 | 35.66 | 82.1 | 36.95 | 9.66 | 1 | 25.49
2018-09-01 16:00 | 19862.6707 | 497.176 | 32.95 | 32.95 | 39.33 | 84.54 | 41.19 | 14.4 | 1 | 30.2
2018-09-01 17:00 | 19089.1521 | 211.983 | 324.4957 | 280.17 | 36.09 | 54.38 | 18.52 | 8.07 | 2 | 14.22
2018-09-01 18:00 | 16609.5733 | 13.7614 | 32.45 | 32.45 | 32.38 | 42.72 | 13.27 | 9.45 | 3.5 | 13.05
2018-09-01 19:00 | 18214.5241 | -0.048233 | 29.06 | 29.06 | 16.06 | 38.82 | 8.23 | 1.64 | 2.11 | 4.9
2018-09-01 20:00 | 16268.7042 | -0.048233 | 27.88 | 27.88 | 16.99 | 38.84 | 8.13 | 1.34 | 15 | 5.06
2018-09-01 21:00 | 17544.5991 | -0.048233 | 30.06 | 30.06 | 15.2 | 37.95 | 3.75 | 1.29 | 22.01 | 3.3
2018-09-01 22:00 | 17280.8491 | -0.048233 | 20.65 | 26.97 | 14.92 | 27.72 | 3 | 0.5 | 30 | 2.61
2018-09-01 23:00 | 15012.8042 | -0.048233 | 18.65 | 23.09 | 14.39 | 26.06 | 3 | 0.5 | 20 | 2.61
2018-09-02 | 16003.2441 | -0.048233 | 17.98 | 21.2 | 11.09 | 23.42 | 1.67 | 0.5 | 10.26 | 2.11
2018-09-02 01:00 | 14289.8542 | -0.048233 | 17.7 | 21.44 | 7 | 21.42 | 1.61 | 0.45 | 3.15 | 1
2018-09-02 02:00 | 15544.3191 | -0.048233 | 16.9 | 19.25 | 4.86 | 20.31 | 1.61 | 0.97 | 2.18 | 1
2018-09-02 03:00 | 14030.5042 | -0.048233 | 16.43 | 17.75 | 4.57 | 20.76 | 1.61 | 0.97 | 2.1 | 1
2018-09-02 04:00 | 14363.0042 | -0.048233 | 16.3 | 17.24 | 4.55 | 20.67 | 1.61 | 0.62 | 2 | 1
2018-09-02 05:00 | 17243.9241 | -0.048233 | 15.95 | 15.95 | 6.88 | 20.94 | 2 | 0.89 | 8.61 | 2.1
2018-09-02 06:00 | 17767.8042 | -0.048233 | 16.49 | 16.49 | 9.12 | 23.55 | 2.11 | 1.01 | 3.11 | 3.39
2018-09-02 07:00 | 20804.2097 | 238.63 | 17.89 | 17.89 | 9.93 | 23.69 | 2.11 | 1 | 3.5 | 1
2018-09-02 08:00 | 21253.5584 | 534.553 | 18.71 | 18.71 | 11.36 | 25.69 | 2.19 | 1.03 | 10.53 | 2.61
2018-09-02 09:00 | 19805.1972 | 809.576 | 20.81 | 20.81 | 13.98 | 24.71 | 3 | 1.03 | 15.8 | 3.16
2018-09-02 10:00 | 22509.0242 | 991.568 | 22.11 | 22.11 | 12.58 | 30.38 | 4 | 1.02 | 1 | 3.7
2018-09-02 11:00 | 19935.9495 | 1113.21 | 29.05 | 29.05 | 12.8 | 37.29 | 4.28 | 1.02 | 1 | 4
2018-09-02 12:00 | 23337.4229 | 1153.78 | 30.02 | 30.02 | 12.84 | 42.41 | 6 | 5.5 | 1 | 4.51
2018-09-02 13:00 | 22250.583 | 1114.6 | 150.71 | 42.86 | 12.54 | 47.33 | 22.8 | 15 | 0.86 | 19.35
2018-09-02 14:00 | 18727.0469 | 950.681 | 34.18 | 34.11 | 40.95 | 56.9 | 25.2 | 1.72 | 2.11 | 20.49
2018-09-02 15:00 | 17562.4733 | 645.814 | 57.12 | 36.87 | 38.9 | 64.48 | 31.54 | 9.04 | 1 | 21.09
2018-09-02 16:00 | 18907.6066 | 323.902 | 161.26 | 161.26 | 39.59 | 64.32 | 35.09 | 11.82 | 1 | 31.79
2018-09-02 17:00 | 16695.6078 | 150.324 | 148.37 | 148.37 | 36.37 | 44.79 | 19.39 | 1.34 | 2 | 14.92
2018-09-02 18:00 | 15904.3236 | 13.3933 | 47.98 | 47.98 | 14.31 | 36.31 | 11.08 | 1.27 | 4.5 | 6
2018-09-02 19:00 | 16034.0542 | -0.048233 | 30.61 | 30.61 | 15.2 | 34.51 | 8.74 | 0.97 | 2.61 | 5
2018-09-02 20:00 | 15924.8042 | -0.048233 | 34.97 | 29.32 | 15.38 | 32.66 | 5.73 | 0.97 | 17.62 | 3.24
2018-09-02 21:00 | 17554.0941 | -0.048233 | 21.94 | 22.19 | 13.04 | 29.76 | 3.4 | 0.97 | 20 | 2.01
2018-09-02 22:00 | 16969.6241 | -0.048233 | 21.65 | 25.3 | 12.27 | 24.3 | 3 | 0.5 | 20 | 3.01
2018-09-02 23:00 | 16494.8741 | -0.048233 | 19.77 | 21.23 | 11.47 | 24.91 | 2 | 0.5 | 13.71 | 2
2018-09-03 | 14308.8542 | -0.048233 | 18.34 | 20.99 | 9.49 | 23.44 | 1.59 | 0.5 | 3.46 | 2
2018-09-03 01:00 | 15612.8941 | -0.048233 | 17.31 | 20.52 | 6.28 | 21.87 | 1.47 | 0.5 | 3.15 | 1.27
2018-09-03 02:00 | 13990.6042 | -0.048233 | 16.57 | 20.6 | 5.43 | 20.62 | 1.47 | 0.82 | 2.61 | 1
2018-09-03 03:00 | 15267.9091 | -0.048233 | 15.77 | 20.45 | 5.03 | 19.86 | 1.45 | 0.82 | 2.39 | 1
2018-09-03 04:00 | 13714.1542 | -0.048233 | 16.24 | 20.36 | 5.03 | 19.42 | 1.47 | 0.82 | 2.11 | 1.01
2018-09-03 05:00 | 13809.1542 | -0.048233 | 16.59 | 19.99 | 5.02 | 20.21 | 1.61 | 0.82 | 3.5 | 1.9
2018-09-03 06:00 | 15382.9041 | -0.048233 | 17.05 | 19.89 | 4.94 | 24.9 | 2 | 0.99 | 3.5 | 3.1
2018-09-03 07:00 | 15602.4066 | 206.011 | 17.24 | 19.51 | 6.33 | 24.92 | 2 | 1 | 3.46 | 2
2018-09-03 08:00 | 14429.9328 | 498.403 | 18.12 | 20.25 | 8.93 | 23.08 | 2 | 1.02 | 5 | 2.5
2018-09-03 09:00 | 14795.3371 | 763.039 | 18.06 | 21.08 | 9.97 | 23.9 | 3 | 1 | 3.33 | 3
2018-09-03 10:00 | 15127.3288 | 886.504 | 19.02 | 23.57 | 11.35 | 28.22 | 3.11 | 0.99 | 1 | 4.08
2018-09-03 11:00 | 17180.9282 | 1010.24 | 19.88 | 27.11 | 11.97 | 29.83 | 5.81 | 0.99 | 1 | 5.08
2018-09-03 12:00 | 15426.4467 | 924.365 | 29.31 | 29.31 | 11.8 | 34.96 | 8.25 | 8.34 | 1 | 6.46
2018-09-03 13:00 | 17268.9985 | 886.719 | 33.85 | 32.51 | 38.33 | 45.37 | 18.95 | 15.38 | 1 | 15.98
2018-09-03 14:00 | 17010.8137 | 423.994 | 46.95 | 46.95 | 43.45 | 49.81 | 20.33 | 1.22 | 2.11 | 16.5
2018-09-03 15:00 | 17083.9262 | 476.295 | 45.79 | 33.89 | 43.53 | 64.21 | 32.59 | 1.22 | 1.6 | 27.53
2018-09-03 16:00 | 17092.0909 | 428.034 | 71.14 | 42.79 | 43.27 | 63.3 | 34.52 | 14.99 | 1 | 30.52
2018-09-03 17:00 | 15092.1921 | 144.518 | 35.64 | 32.88 | 43.29 | 42.56 | 16.62 | 1.22 | 2 | 12.32
2018-09-03 18:00 | 15003.6854 | 11.3531 | 37.1 | 37.1 | 33.45 | 34.88 | 12.53 | 1.26 | 3.5 | 4.24
2018-09-03 19:00 | 16306.0291 | -0.048233 | 36.77 | 29.45 | 16.71 | 33.11 | 7.89 | 0.97 | 2.61 | 6.49
2018-09-03 20:00 | 16283.8741 | -0.048233 | 36.03 | 28.43 | 13.94 | 30.43 | 6.54 | 0.97 | 15 | 4.47
2018-09-03 21:00 | 14541.6042 | -0.048233 | 21.85 | 22.57 | 12.64 | 27.12 | 4.03 | 0.97 | 20 | 3.28
2018-09-03 22:00 | 15947.3291 | -0.048233 | 21.8 | 21.8 | 9.92 | 24.53 | 3.01 | 0.5 | 23.52 | 3.01
2018-09-03 23:00 | 15573.8591 | -0.048233 | 18.74 | 20.96 | 9.9 | 23.08 | 2.14 | 0.5 | 20 | 2.14
2018-09-04 | 13993.4542 | -0.048233 | 18.43 | 30.65 | 10 | 21.19 | 1.61 | 0.5 | 3.46 | 2.11
2018-09-04 01:00 | 15424.0491 | -0.048233 | 16.71 | 21.68 | 8.88 | 20.13 | 1.59 | 0.5 | 3.5 | 1.01
2018-09-04 02:00 | 15376.5741 | -0.048233 | 14.43 | 19.91 | 5.29 | 18.7 | 1.59 | 0.89 | 3.3 | 1
2018-09-04 03:00 | 15338.5941 | -0.048233 | 12.72 | 15.94 | 4.88 | 18.12 | 1.59 | 0.89 | 2.75 | 0.01
2018-09-04 04:00 | 13794.9042 | -0.048233 | 14.9 | 16.46 | 4.86 | 17.85 | 1.59 | 0.89 | 3.11 | 1
2018-09-04 05:00 | 13937.4042 | -0.048233 | 14.77 | 16.59 | 4.94 | 17.98 | 2 | 0.89 | 4.07 | 2
2018-09-04 06:00 | 13843.3542 | -0.048233 | 15.34 | 17.68 | 5.11 | 19.5 | 2 | 0.99 | 2.61 | 3.11
2018-09-04 07:00 | 15351.4116 | 243.101 | 51.08 | 51.08 | 8.94 | 22.91 | 2 | 0.99 | 2.61 | 2
2018-09-04 08:00 | 15558.6072 | 480.495 | 16.65 | 16.65 | 9.03 | 27.19 | 2.11 | 0.99 | 3.46 | 2.34
2018-09-04 09:00 | 14278.6121 | 613.118 | 17.64 | 20.24 | 12.97 | 23.55 | 2.61 | 0.99 | 13.34 | 2.61
2018-09-04 10:00 | 14755.9548 | 873.584 | 18.05 | 20.27 | 13.68 | 24.47 | 3.73 | 1.03 | 1 | 4.33
2018-09-04 11:00 | 14935.862 | 1034.96 | 19.56 | 21.34 | 14.6 | 28.48 | 5.65 | 1.04 | 1 | 5.24
2018-09-04 12:00 | 16919.6996 | 1028.63 | 28.08 | 27.77 | 15.81 | 34.14 | 8.25 | 1.31 | 1 | 6.31
2018-09-04 13:00 | 15470.37 | 1071.6 | 33.4 | 29.94 | 15.84 | 41.91 | 15.18 | 9.33 | 1 | 13.68
2018-09-04 14:00 | 17164.0493 | 957.241 | 36.92 | 31.73 | 15.44 | 46.95 | 19.92 | 1 | 1.1 | 16.64
2018-09-04 15:00 | 17002.6986 | 767.302 | 38.54 | 33.35 | 16 | 59.91 | 32.47 | 15.07 | 1 | 25.51
2018-09-04 16:00 | 15094.4046 | 507.847 | 36.68 | 35.41 | 17.03 | 61.66 | 41.6 | 20.63 | 1 | 36.74
2018-09-04 17:00 | 14372.4094 | 201.852 | 51.58 | 51.58 | 16.87 | 40.65 | 20.74 | 11.1 | 1.81 | 15.1
2018-09-04 18:00 | 15344.5483 | 10.5955 | 34.38 | 34.38 | 16.39 | 36.8 | 16.26 | 9.84 | 3.5 | 4
2018-09-04 19:00 | 15099.1091 | -0.048233 | 20.34 | 30.96 | 17.93 | 30.83 | 6.03 | 0.82 | 2.21 | 3.97
2018-09-04 20:00 | 13703.7042 | -0.048233 | 29.72 | 29.72 | 18.04 | 30.5 | 5.46 | 0.82 | 9.5 | 3
2018-09-04 21:00 | 15380.7941 | -0.048233 | 19.16 | 24.3 | 16.01 | 26.17 | 3 | 0.82 | 29.4 | 3
2018-09-04 22:00 | 15335.4291 | -0.048233 | 18.85 | 21.38 | 13.33 | 24.46 | 2.61 | 0.5 | 25 | 3
2018-09-04 23:00 | 15140.2541 | -0.048233 | 18.12 | 20.27 | 10.75 | 22.53 | 2.14 | 0.5 | 25 | 2.14
2018-09-05 | 13615.3542 | -0.048233 | 17.24 | 19.58 | 10.17 | 25.3 | 2.04 | 0.5 | 2.79 | 2.11
2018-09-05 01:00 | 15126.5391 | -0.048233 | 16.24 | 18.05 | 8.99 | 22.84 | 1.5 | 0.5 | 3.5 | 1
2018-09-05 02:00 | 15059.0191 | -0.048233 | 15.28 | 17.29 | 7.48 | 19.89 | 1.59 | 0.97 | 3.44 | 1
2018-09-05 03:00 | 13783.5042 | -0.048233 | 15.18 | 16.84 | 6.32 | 20.91 | 1.59 | 0.97 | 2.99 | 1
2018-09-05 04:00 | 15260.5241 | -0.048233 | 11.6 | 16.81 | 5.16 | 20.36 | 1.59 | 0.97 | 2.89 | 1
2018-09-05 05:00 | 15297.4491 | -0.048233 | 9.46 | 17.48 | 6.24 | 20.76 | 2 | 0.97 | 4.31 | 2
2018-09-05 06:00 | 13804.4042 | -0.048233 | 16.32 | 18.28 | 9.1 | 24.33 | 2 | 1 | 3.2 | 2.11
2018-09-05 07:00 | 15285.0426 | 237.192 | 15.73 | 19.65 | 11.92 | 26.74 | 2 | 1 | 2.61 | 1
2018-09-05 08:00 | 15613.5611 | 499.584 | 16.91 | 20.19 | 14.54 | 27.45 | 2 | 1 | 3.5 | 2
2018-09-05 09:00 | 16356.4995 | 768.791 | 17.46 | 20.5 | 15.87 | 28.72 | 2.61 | 0.99 | 26.2 | 2.11
2018-09-05 10:00 | 16786.3339 | 927.217 | 17.97 | 20.98 | 16.07 | 29.58 | 1.99 | 1.29 | 1 | 2.88
2018-09-05 11:00 | 15379.5025 | 1002.95 | 18.61 | 25.49 | 16.62 | 36.01 | 4.76 | 1.03 | 1 | 5.02
2018-09-05 12:00 | 15412.439 | 1080.62 | 37.45 | 37.45 | 16.56 | 38.62 | 7.04 | 8.86 | 0.89 | 5.27
2018-09-05 13:00 | 17074.5526 | 1008.41 | 38.84 | 38.84 | 18.47 | 50.6 | 15.77 | 14.89 | 1 | 14.27
2018-09-05 14:00 | 15257.9139 | 770.962 | 18.32 | 29.57 | 17.49 | 59.12 | 22.2 | 0.99 | 1 | 18.33
2018-09-05 15:00 | 15391.0773 | 756.134 | 18.16 | 27.97 | 16.99 | 72.55 | 36.73 | 15.31 | 1 | 25
2018-09-05 16:00 | 15019.0411 | 389.517 | 18.98 | 27.69 | 18.45 | 59.83 | 32.03 | 19.49 | 1 | 28.06
2018-09-05 17:00 | 14786.9219 | 193.181 | 19.98 | 23.84 | 20 | 42.52 | 20.1 | 10.15 | 2 | 14.95
2018-09-05 18:00 | 14664.5801 | 6.4001 | 21.36 | 29.26 | 20.67 | 36.89 | 16.6 | 8.41 | 3.11 | 4.14
2018-09-05 19:00 | 16346.1191 | -0.048233 | 20.59 | 22.3 | 21.35 | 34.5 | 5.2 | 1.2 | 2 | 3.2
2018-09-05 20:00 | 14767.7042 | -0.048233 | 22.88 | 25.44 | 20.44 | 32.93 | 5.91 | 1.11 | 1 | 2.92
2018-09-05 21:00 | 14681.2542 | -0.048233 | 20.55 | 24.7 | 18.57 | 29.9 | 2.17 | 1 | 25 | 1.5
2018-09-05 22:00 | 14460.8542 | -0.048233 | 47.87 | 47.87 | 15.93 | 27.77 | 2.11 | 0.5 | 25 | 3
2018-09-05 23:00 | 14234.7542 | -0.048233 | 18.69 | 20.97 | 15.09 | 25.53 | 2.1 | 0.5 | 14.19 | 2.61
2018-09-06 | 15808.0691 | -0.048233 | 17.38 | 20.67 | 15.58 | 23.61 | 1.85 | 0.45 | 2.26 | 2.01
2018-09-06 01:00 | 15636.1041 | -0.048233 | 16.37 | 18.19 | 15.12 | 20.96 | 1.27 | 0.45 | 3.65 | 1
2018-09-06 02:00 | 15694.1291 | -0.048233 | 15.92 | 17.68 | 14.11 | 19.42 | 1.27 | 0.97 | 3.5 | 1
2018-09-06 03:00 | 15495.7891 | -0.048233 | 15.73 | 17.56 | 11.08 | 19.16 | 1.27 | 0.97 | 2.99 | 1
2018-09-06 04:00 | 14185.3542 | -0.048233 | 15.89 | 17.55 | 13.15 | 19.5 | 1.31 | 0.97 | 2.94 | 1
2018-09-06 05:00 | 15367.1542 | -0.048233 | 15.8 | 18.1 | 12.75 | 20.73 | 1.5 | 0.97 | 4.14 | 1.5
2018-09-06 06:00 | 19417.2241 | -0.048233 | 15.09 | 18.68 | 13.19 | 25.8 | 1.86 | 0.99 | 3.5 | 2
2018-09-06 07:00 | 21222.5836 | 202.193 | 15.93 | 19.68 | 13.29 | 26.79 | 1.99 | 0.99 | 2.81 | 1
2018-09-06 08:00 | 21128.2181 | 139.747 | 17.3 | 19.35 | 15.7 | 27.89 | 2 | 0.99 | 3.42 | 2
2018-09-06 09:00 | 21270.9266 | 523.449 | 19.11 | 19.16 | 17.72 | 26.07 | 2.21 | 0.99 | 3.01 | 1.01
2018-09-06 10:00 | 20721.9947 | 910.626 | 19.2 | 19.2 | 18.56 | 26.95 | 2.5 | 1 | 1 | 2.11
2018-09-06 11:00 | 20057.712 | 543.381 | 19.93 | 19.93 | 20.11 | 29.52 | 2.5 | 1.1 | 0.59 | 2.21
2018-09-06 12:00 | 21234.9795 | 1122.61 | 20.46 | 20.46 | 20.44 | 33.42 | 3.54 | 1.18 | 0.89 | 2.5
2018-09-06 13:00 | 22868.103 | 709.927 | 31.7 | 20.87 | 21.47 | 38.87 | 15.49 | 7.75 | 0.78 | 12.32
2018-09-06 14:00 | 19252.756 | 426.059 | 75.69 | 21.06 | 21.47 | 43.33 | 19.75 | 0.99 | 1 | 16.95
2018-09-06 15:00 | 20322.0166 | 403.575 | 35.71 | 21.98 | 21.81 | 51.69 | 29.55 | 13.12 | 1 | 24.49
2018-09-06 16:00 | 17652.9475 | 238.05 | 73.56 | 23.48 | 22.08 | 50.48 | 35.47 | 17.5 | 1 | 31.31
2018-09-06 17:00 | 19231.249 | 162.672 | 40.77 | 25.98 | 21.85 | 34.7 | 21.4 | 9.13 | 1.35 | 15.04
2018-09-06 18:00 | 16760.0776 | 6.1869 | 33.66 | 22.88 | 20.88 | 27.86 | 4.3 | 1.25 | 2.21 | 2.99
2018-09-06 19:00 | 18533.1341 | -0.048233 | 30.34 | 21.16 | 21.3 | 28.6 | 4.6 | 0.97 | 2 | 2.99
2018-09-06 20:00 | 18623.8641 | -0.048233 | 43.55 | 20.93 | 20.74 | 27.29 | 4.49 | 0.97 | 1.22 | 2.47
2018-09-06 21:00 | 18299.9791 | -0.048233 | 20.3 | 20.3 | 17.25 | 27.48 | 2.03 | 0.97 | 25 | 2.61
2018-09-06 22:00 | 15933.3542 | -0.048233 | 77.31 | 18.83 | 15.81 | 22.16 | 2.65 | 0.5 | 28.82 | 2.8
2018-09-06 23:00 | 17064.5741 | -0.048233 | 17.76 | 17.76 | 15.24 | 20.21 | 2.61 | 0.5 | 20 | 2.7
2018-09-07 | 15224.6542 | -0.048233 | 17.28 | 17.28 | 15.44 | 21.69 | 2.11 | 0.45 | 11.1 | 2.11
2018-09-07 01:00 | 15180.0042 | -0.048233 | 16.55 | 16.55 | 14.74 | 18.42 | 1.5 | 0.45 | 3.46 | 1.01
2018-09-07 02:00 | 15054.6042 | -0.048233 | 15.42 | 15.42 | 12.65 | 16.66 | 1.47 | 0.97 | 3.46 | 1.01
2018-09-07 03:00 | 14908.3042 | -0.048233 | 0 | 0 | 12.46 | 15.54 | 1.47 | 0.97 | 2.61 | 1
2018-09-07 04:00 | 15070.7542 | -0.048233 | 9.92 | 9.92 | 12.46 | 15.79 | 1.47 | 0.97 | 3.07 | 1.01
2018-09-07 05:00 | 16215.5042 | -0.048233 | 13.17 | 13.17 | 14.96 | 18.61 | 1.59 | 0.97 | 9.11 | 1.83
2018-09-07 06:00 | 19907.7991 | -0.048233 | 16.28 | 16.28 | 15.72 | 23.5 | 1.99 | 1 | 3.38 | 87.1162
2018-09-07 07:00 | 19354.4583 | 191.114 | 16.74 | 16.74 | 16.39 | 23.6 | 2 | 0.99 | 3.5 | 2
2018-09-07 08:00 | 19746.8995 | 358.21 | 16.6 | 16.6 | 16.52 | 26.92 | 2 | 0.99 | 15.6 | 2.06
2018-09-07 09:00 | 20442.8239 | 772.762 | 17.94 | 17.94 | 17.34 | 26.93 | 3 | 1 | 10.82 | 3
2018-09-07 10:00 | 20685.3532 | 850.056 | 17.94 | 17.94 | 18.1 | 25.2 | 3.75 | 0.99 | 1 | 3.75
2018-09-07 11:00 | 20770.667 | 956.86 | 18.53 | 18.53 | 19.12 | 26.14 | 5.57 | 1.35 | 2.11 | 5.57
2018-09-07 12:00 | 21248.0895 | 1048.41 | 20.17 | 20.17 | 22.64 | 28.19 | 6.65 | 1.33 | 1 | 6.26
2018-09-07 13:00 | 20680.6858 | 524.143 | 31.4 | 20.66 | 28.36 | 28.46 | 5 | 1.38 | 0.66 | 12.5
2018-09-07 14:00 | 19634.8926 | 957.308 | 37.37 | 21.03 | 28.64 | 31.28 | 20.22 | 1 | 0.85 | 18
2018-09-07 15:00 | 20576.2326 | 766.538 | 37.32 | 21.6 | 30.95 | 38.55 | 31.4 | 13.01 | 1 | 28.58
2018-09-07 16:00 | 19539.6508 | 449.996 | 40.66 | 23.3 | 31.01 | 42.05 | 34.54 | 15.32 | 1 | 30.34
2018-09-07 17:00 | 17022.3992 | 127.315 | 34.35 | 24.65 | 31.04 | 29.16 | 20.09 | 1 | 1.94 | 13.94
2018-09-07 18:00 | 16491.2683 | 7.2298 | 37.04 | 21.73 | 28.33 | 25.41 | 6.11 | 9.06 | 8.11 | 2.99
2018-09-07 19:00 | 18317.9141 | -0.048233 | 20.75 | 20.75 | 28.4 | 25.66 | 6.76 | 1.18 | 2.27 | 3.78
2018-09-07 20:00 | 16554.6542 | -0.048233 | 46.28 | 20.73 | 23.78 | 25.68 | 7.18 | 1.15 | 8.61 | 3
2018-09-07 21:00 | 18280.9891 | -0.048233 | 19.11 | 19.11 | 15.71 | 25.37 | 3.73 | 1 | 16.47 | 3
2018-09-07 22:00 | 15885.8542 | -0.048233 | 20.69 | 21 | 15.02 | 22.01 | 3 | 0.5 | 57.6962 | 3
2018-09-07 23:00 | 15219.9042 | -0.048233 | 19.97 | 20.09 | 14.84 | 22.14 | 2.24 | 0.5 | 20 | 2.24
2018-09-08 | 16525.4691 | -0.048233 | 18.42 | 18.42 | 12.98 | 16.77 | 1.87 | 0.5 | 24.37 | 2.11
2018-09-08 01:00 | 16567.6691 | -0.048233 | 17.96 | 18.21 | 8.41 | 13.24 | 1.47 | 0.5 | 15 | 1.27
2018-09-08 02:00 | 14633.7542 | -0.048233 | 15.52 | 15.52 | 7.46 | 8.88 | 1.5 | 0.62 | 15.02 | 1.25
2018-09-08 03:00 | 16114.0191 | -0.048233 | 4.93 | 4.93 | 6.87 | 8.84 | 1.5 | 0.62 | 2.26 | 1.01
2018-09-08 04:00 | 16392.5391 | -0.048233 | 7.21 | 7.21 | 7.69 | 11.98 | 1.5 | 0.62 | 2.11 | 1.3
2018-09-08 05:00 | 17535.1041 | -0.048233 | 16.22 | 16.22 | 8.58 | 17.19 | 2 | 0.62 | 20 | 26
2018-09-08 06:00 | 19802.2991 | -0.048233 | 16.8 | 16.8 | 13.58 | 24.4 | 2 | 0.99 | 1 | 46
2018-09-08 07:00 | 19181.3047 | 35.8471 | 17.52 | 17.52 | 15.39 | 25.61 | 2 | 1 | 1 | 2
2018-09-08 08:00 | 21270.0732 | 77.2068 | 17.42 | 17.42 | 15.35 | 22.14 | 2 | 0.99 | 2.55 | 2.1
2018-09-08 09:00 | 23064.5144 | 117.099 | 19.17 | 19.17 | 15.64 | 25.15 | 4 | 0.99 | 2.11 | 3
2018-09-08 10:00 | 19433.1981 | 141.998 | 18.97 | 18.97 | 28.45 | 23.59 | 5.77 | 1.16 | 1 | 6.19
2018-09-08 11:00 | 19239.0561 | 180.638 | 18.89 | 18.89 | 31.47 | 24.42 | 5.37 | 1.13 | 2 | 4.79
2018-09-08 12:00 | 21961.7947 | 190.867 | 20.1 | 20.1 | 34.88 | 26.02 | 5 | 1.27 | 1 | 3.86
2018-09-08 13:00 | 19666.0174 | 346.071 | 33.87 | 21.01 | 38.37 | 26.69 | 21.88 | 12 | 1.29 | 18.93
2018-09-08 14:00 | 18451.1375 | 155.25 | 54.4 | 21.23 | 39.98 | 29.39 | 28.63 | 15 | 2 | 25
2018-09-08 15:00 | 17454.2892 | 125.936 | 38.19 | 23.05 | 42 | 35.59 | 47.84 | 24 | 1.42 | 41.59
2018-09-08 16:00 | 18893.4211 | 132.456 | 47.11 | 27.71 | 42.63 | 39.2 | 87.9841 | 61.4973 | 1 | 82.2062
2018-09-08 17:00 | 18515.0883 | 60.8467 | 34.79 | 27.87 | 40.29 | 30.13 | 25.07 | 10.69 | 1.86 | 18.58
2018-09-08 18:00 | 18141.29 | 3.5356 | 36.38 | 22.22 | 38.45 | 25.09 | 16.91 | 9.3 | 20.07 | 2.95
2018-09-08 19:00 | 18104.8041 | -0.048233 | 21.19 | 21.19 | 36.41 | 25.76 | 7.41 | 1.49 | 2.11 | 2.67
2018-09-08 20:00 | 18000.3591 | -0.048233 | 21.13 | 21.13 | 36.67 | 26.49 | 6.3 | 1.25 | 28 | 2.5
2018-09-08 21:00 | 15722.4542 | -0.048233 | 20.08 | 20.08 | 23.36 | 24.53 | 5.12 | 1.14 | 20 | 3.11
2018-09-08 22:00 | 16924.2591 | -0.048233 | 19.79 | 19.79 | 13.73 | 20.96 | 3.35 | 0.5 | 28.56 | 3.35
2018-09-08 23:00 | 16501.2041 | -0.048233 | 18.9 | 18.97 | 12.18 | 20.08 | 2.11 | 0.5 | 22 | 2.11
2018-09-09 | 16460.0591 | -0.048233 | 17.49 | 17.49 | 12.78 | 19.09 | 1.69 | 0.5 | 11.15 | 2.1
2018-09-09 01:00 | 14758.2042 | -0.048233 | 16.65 | 16.65 | 12.39 | 16.89 | 1.5 | 0.5 | 3.15 | 1.3
2018-09-09 02:00 | 14566.3042 | -0.048233 | 16.56 | 16.82 | 10.59 | 16.17 | 1.5 | 0.97 | 2.61 | 1
2018-09-09 03:00 | 16010.6291 | -0.048233 | 15.75 | 17.18 | 10.07 | 16.34 | 1.5 | 0.97 | 1.95 | 1.13
2018-09-09 04:00 | 15928.3391 | -0.048233 | 15.94 | 15.94 | 8.15 | 16.71 | 1.52 | 0.62 | 2.05 | 1.32
2018-09-09 05:00 | 15476.4042 | -0.048233 | 16.06 | 16.06 | 8.15 | 17.06 | 1.92 | 0.62 | 3 | 2
2018-09-09 06:00 | 19360.2541 | -0.048233 | 17.1 | 17.1 | 9.99 | 18.6 | 2.1 | 0.99 | 2.63 | 25
2018-09-09 07:00 | 18139.0863 | 55.775 | 17.22 | 17.22 | 11.77 | 19.65 | 2.01 | 0.99 | 3.46 | 2.01
2018-09-09 08:00 | 18167.4796 | 77.6627 | 18.56 | 18.56 | 12.36 | 20.51 | 2.04 | 1 | 15.61 | 2.04
2018-09-09 09:00 | 19225.379 | 109.241 | 19.97 | 22.7 | 23.53 | 22.55 | 3.89 | 1 | 20 | 3
2018-09-09 10:00 | 19492.0962 | 148.996 | 19.84 | 19.84 | 23.6 | 24.13 | 5.8 | 0.97 | 2 | 4.86
2018-09-09 11:00 | 21832.6321 | 999.438 | 21.21 | 21.4 | 36.69 | 24.71 | 5.76 | 0.97 | 13.5 | 4.76
2018-09-09 12:00 | 19843.4679 | 161.861 | 22.59 | 22.59 | 37.7 | 24.68 | 7.11 | 1.69 | 2 | 5.43
2018-09-09 13:00 | 21905.9377 | 151.922 | 26.94 | 24.34 | 38.64 | 26.02 | 20.89 | 12 | 1 | 18.43
2018-09-09 14:00 | 19019.1824 | 320.192 | 28.27 | 25.62 | 43.69 | 31.52 | 20.15 | 0.97 | 1.17 | 18.39
2018-09-09 15:00 | 19129.7938 | 280.506 | 29.99 | 29.99 | 44.1 | 36.78 | 31.81 | 0.97 | 2 | 24.46
2018-09-09 16:00 | 16551.2299 | 69.3473 | 39.22 | 39.22 | 46.57 | 38.6 | 28.77 | 12.05 | 2 | 25.65
2018-09-09 17:00 | 17998.7679 | 66.4435 | 251.7757 | 207.45 | 43.46 | 32.18 | 15.69 | 0.97 | 2 | 5
2018-09-09 18:00 | 15820.9788 | 2.6619 | 26.12 | 26.12 | 37.7 | 28.26 | 9.3 | 1.31 | 13.03 | 4.02
2018-09-09 19:00 | 15748.1042 | -0.048233 | 21.5 | 21.5 | 37.5 | 24.38 | 7.11 | 0.97 | 2.23 | 3.11
2018-09-09 20:00 | 17376.8541 | -0.048233 | 20.66 | 20.66 | 36.02 | 25.19 | 6.4 | 0.97 | 16.71 | 2.89
2018-09-09 21:00 | 15469.7542 | -0.048233 | 20.03 | 20.03 | 11.3 | 21.96 | 3.28 | 0.97 | 16.25 | 3
2018-09-09 22:00 | 15046.0542 | -0.048233 | 19.45 | 19.45 | 9.73 | 20.33 | 3 | 0.5 | 20 | 3
2018-09-09 23:00 | 16175.2091 | -0.048233 | 17.95 | 17.95 | 5.82 | 19.49 | 2.39 | 0.5 | 20 | 2.39
2018-09-10 | 14168.2542 | -0.048233 | 17.52 | 17.52 | 9.57 | 19.11 | 2.1 | 0.5 | 2.62 | 2.61
2018-09-10 01:00 | 15794.3541 | -0.048233 | 16.8 | 16.8 | 7.12 | 18.73 | 1.61 | 0.5 | 3.11 | 1.01
2018-09-10 02:00 | 15667.7541 | -0.048233 | 16.04 | 16.04 | 6.62 | 17.92 | 1.92 | 0.89 | 2.61 | 1.01
2018-09-10 03:00 | 15553.8141 | -0.048233 | 16.02 | 16.02 | 6.55 | 17.59 | 1.61 | 0.89 | 2.28 | 1
2018-09-10 04:00 | 15240.4791 | -0.048233 | 15.95 | 15.95 | 6.51 | 17.53 | 2 | 0.89 | 2.11 | 1.01
2018-09-10 05:00 | 13999.1542 | -0.048233 | 16.02 | 16.02 | 6.57 | 17.83 | 2.01 | 0.89 | 10.24 | 2.42
2018-09-10 06:00 | 14479.8542 | -0.048233 | 16.57 | 16.57 | 6.49 | 17.65 | 2.04 | 0.99 | 1 | 2.5
2018-09-10 07:00 | 16118.3746 | 56.0802 | 16.84 | 16.84 | 6.87 | 19.18 | 2 | 0.99 | 1.2 | 2
2018-09-10 08:00 | 16510.9076 | 78.1494 | 17.34 | 17.34 | 6.6 | 20.64 | 2.31 | 0.99 | 11.49 | 2.31
2018-09-10 09:00 | 15263.5151 | 109.858 | 18.7 | 18.7 | 9.69 | 22.43 | 4.66 | 0.99 | 10.89 | 3
2018-09-10 10:00 | 15334.3917 | 172.465 | 18.88 | 19.44 | 34.2 | 23.61 | 4.58 | 0.99 | 1.41 | 3.6
2018-09-10 11:00 | 17315.6401 | 225.929 | 19.93 | 19.93 | 34.4 | 24.21 | 5.5 | 0.99 | 12.79 | 4.5
2018-09-10 12:00 | 15746.9834 | 163.772 | 137.88 | 20.41 | 34.5 | 24.01 | 6.12 | 1.39 | 0.9 | 5.18
2018-09-10 13:00 | 16015.7869 | 232.723 | 52.4 | 25.14 | 33.91 | 25.3 | 16.22 | 10 | 2 | 14.58
2018-09-10 14:00 | 17074.9039 | 340.743 | 21.53 | 25.08 | 34.13 | 30.18 | 19.81 | 1.11 | 1.41 | 18
2018-09-10 15:00 | 15125.3594 | 140.431 | 36.86 | 31.29 | 35.8 | 34.2 | 29.6 | 1.25 | 1.28 | 22.92
2018-09-10 16:00 | 15450.4101 | 95.5896 | 46.7 | 46.7 | 34.33 | 37.63 | 29.38 | 10.58 | 1 | 26.23
2018-09-10 17:00 | 15109.8604 | 88.1162 | 39.9 | 39.9 | 33.1 | 35.07 | 15.89 | 1.26 | 2.11 | 11.58
2018-09-10 18:00 | 14770.4921 | 1.8864 | 28.59 | 28.59 | 23.05 | 30.53 | 7.4 | 1.2 | 13 | 4
2018-09-10 19:00 | 14600.5042 | -0.048233 | 22.59 | 27.22 | 29.62 | 25.25 | 7.76 | 0.71 | 2.61 | 3.57
2018-09-10 20:00 | 14625.2042 | -0.048233 | 23.54 | 23.54 | 17.37 | 24.66 | 6.32 | 0.71 | 1 | 3
2018-09-10 21:00 | 15956.8241 | -0.048233 | 22.23 | 22.23 | 11.87 | 23.69 | 3.93 | 0.71 | 16.22 | 3.7
2018-09-10 22:00 | 14244.2542 | -0.048233 | 19.88 | 20 | 9.68 | 21 | 3.3 | 0.5 | 15.76 | 3
2018-09-10 23:00 | 15507.3941 | -0.048233 | 18.56 | 18.56 | 6.64 | 19.73 | 2.72 | 0.5 | 15.39 | 2.72
2018-09-11 | 15351.2541 | -0.048233 | 17.74 | 17.74 | 10.03 | 18.81 | 1.61 | 0.5 | 2.97 | 2.61
2018-09-11 01:00 | 15235.2041 | -0.048233 | 16.94 | 16.94 | 9.66 | 17.89 | 1.61 | 0.5 | 2.49 | 1.18
2018-09-11 02:00 | 13425.3542 | -0.048233 | 16.53 | 16.53 | 8.79 | 17.54 | 1.61 | 0.89 | 2.12 | 1
2018-09-11 03:00 | 13059.6042 | -0.048233 | 16.43 | 16.43 | 6.56 | 17.08 | 1.61 | 0.89 | 1.85 | 1
2018-09-11 04:00 | 13955.4891 | -0.048233 | 16.48 | 16.48 | 8.55 | 17.43 | 1.61 | 0.89 | 1.93 | 1.01
2018-09-11 05:00 | 13713.8941 | -0.048233 | 17.04 | 17.04 | 9.86 | 18.19 | 2.01 | 0.89 | 3.5 | 2.11
2018-09-11 06:00 | 12661.5542 | -0.048233 | 17.28 | 19.05 | 11.93 | 20.95 | 2.57 | 0.99 | 1 | 2.61
2018-09-11 07:00 | 12710.3689 | 56.3357 | 17.57 | 20.05 | 11.76 | 22.73 | 2 | 0.99 | 1 | 2
2018-09-11 08:00 | 14266.2755 | 111.536 | 18.02 | 20.02 | 12.95 | 23.91 | 2.11 | 0.99 | 2.61 | 2.11
2018-09-11 09:00 | 13055.6743 | 172.815 | 18.57 | 20.11 | 13.03 | 24.17 | 3.7 | 0.99 | 3.11 | 3
2018-09-11 10:00 | 13300.5263 | 195.554 | 18.77 | 20.2 | 12.97 | 26.67 | 4.03 | 0.99 | 2 | 3.6
2018-09-11 11:00 | 14830.8176 | 256.647 | 20 | 20.15 | 13.71 | 25.2 | 6.34 | 0.99 | 1 | 5.33
2018-09-11 12:00 | 13737.4664 | 361.491 | 20.5 | 20.5 | 14.92 | 27.98 | 7.09 | 1.18 | 1 | 5.59
2018-09-11 13:00 | 15292.2777 | 265.05 | 20.85 | 20.85 | 15.24 | 31.8 | 25 | 8.65 | 0.88 | 24.69
2018-09-11 14:00 | 15571.6871 | 217.893 | 64.19 | 31.58 | 15.89 | 33.02 | 29.57 | 0.97 | 1 | 16.66
2018-09-11 15:00 | 15860.7445 | 220.881 | 143.03 | 140.71 | 17.23 | 39.09 | 36.95 | 0.97 | 1 | 21.56
2018-09-11 16:00 | 14377.0093 | 152.694 | 147.31 | 142.96 | 18.23 | 46.42 | 36.7 | 0.97 | 1 | 20.77
2018-09-11 17:00 | 15801.3617 | 39.594 | 139.98 | 139.98 | 18.5 | 40.09 | 18.41 | 0.97 | 2 | 14.21
2018-09-11 18:00 | 14121.7042 | -0.048233 | 23.37 | 24.66 | 17.6 | 30.01 | 7.22 | 1.26 | 2 | 4
2018-09-11 19:00 | 14150.2042 | -0.048233 | 21.91 | 21.91 | 17.42 | 29.51 | 5 | 0.97 | 1.05 | 3
2018-09-11 20:00 | 15682.5241 | -0.048233 | 22.16 | 22.62 | 15.53 | 25.88 | 3.91 | 0.97 | 3.46 | 3
2018-09-11 21:00 | 15393.4541 | -0.048233 | 21.13 | 21.13 | 12.95 | 23.66 | 3.31 | 0.97 | 3.46 | 3
2018-09-11 22:00 | 15125.4841 | -0.048233 | 20.05 | 20.15 | 10.63 | 22.37 | 3 | 0.5 | 20 | 3
2018-09-11 23:00 | 15007.3241 | -0.048233 | 19.18 | 19.21 | 10.2 | 20.7 | 3 | 0.5 | 13 | 3
2018-09-12 | 14802.6541 | -0.048233 | 17.97 | 18.46 | 12.29 | 19.67 | 2.1 | 0.45 | 4.93 | 2.11
2018-09-12 01:00 | 14692.9341 | -0.048233 | 11.74 | 18.5 | 9.85 | 18.67 | 2.01 | 0.45 | 3.11 | 1
2018-09-12 02:00 | 12999.7542 | -0.048233 | 10.83 | 18.45 | 5.77 | 17.85 | 2 | 0.97 | 3.11 | 0.88
2018-09-12 03:00 | 12876.2542 | -0.048233 | 10.88 | 17.96 | 4.93 | 17.43 | 2 | 0.97 | 2.11 | 1
2018-09-12 04:00 | 14683.4391 | -0.048233 | 14.38 | 18.15 | 5.35 | 17.74 | 2.01 | 0.97 | 1.92 | 1.01
2018-09-12 05:00 | 14428.5542 | -0.048233 | 16.51 | 18.76 | 10.81 | 18.87 | 2.1 | 0.97 | 8.61 | 2.61
2018-09-12 06:00 | 16257.3042 | -0.048233 | 18.32 | 19.72 | 13.15 | 22.62 | 2.11 | 1 | 0.79 | 3.75
2018-09-12 07:00 | 17589.4533 | 207.214 | 18.31 | 20.09 | 15.1 | 24.6 | 2.1 | 1 | 1 | 2.1
2018-09-12 08:00 | 17688.0737 | 229.025 | 18.35 | 19.22 | 14.83 | 22.93 | 2.29 | 0.99 | 2.61 | 3
2018-09-12 09:00 | 18575.4203 | 329.074 | 19.18 | 19.52 | 15.99 | 25.36 | 3.95 | 0.99 | 3.5 | 3
2018-09-12 10:00 | 21220.9515 | 608.646 | 19.1 | 19.1 | 17.9 | 24.5 | 3.75 | 1.02 | 1 | 3.87
2018-09-12 11:00 | 18920.4584 | 661.272 | 109.69 | 19.84 | 18.49 | 26.67 | 4 | 1.01 | 1 | 4
2018-09-12 12:00 | 19554.5492 | 691.736 | 20.2 | 20.2 | 19.72 | 27.82 | 4.68 | 1.22 | 1 | 4.75
2018-09-12 13:00 | 19097.6239 | 425.762 | 21.21 | 21.21 | 19.68 | 31.73 | 4.84 | 1.22 | 0.95 | 3.34
2018-09-12 14:00 | 17996.3877 | 322.566 | 44.92 | 21.72 | 20.7 | 36.6 | 22.74 | 1.24 | 1 | 18.86
2018-09-12 15:00 | 17045.7056 | 209.848 | 31.31 | 24.47 | 21.49 | 44.05 | 32.86 | 1.11 | 1 | 27.81
2018-09-12 16:00 | 18222.6468 | 168.651 | 74 | 26.89 | 21.68 | 49.64 | 30.99 | 1.14 | 1 | 25.99
2018-09-12 17:00 | 16342.0891 | 140.199 | 38.94 | 26.56 | 21.68 | 39 | 15.9 | 0.99 | 1.98 | 12.13
2018-09-12 18:00 | 15781.3542 | -0.048233 | 32.14 | 24.91 | 21.36 | 30.74 | 6.97 | 1.25 | 2.61 | 3.95
2018-09-12 19:00 | 17444.3741 | -0.048233 | 33.88 | 33.88 | 21.45 | 30 | 4.84 | 0.97 | 1.5 | 3
2018-09-12 20:00 | 17617.3941 | -0.048233 | 20.82 | 21.04 | 20.5 | 27.41 | 3.75 | 0.97 | 3.46 | 3
2018-09-12 21:00 | 15547.6542 | -0.048233 | 19.5 | 20.75 | 18.28 | 26.55 | 3 | 0.97 | 3.64 | 3
2018-09-12 22:00 | 16595.0991 | -0.048233 | 19.38 | 19.83 | 15.61 | 24.08 | 3 | 0.5 | 14.61 | 3
2018-09-12 23:00 | 14580.5542 | -0.048233 | 18 | 18.38 | 14.53 | 21.3 | 2.5 | 0.5 | 20 | 2.9
2018-09-13 | 16026.4541 | -0.048233 | 17.4 | 18.51 | 15.31 | 20.02 | 2 | 0.45 | 4.24 | 2.01
2018-09-13 01:00 | 14325.0042 | -0.048233 | 8.26 | 17.64 | 13.52 | 18.35 | 1.51 | 0.45 | 2.54 | 1
2018-09-13 02:00 | 15764.8141 | -0.048233 | -0.37 | 17.14 | 10.69 | 17.81 | 1.68 | 0.89 | 2.61 | 0.67
2018-09-13 03:00 | 14086.5542 | -0.048233 | -0.74 | 16.81 | 9.44 | 17.11 | 1.51 | 0.89 | 2.11 | 0.72
2018-09-13 04:00 | 14226.2042 | -0.048233 | -3.19 | 16.73 | 9.95 | 17.72 | 2 | 0.89 | 2 | 1
2018-09-13 05:00 | 16771.2841 | -0.048233 | -1.05 | 17.01 | 14.02 | 18.78 | 2 | 0.89 | 12.94 | 2.32
2018-09-13 06:00 | 19184.0691 | -0.048233 | -0.26 | 18.39 | 15.24 | 20.92 | 2 | 0.99 | 2 | 3.91
2018-09-13 07:00 | 20404.1336 | 201.411 | 0 | 18.88 | 13.88 | 21.66 | 2 | 0.99 | 2 | 1.44
2018-09-13 08:00 | 19349.6371 | 527.039 | -0.53 | 18.11 | 15.5 | 22.58 | 2.11 | 0.99 | 3.11 | 2.61
2018-09-13 09:00 | 20047.6714 | 768.812 | 16.42 | 19.68 | 17.43 | 24.02 | 3 | 0.99 | 2.61 | 3.11
2018-09-13 10:00 | 20077.1889 | 977.883 | 16.99 | 19.61 | 17.68 | 26.91 | 3 | 1 | 1.21 | 3
2018-09-13 11:00 | 20146.1845 | 1108.51 | 17.08 | 19.78 | 18.56 | 27.4 | 3.74 | 0.99 | 0.44 | 3.88
2018-09-13 12:00 | 22740.7993 | 1146.26 | 18.63 | 20.02 | 17.6 | 35.55 | 2.82 | 1.15 | 0.86 | 2.58
2018-09-13 13:00 | 21883.865 | 1001 | 19.04 | 21.04 | 18.32 | 47.42 | 26.22 | 19.26 | 1.01 | 25.37
2018-09-13 14:00 | 18820.7331 | 965.298 | 33.29 | 33.29 | 18.31 | 47.97 | 24.23 | 1.24 | 1.43 | 21.66
2018-09-13 15:00 | 18064.2623 | 744.013 | 31.73 | 29.4 | 18.65 | 60.63 | 28.36 | 1.32 | 2 | 23.75
2018-09-13 16:00 | 19261.7796 | 462.611 | 31.64 | 31.6 | 21.05 | 56.52 | 25.83 | 1.35 | 2 | 20.56
2018-09-13 17:00 | 16298.8707 | 109.706 | 30.88 | 30.19 | 21.07 | 41.87 | 12.78 | 1 | 2 | 10.47
2018-09-13 18:00 | 17312.7239 | 1.1648 | 30.18 | 27.14 | 21.07 | 31.77 | 5.94 | 1.27 | 3.5 | 3.01
2018-09-13 19:00 | 17215.4391 | -0.048233 | 19.3 | 21.41 | 21.04 | 29.06 | 4 | 0.97 | 1.5 | 3
2018-09-13 20:00 | 15631.2542 | -0.048233 | 19.36 | 20.81 | 19.54 | 26.46 | 4 | 0.97 | 3.46 | 2.68
2018-09-13 21:00 | 16952.7441 | -0.048233 | 19.34 | 22.15 | 17.54 | 25.87 | 2.58 | 0.97 | 3.75 | 2.61
2018-09-13 22:00 | 16485.3791 | -0.048233 | 19.21 | 19.21 | 15.88 | 22.74 | 2.81 | 0.5 | 30 | 3
2018-09-13 23:00 | 14096.0542 | -0.048233 | 17.87 | 19.8 | 15.59 | 20.71 | 2.11 | 0.5 | 22 | 2.61
2018-09-14 | 15648.7641 | -0.048233 | 10.9 | 17.98 | 14.61 | 17.87 | 1.7 | 0.5 | 20 | 2.55
2018-09-14 01:00 | 15626.6091 | -0.048233 | 0.41 | 17.42 | 13.14 | 16.32 | 1.61 | 0.5 | 8.84 | 1.61
2018-09-14 02:00 | 15320.6591 | -0.048233 | -0.67 | 17.05 | 9.37 | 13.43 | 1.7 | 0.89 | 9.8 | 1.01
2018-09-14 03:00 | 13683.7542 | -0.048233 | -0.93 | 16.62 | 8.99 | 11.28 | 1.7 | 0.89 | 2 | 1
2018-09-14 04:00 | 13640.0542 | -0.048233 | -0.74 | 16.86 | 10.47 | 15.77 | 1.7 | 0.89 | 1.85 | 1.01
2018-09-14 05:00 | 16632.0241 | -0.048233 | -0.03 | 17.41 | 13.54 | 18.19 | 1.7 | 0.89 | 13.34 | 2.55
2018-09-14 06:00 | 18792.2251 | 9.5357 | 15.7 | 19.1 | 16.71 | 22.95 | 2.11 | 0.99 | 3.01 | 50
2018-09-14 07:00 | 20757.4014 | 244.262 | 15.96 | 19.98 | 16.26 | 23.2 | 2 | 0.99 | 3.32 | 2.1
2018-09-14 08:00 | 21381.2197 | 536.559 | 15.26 | 18.33 | 17.5 | 24.88 | 2.12 | 0.99 | 10.26 | 2.72
2018-09-14 09:00 | 20672.0446 | 795.047 | 17.8 | 19.24 | 19.13 | 23.25 | 3.75 | 0.99 | 10.88 | 3.55
2018-09-14 10:00 | 21115.5027 | 992.845 | 18.08 | 20.69 | 19.82 | 27.36 | 3.75 | 0.99 | 2 | 3.75
2018-09-14 11:00 | 21349.518 | 1106.51 | 18.75 | 20.7 | 20.95 | 26.73 | 3.55 | 0.99 | 2 | 4
2018-09-14 12:00 | 21584.5605 | 1133.59 | 32.42 | 26.47 | 21.02 | 38.62 | 3.92 | 10 | 1 | 3.39
2018-09-14 13:00 | 22005.7491 | 1085.53 | 45.16 | 45.16 | 28.2 | 39.17 | 23.19 | 12.78 | 1.92 | 21.19
2018-09-14 14:00 | 19096.3072 | 985.376 | 33.09 | 28.95 | 28.44 | 45.66 | 27.33 | 1.27 | 2 | 23.37
2018-09-14 15:00 | 20343.9912 | 773.404 | 38.16 | 28.46 | 31.9 | 51.21 | 24.26 | 1.22 | 2 | 18.18
2018-09-14 16:00 | 19313.598 | 482.728 | 34.05 | 33.05 | 32.15 | 49.38 | 23.14 | 1.24 | 1.89 | 18.97
2018-09-14 17:00 | 18990.7185 | 170.681 | 33.51 | 30.76 | 24.26 | 35.55 | 15.58 | 1 | 8.61 | 5
2018-09-14 18:00 | 16606.165 | 1.1737 | 29.84 | 28.97 | 21.94 | 29.55 | 6.79 | 1 | 10 | 3
2018-09-14 19:00 | 18431.8541 | -0.048233 | 95.82 | 95.82 | 22.14 | 27.57 | 4.55 | 0.97 | 2.51 | 2.93
2018-09-14 20:00 | 18460.3391 | -0.048233 | 31.49 | 30.37 | 21.04 | 27.91 | 3.66 | 0.97 | 16.47 | 2.61
2018-09-14 21:00 | 16207.9042 | -0.048233 | 252.3957 | 208.07 | 18.24 | 32.13 | 2.38 | 0.97 | 20 | 3
2018-09-14 22:00 | 17261.8591 | -0.048233 | 19.95 | 22.28 | 17 | 23.74 | 2.25 | 0.5 | 57.6962 | 2.61
2018-09-14 23:00 | 14955.8042 | -0.048233 | 37.92 | 20.79 | 15.98 | 23.23 | 2.25 | 0.5 | 57.6962 | 2.61
2018-09-15 | 16232.1791 | -0.048233 | 18.84 | 18.84 | 9.29 | 18.94 | 1.61 | 0.49 | 10.71 | 2.5
2018-09-15 01:00 | 14513.1042 | -0.048233 | 16.51 | 17.75 | 8.11 | 16.89 | 1.49 | 0.49 | 3.15 | 1.01
2018-09-15 02:00 | 14464.6542 | -0.048233 | 16.95 | 17.23 | 7.92 | 14.7 | 1.5 | 0.62 | 2.84 | 1
2018-09-15 03:00 | 15682.5241 | -0.048233 | 15.85 | 16.69 | 8.03 | 13.78 | 1.5 | 0.82 | 2.11 | 1
2018-09-15 04:00 | 16024.3441 | -0.048233 | 16.38 | 16.62 | 8.03 | 15.19 | 1.61 | 0.82 | 2 | 1
2018-09-15 05:00 | 17417.9991 | -0.048233 | 17.61 | 17.61 | 10.88 | 17.8 | 1.8 | 0.82 | 10.55 | 2.5
2018-09-15 06:00 | 19556.0448 | 9.5354 | 18.8 | 18.8 | 16.99 | 20.17 | 1.91 | 0.99 | 2.61 | 2.61
2018-09-15 07:00 | 20907.9436 | 240.956 | 19.13 | 19.6 | 17.33 | 20.7 | 1.8 | 0.99 | 3.08 | 2.01
2018-09-15 08:00 | 21249.0187 | 488.25 | 18.98 | 19.27 | 19.01 | 21.38 | 2.03 | 0.99 | 10.64 | 2.91
2018-09-15 09:00 | 22310.4859 | 788.38 | 19.52 | 20.23 | 19.35 | 23.73 | 3.38 | 0.99 | 15.8 | 3.38
2018-09-15 10:00 | 20463.7771 | 937.818 | 22.58 | 23.49 | 19.77 | 27.39 | 4 | 0.99 | 2.11 | 3.29
2018-09-15 11:00 | 20087.3035 | 1027.53 | 40.19 | 20.93 | 20.39 | 30 | 4.79 | 0.99 | 2.11 | 4.79
2018-09-15 12:00 | 23430.4423 | 1150.95 | 32.31 | 21.56 | 20.57 | 31.88 | 5.1 | 8.68 | 1 | 4.6
2018-09-15 13:00 | 22815.4405 | 1100.01 | 63.12 | 25.9 | 20.51 | 38.81 | 23.88 | 13.01 | 1.36 | 21.49
2018-09-15 14:00 | 19242.0495 | 973.789 | 34.92 | 29.19 | 19.79 | 39.66 | 28.15 | 0.99 | 1.62 | 21.89
2018-09-15 15:00 | 18091.9891 | 754.199 | 45.45 | 30.2 | 21.23 | 45.54 | 32.39 | 1.33 | 2.11 | 25.2
2018-09-15 16:00 | 19352.9569 | 472.035 | 69.38 | 40.5 | 21.6 | 46.72 | 29.8 | 1.29 | 1 | 29.5
2018-09-15 17:00 | 18835.9426 | 169.974 | 34.72 | 34.72 | 20.91 | 35.29 | 19.29 | 1 | 2.11 | 15.44
2018-09-15 18:00 | 17989.8091 | -0.048233 | 31.44 | 31.1 | 20.93 | 28.72 | 6.35 | 1 | 3.11 | 2.21
2018-09-15 19:00 | 17870.5941 | -0.048233 | 29.75 | 29.75 | 20.55 | 26.29 | 4.39 | 0.97 | 2 | 2.82
2018-09-15 20:00 | 16134.7542 | -0.048233 | 28.11 | 23.39 | 20.46 | 28.29 | 4.98 | 0.97 | 3.01 | 3
2018-09-15 21:00 | 15867.8042 | -0.048233 | 32.54 | 21.75 | 17.54 | 25.58 | 3 | 0.97 | 4 | 3
2018-09-15 22:00 | 17079.3441 | -0.048233 | 20.69 | 23.9 | 16.55 | 22.29 | 2.25 | 0.5 | 30 | 2.67
2018-09-15 23:00 | 16556.0641 | -0.048233 | 19.32 | 20.47 | 16.09 | 21.85 | 2.11 | 0.5 | 22 | 2.61
2018-09-16 | 14613.8042 | -0.048233 | 18.55 | 21.22 | 14.08 | 19.64 | 1.99 | 0.45 | 7.87 | 2.61
2018-09-16 01:00 | 15951.5491 | -0.048233 | 18.16 | 18.85 | 11.94 | 18.23 | 1.61 | 0.49 | 3.4 | 2.01
2018-09-16 02:00 | 15652.9841 | -0.048233 | 17.53 | 17.53 | 10.09 | 17.07 | 1.61 | 0.62 | 2.61 | 1.41
2018-09-16 03:00 | 15545.3741 | -0.048233 | 16.94 | 17.01 | 9.8 | 16.33 | 1.61 | 0.82 | 2.11 | 1.41
2018-09-16 04:00 | 15956.8241 | -0.048233 | 16.63 | 16.63 | 9.85 | 16.15 | 1.99 | 0.82 | 2.11 | 2.01
2018-09-16 05:00 | 17436.9891 | -0.048233 | 16.98 | 16.98 | 13.44 | 16.43 | 2.5 | 0.82 | 8.81 | 3.11
2018-09-16 06:00 | 19247.5753 | 3.1472 | 17.64 | 17.64 | 13.87 | 20.02 | 2.5 | 0.99 | 3.5 | 5.64
2018-09-16 07:00 | 20198.3036 | 66.3115 | 17.45 | 17.45 | 15.39 | 19.47 | 2.5 | 0.99 | 3.46 | 2.27
2018-09-16 08:00 | 21392.9978 | 190.723 | 17.96 | 18.71 | 14.44 | 21.36 | 2.5 | 0.99 | 8.11 | 5
2018-09-16 09:00 | 22363.0418 | 433.196 | 18.37 | 20.69 | 17.02 | 22.98 | 2.5 | 0.99 | 10.69 | 3
2018-09-16 10:00 | 19381.3423 | 168.413 | 19.66 | 21.76 | 16.52 | 25.79 | 3.35 | 0.99 | 2.11 | 3.11
2018-09-16 11:00 | 18788.1994 | 152.052 | 22.19 | 22.43 | 18.4 | 26.41 | 4.97 | 0.99 | 2.11 | 4.47
2018-09-16 12:00 | 21556.1936 | 155.411 | 29.88 | 29.88 | 18.73 | 29.22 | 5.51 | 7.93 | 0.77 | 5.13
2018-09-16 13:00 | 21711.2132 | 195.349 | 40.61 | 29.87 | 19.12 | 31.35 | 27.86 | 16.5 | 1.37 | 21.35
2018-09-16 14:00 | 19407.5774 | 169.808 | 96.5 | 35.89 | 18.91 | 37.03 | 36.97 | 0.99 | 1 | 28.23
2018-09-16 15:00 | 17100.1216 | 303.128 | 51.43 | 51.43 | 22.46 | 45.55 | 33.28 | 1.43 | 1 | 25.99
2018-09-16 16:00 | 18648.3657 | 132.176 | 985.6911 | 57.92 | 21.95 | 50.19 | 40.44 | 11.55 | 1 | 38.7
2018-09-16 17:00 | 18490.5875 | 83.6232 | 50.85 | 30.21 | 20.86 | 34.04 | 16.92 | 0.99 | 2.17 | 13.86
2018-09-16 18:00 | 17808.3491 | -0.048233 | 34.02 | 34.02 | 20.26 | 27.24 | 5.7 | 1.27 | 2.61 | 2.27
2018-09-16 19:00 | 17823.1191 | -0.048233 | 27.73 | 27.73 | 20.89 | 25.55 | 4.5 | 0.97 | 1 | 3
2018-09-16 20:00 | 15855.4542 | -0.048233 | 32.88 | 24.98 | 19.91 | 27.77 | 5.62 | 0.97 | 1 | 3
2018-09-16 21:00 | 17329.3791 | -0.048233 | 22.83 | 23.34 | 17.38 | 24.03 | 3.16 | 0.97 | 3.98 | 3
2018-09-16 22:00 | 15022.3042 | -0.048233 | 21.05 | 21.93 | 14.21 | 22.25 | 2.25 | 0.5 | 20 | 2.32
2018-09-16 23:00 | 15974.7591 | -0.048233 | 18.82 | 27.82 | 13.87 | 21.54 | 2.02 | 0.5 | 20 | 2.11
2018-09-17 | 14049.5042 | -0.048233 | 18 | 21.58 | 18.12 | 20.54 | 1.99 | 0.5 | 3 | 2.61
2018-09-17 01:00 | 14100.8042 | -0.048233 | 16.97 | 20.83 | 16.36 | 19.3 | 1.61 | 0.5 | 3 | 1.61
2018-09-17 02:00 | 14062.8042 | -0.048233 | 15.96 | 19.93 | 13.07 | 18.21 | 1.61 | 0.89 | 2.61 | 1.41
2018-09-17 03:00 | 15421.9391 | -0.048233 | 15.57 | 18.96 | 12.42 | 18.53 | 1.5 | 0.89 | 2 | 1.3
2018-09-17 04:00 | 13928.8542 | -0.048233 | 15.87 | 18.59 | 11.55 | 18.1 | 1.61 | 0.89 | 2 | 1.61
2018-09-17 05:00 | 15862.9291 | -0.048233 | 16.43 | 18.07 | 15.03 | 18.6 | 2.5 | 0.89 | 3 | 2.51
2018-09-17 06:00 | 16409.984 | 1.4872 | 16.87 | 17.66 | 14.16 | 20.01 | 2.25 | 0.99 | 3.46 | 3
2018-09-17 07:00 | 14936.0167 | 37.1228 | 17.56 | 17.56 | 14.53 | 20.09 | 2.1 | 0.99 | 3.5 | 2.1
2018-09-17 08:00 | 14865.4125 | 69.8026 | 17.52 | 17.52 | 12.9 | 24.07 | 2.44 | 0.99 | 3.5 | 3
2018-09-17 09:00 | 15377.3906 | 117.727 | 18.37 | 18.77 | 14.98 | 22.67 | 2.5 | 0.99 | 3.5 | 3.11
2018-09-17 10:00 | 17234.0485 | 149.591 | 19.93 | 19.93 | 16.14 | 23.63 | 3.13 | 1.15 | 1.71 | 3.08
2018-09-17 11:00 | 17156.9913 | 152.551 | 31.61 | 21.06 | 16.65 | 26.09 | 4.94 | 7.5 | 1.6 | 15.96
2018-09-17 12:00 | 17325.881 | 155.636 | 37.48 | 28.38 | 18.55 | 30.81 | 19.43 | 10 | 0.84 | 16.89
2018-09-17 13:00 | 17286.2288 | 152.051 | 67.58 | 29.09 | 19.28 | 36.97 | 28.77 | 17.7 | 1 | 22.1
2018-09-17 14:00 | 17103.4606 | 128.811 | 369.4757 | 29.96 | 19.32 | 46.17 | 38.53 | 1.61 | 1 | 28.52
2018-09-17 15:00 | 16881.4716 | 99.3949 | 47.14 | 30.45 | 30.01 | 58.17 | 39.54 | 17.88 | 1 | 29.71
2018-09-17 16:00 | 15325.4515 | 76.0542 | 110.84 | 32.09 | 30.69 | 58.18 | 37.73 | 14.99 | 1 | 35.19
2018-09-17 17:00 | 16947.5978 | 62.0737 | 62.57 | 28.76 | 28.36 | 36.94 | 20.08 | 1.61 | 2 | 13.59
2018-09-17 18:00 | 16718.5341 | -0.048233 | 32.69 | 32.5 | 20.91 | 29.86 | 13.42 | 1.48 | 2.61 | 3.53
2018-09-17 19:00 | 16500.1491 | -0.048233 | 31.79 | 23.44 | 23.13 | 27.83 | 5.4 | 1 | 1 | 2.44
2018-09-17 20:00 | 16506.4791 | -0.048233 | 30.48 | 25.66 | 19.62 | 25.02 | 4.01 | 1 | 1.93 | 2.51
2018-09-17 21:00 | 14751.5542 | -0.048233 | 21.43 | 21.43 | 17.86 | 24.98 | 4.04 | 1.22 | 8.11 | 3
2018-09-17 22:00 | 16046.4991 | -0.048233 | 20.51 | 20.51 | 14.53 | 23.05 | 3 | 0.61 | 20 | 3
2018-09-17 23:00 | 14261.3542 | -0.048233 | 19.25 | 21.06 | 14.84 | 20.5 | 2.5 | 0.56 | 20 | 2.72
2018-09-18 | 14038.1042 | -0.048233 | 18.75 | 19.56 | 15.1 | 19.69 | 1.8 | 0.45 | 3 | 2.01
2018-09-18 01:00 | 13853.8042 | -0.048233 | 17.83 | 18.38 | 14.4 | 18.82 | 1.49 | 0.5 | 3 | 1.3
2018-09-18 02:00 | 13780.6542 | -0.048233 | 16.91 | 17.56 | 12.21 | 17.91 | 1.49 | 0.97 | 2.99 | 1.29
2018-09-18 03:00 | 13756.9042 | -0.048233 | 16.18 | 17.85 | 11.55 | 18.31 | 1.49 | 0.97 | 2.61 | 1.25
2018-09-18 04:00 | 15205.6641 | -0.048233 | 16.15 | 18.01 | 11.54 | 18.59 | 1.49 | 0.97 | 2.5 | 1.29
2018-09-18 05:00 | 15187.7291 | -0.048233 | 16.56 | 18.35 | 14.88 | 19.04 | 2.01 | 0.97 | 3 | 2.01
2018-09-18 06:00 | 15139.6472 | 7.3765 | 16.79 | 20.27 | 15.51 | 22.02 | 2.1 | 0.99 | 2.46 | 2.1
2018-09-18 07:00 | 15112.2863 | 203.442 | 17.31 | 21.2 | 15.61 | 22.26 | 1.8 | 0.99 | 2.62 | 1.8
2018-09-18 08:00 | 15489.3517 | 357.85 | 17.36 | 20.9 | 16.71 | 25.05 | 2.11 | 0.99 | 3.5 | 2.11
2018-09-18 09:00 | 16369.3589 | 818.98 | 18.48 | 21.22 | 19.66 | 23.33 | 3 | 0.99 | 2.61 | 3
2018-09-18 10:00 | 15124.19 | 1003.2 | 19.61 | 21.56 | 19.23 | 28.96 | 3 | 1.22 | 2 | 3
2018-09-18 11:00 | 16989.3507 | 1114.65 | 21.76 | 22.37 | 19.79 | 30.75 | 5.07 | 7.5 | 0.73 | 4.51
2018-09-18 12:00 | 15502.4135 | 1131.33 | 60.95 | 49.33 | 30.23 | 34.35 | 19.88 | 9.89 | 1 | 14.16
2018-09-18 13:00 | 15480.7535 | 1032.53 | 67.59 | 28.7 | 34.63 | 46.67 | 33.87 | 23.18 | 1 | 24.7
2018-09-18 14:00 | 15389.1972 | 928.155 | 36.08 | 29.27 | 36.23 | 46 | 41.79 | 7.72 | 1 | 31.84
2018-09-18 15:00 | 16937.66 | 725.654 | 58.54 | 30.31 | 36.84 | 59.24 | 49.93 | 13.55 | 1 | 41.28
2018-09-18 16:00 | 15141.3983 | 459.314 | 667.0011 | 57.97 | 37.39 | 53.05 | 50.87 | 13.01 | 1 | 43.92
2018-09-18 17:00 | 16525.2592 | 74.7528 | 180.46 | 91.49 | 34.8 | 39.72 | 26.77 | 6.99 | 2.11 | 15.37
2018-09-18 18:00 | 14914.9542 | -0.048233 | 33.09 | 32.42 | 23.33 | 31.47 | 22.16 | 10.3 | 2 | 15
2018-09-18 19:00 | 14877.9042 | -0.048233 | 30.88 | 27.7 | 23.47 | 30.03 | 6.11 | 1 | 1.28 | 2.61
2018-09-18 20:00 | 16600.3741 | -0.048233 | 29.71 | 24.61 | 22.04 | 29.39 | 18.67 | 1 | 1.24 | 2.99
2018-09-18 21:00 | 16429.4641 | -0.048233 | 18.69 | 22.01 | 19.31 | 26.24 | 3 | 1 | 4 | 2.69
2018-09-18 22:00 | 14634.7042 | -0.048233 | 19.31 | 19.93 | 15.58 | 23.46 | 2.5 | 0.5 | 20 | 3.75
2018-09-18 23:00 | 16129.8441 | -0.048233 | 18.49 | 19.1 | 14.79 | 22 | 2.5 | 0.5 | 20 | 2.76
2018-09-19 | 15910.4041 | -0.048233 | 18.34 | 19.49 | 16.42 | 21.5 | 2.01 | 0.5 | 9.11 | 2.01
2018-09-19 01:00 | 14177.7542 | -0.048233 | 18 | 18.51 | 15.59 | 20 | 1.54 | 0.5 | 3.25 | 1.54
2018-09-19 02:00 | 15581.2441 | -0.048233 | 16.92 | 17.62 | 15.97 | 19.28 | 1.51 | 0.97 | 2.61 | 1.31
2018-09-19 03:00 | 13922.2042 | -0.048233 | 16.2 | 17.22 | 15.52 | 18.59 | 1.51 | 0.97 | 2.11 | 1.31
2018-09-19 04:00 | 15645.5991 | -0.048233 | 16.27 | 17.4 | 16.7 | 19.33 | 1.61 | 0.97 | 2 | 1.61
2018-09-19 05:00 | 16778.6691 | -0.048233 | 17.05 | 18.88 | 17.55 | 20.45 | 1.95 | 0.97 | 3.32 | 2.1
2018-09-19 06:00 | 17236.9028 | 8.1082 | 17.01 | 20.71 | 20.02 | 26.25 | 2 | 0.99 | 3.46 | 3.01
2018-09-19 07:00 | 20331.6002 | 237.659 | 17.39 | 20.88 | 21.21 | 23.01 | 2 | 0.99 | 3.46 | 2
2018-09-19 08:00 | 19206.9119 | 538.802 | 18.15 | 20.42 | 21.1 | 23.69 | 2 | 0.99 | 3.5 | 3
2018-09-19 09:00 | 21531.4384 | 811.672 | 18.41 | 20.54 | 22.03 | 26.78 | 3.13 | 0.99 | 3.32 | 3.13
2018-09-19 10:00 | 22363.5155 | 969.645 | 19.45 | 20.52 | 24.07 | 30.01 | 4.77 | 10.93 | 1 | 4.91
2018-09-19 11:00 | 19883.329 | 1064.82 | 394.2257 | 349.9 | 24.59 | 31.28 | 21.98 | 21.72 | 2.11 | 21.76
2018-09-19 12:00 | 22439.7972 | 1138.95 | 36.27 | 23.55 | 24.46 | 35.28 | 32.08 | 54.4973 | 1 | 31.19
2018-09-19 13:00 | 22481.5541 | 1091.53 | 51.05 | 28.38 | 24.78 | 42.6 | 90.8741 | 88.0573 | 1 | 89.8662
2018-09-19 14:00 | 21011.0297 | 966.668 | 51.45 | 30.97 | 30.32 | 46.75 | 463.8478 | 449.6116 | 1 | 462.4306
2018-09-19 15:00 | 17844.8998 | 745.105 | 129.88 | 59.45 | 31.46 | 53.43 | 500.3678 | 487.2216 | 1 | 498.5106
2018-09-19 16:00 | 18869.6424 | 408.917 | 110.97 | 30.62 | 30.72 | 47.6 | 525.2878 | 512.2216 | 1 | 521.9006
2018-09-19 17:00 | 18241.4406 | 145.465 | 110.35 | 29.12 | 31.3 | 34.15 | 79.9141 | 67.5373 | 2.11 | 45.23
2018-09-19 18:00 | 18183.9291 | -0.048233 | 98.05 | 32.11 | 28.56 | 32.16 | 24.25 | 14.5 | 2.69 | 16.29
2018-09-19 19:00 | 18301.0341 | -0.048233 | 31.61 | 30.3 | 29.3 | 30.15 | 20.86 | 4.61 | 2 | 4.78
2018-09-19 20:00 | 18234.5691 | -0.048233 | 30.08 | 28.05 | 22.51 | 28.52 | 6 | 1.98 | 3.01 | 3.47
2018-09-19 21:00 | 16161.3542 | -0.048233 | 19.57 | 23.57 | 21 | 28.7 | 3.39 | 1.34 | 8.25 | 3.39
2018-09-19 22:00 | 17234.4291 | -0.048233 | 19.66 | 19.66 | 19.04 | 24.02 | 3.11 | 0.5 | 20 | 3.75
2018-09-19 23:00 | 14942.5042 | -0.048233 | 19.23 | 20.56 | 17.09 | 24.54 | 3 | 0.5 | 20 | 3
2018-09-20 | 14721.1542 | -0.048233 | 19 | 19 | 16.22 | 20.01 | 1.76 | 0.5 | 3.46 | 2.01
2018-09-20 01:00 | 14515.0042 | -0.048233 | 18.94 | 19.08 | 15.23 | 18.69 | 1.61 | 0.5 | 2.99 | 1.11
2018-09-20 02:00 | 14340.2042 | -0.048233 | 17.13 | 18.63 | 13.66 | 18.34 | 1.61 | 0.97 | 2.61 | 1.01
2018-09-20 03:00 | 14263.2542 | -0.048233 | 16.64 | 18.49 | 12.35 | 17.96 | 1.61 | 0.97 | 2.11 | 1
2018-09-20 04:00 | 16298.6441 | -0.048233 | 16.01 | 18.64 | 13.58 | 18.56 | 1.61 | 0.97 | 2 | 1.01
2018-09-20 05:00 | 15702.5042 | -0.048233 | 17.26 | 19.62 | 17.12 | 21.81 | 1.76 | 0.97 | 3 | 2.31
2018-09-20 06:00 | 17668.8654 | 6.8057 | 17.03 | 24.22 | 16.74 | 24.24 | 2 | 0.99 | 3.11 | 3
2018-09-20 07:00 | 18721.5132 | 191.856 | 17.1 | 20.97 | 14.75 | 22.88 | 2 | 0.99 | 3.01 | 1.46
2018-09-20 08:00 | 18525.5899 | 245.621 | 16.95 | 20.1 | 17.7 | 25.18 | 2 | 0.99 | 3.5 | 2.5
2018-09-20 09:00 | 22051.6026 | 422.993 | 18.96 | 20.38 | 19.35 | 28.8 | 2.75 | 1 | 3.37 | 3
2018-09-20 10:00 | 22333.3319 | 568.035 | 41.6 | 22.5 | 19.17 | 31.92 | 2.72 | 8.94 | 1.26 | 3
2018-09-20 11:00 | 20274.3262 | 855.396 | 19.57 | 23.65 | 32.46 | 35.76 | 5 | 11.97 | 0.74 | 5
2018-09-20 12:00 | 22348.0175 | 426.955 | 30.31 | 28.73 | 34.04 | 38.48 | 5.76 | 15 | 1 | 14.78
2018-09-20 13:00 | 20596.0389 | 897.041 | 55.9 | 55.9 | 35.05 | 47.19 | 32.59 | 55.8973 | 1.42 | 31.29
2018-09-20 14:00 | 21650.7881 | 933.074 | 47.33 | 47.33 | 35.08 | 48.55 | 52.89 | 66.0973 | 1.82 | 47.25
2018-09-20 15:00 | 18417.4135 | 751.751 | 47.48 | 35.76 | 36.87 | 58.55 | 115.8241 | 433.9416 | 1.77 | 110.1262
2018-09-20 16:00 | 19057.3143 | 463.805 | 75.78 | 66.22 | 37.5 | 52.07 | 112.9741 | 421.6616 | 1 | 107.2762
2018-09-20 17:00 | 18666.8662 | 147.712 | 55.78 | 32.31 | 36.77 | 40.75 | 24.45 | 13.7 | 2.11 | 16.42
2018-09-20 18:00 | 18327.4091 | -0.048233 | 30.79 | 30.79 | 35.12 | 33.15 | 14.18 | 8.26 | 2.61 | 12.06
2018-09-20 19:00 | 16656.3042 | -0.048233 | 28.98 | 27.03 | 34.75 | 32.69 | 7.92 | 1.62 | 1 | 5.6
2018-09-20 20:00 | 18333.7391 | -0.048233 | 33.08 | 33.08 | 23.59 | 29.65 | 7.06 | 1.27 | 2.61 | 3
2018-09-20 21:00 | 18009.8541 | -0.048233 | 19.75 | 26.8 | 19.24 | 26.37 | 3.75 | 1.25 | 7.57 | 3.75
2018-09-20 22:00 | 15506.8042 | -0.048233 | 19.21 | 21.83 | 18.45 | 23.48 | 3 | 0.5 | 20 | 3
2018-09-20 23:00 | 15042.2542 | -0.048233 | 17.93 | 23.08 | 17 | 24.03 | 2.25 | 0.5 | 19.5 | 2.25
2018-09-21 | 16447.3991 | -0.048233 | 17.86 | 19.9 | 12.13 | 22.45 | 1.76 | 0.5 | 3.5 | 2.61
2018-09-21 01:00 | 14434.2542 | -0.048233 | 16.91 | 18.41 | 11.86 | 20.74 | 1.61 | 0.5 | 3.23 | 1.41
2018-09-21 02:00 | 14177.7542 | -0.048233 | 15.46 | 17.74 | 11.86 | 20.04 | 1.61 | 0.97 | 2.89 | 1.41
2018-09-21 03:00 | 14057.1042 | -0.048233 | 15.47 | 17.46 | 9.47 | 19.17 | 1.61 | 0.97 | 2.61 | 1.01
2018-09-21 04:00 | 14290.8042 | -0.048233 | 15.66 | 17.57 | 9.44 | 19.81 | 1.71 | 0.97 | 2.11 | 1.51
2018-09-21 05:00 | 15519.1542 | -0.048233 | 16.77 | 18.01 | 16.71 | 21.23 | 1.71 | 0.99 | 3.15 | 2.61
2018-09-21 06:00 | 17654.8156 | 6.0164 | 16.88 | 19.14 | 20.27 | 24.91 | 2.22 | 1 | 2.67 | 3.01
2018-09-21 07:00 | 21000.7277 | 172.903 | 17.88 | 22.24 | 20.85 | 23.39 | 2.13 | 1 | 2.84 | 2.13
2018-09-21 08:00 | 19058.5694 | 525.652 | 17.76 | 19.95 | 20 | 25.28 | 2.22 | 0.99 | 3.5 | 2.5
2018-09-21 09:00 | 21843.1515 | 689.409 | 19.27 | 19.87 | 19.26 | 25.06 | 3.48 | 0.99 | 3.5 | 3.85
2018-09-21 10:00 | 22176.0029 | 919.908 | 19.37 | 19.37 | 21.17 | 28.57 | 3.4 | 6.51 | 1 | 4.91
2018-09-21 11:00 | 22012.269 | 1108.71 | 20.92 | 20.92 | 19.88 | 36.16 | 7 | 11.5 | 0.67 | 7
2018-09-21 12:00 | 22470.4028 | 1089.96 | 22.35 | 22.35 | 20.14 | 39.68 | 6.64 | 13.45 | 1 | 12.23
2018-09-21 13:00 | 22761.9942 | 1108.35 | 135.72 | 23.72 | 22.75 | 43.44 | 19.68 | 18.79 | 1.44 | 18.79
2018-09-21 14:00 | 19270.0869 | 958.302 | 66.99 | 24.83 | 22.48 | 44.96 | 27.86 | 16.67 | 1.31 | 20.95
2018-09-21 15:00 | 20165.4968 | 749.215 | 35.82 | 27.14 | 23.61 | 49.08 | 46.63 | 58.6173 | 1 | 39.77
2018-09-21 16:00 | 17708.0608 | 429.064 | 35.25 | 31.99 | 28.94 | 45.71 | 46.5 | 58.7473 | 1 | 39.16
2018-09-21 17:00 | 17074.7053 | 142.374 | 30.24 | 22.07 | 24.67 | 35 | 21.42 | 9.51 | 2.11 | 3.83
2018-09-21 18:00 | 16538.5042 | -0.048233 | 20.83 | 20.83 | 23.21 | 29.65 | 16.08 | 6.22 | 2.64 | 4.5
2018-09-21 19:00 | 18285.2091 | -0.048233 | 20.07 | 20.07 | 29.4 | 28.02 | 8 | 2.5 | 2.11 | 5.57
2018-09-21 20:00 | 16323.8042 | -0.048233 | 21.49 | 21.49 | 22.64 | 28.76 | 5.2 | 1.25 | 2.11 | 3
2018-09-21 21:00 | 17784.0841 | -0.048233 | 19.57 | 19.57 | 19.71 | 26.55 | 3.31 | 1 | 8.25 | 3.31
2018-09-21 22:00 | 17261.8591 | -0.048233 | 19.85 | 19.9 | 19.28 | 23.33 | 2.97 | 0.5 | 20 | 2.97
2018-09-21 23:00 | 15034.6542 | -0.048233 | 18.57 | 19.63 | 18.87 | 22.48 | 2.25 | 0.5 | 19 | 2.25
2018-09-22 | 16450.5641 | -0.048233 | 18.4 | 19 | 17.23 | 20.56 | 1.76 | 0.5 | 3.95 | 2.58
2018-09-22 01:00 | 16355.6141 | -0.048233 | 17.54 | 18.86 | 13.82 | 18.56 | 1.61 | 0.5 | 3.5 | 1.61
2018-09-22 02:00 | 14492.2042 | -0.048233 | 12.45 | 18.2 | 6.96 | 18.34 | 1.51 | 0.97 | 3.5 | 1.31
2018-09-22 03:00 | 15927.2841 | -0.048233 | 8.18 | 18.15 | 5.96 | 18.25 | 1.49 | 0.97 | 2.61 | 1.25
2018-09-22 04:00 | 14627.1042 | -0.048233 | 15.64 | 17.99 | 11.89 | 18.29 | 1.49 | 0.97 | 2.41 | 1.29
2018-09-22 05:00 | 17549.8741 | -0.048233 | 17.51 | 18.02 | 15.38 | 19.43 | 1.76 | 0.97 | 3.44 | 2.2
2018-09-22 06:00 | 17974.2405 | 7.2531 | 17.73 | 18.86 | 19.6 | 24.3 | 2.11 | 1 | 3.44 | 3
2018-09-22 07:00 | 21003.5445 | 228.573 | 18.34 | 20.28 | 20.72 | 22.25 | 2.2 | 1.19 | 3.01 | 2.11
2018-09-22 08:00 | 18928.1524 | 472.371 | 17.68 | 20.47 | 20.77 | 23.5 | 2.61 | 0.99 | 3.5 | 2.61
2018-09-22 09:00 | 19977.6326 | 687.087 | 81.85 | 20.72 | 21.37 | 25.24 | 3.75 | 0.99 | 3.56 | 3.75
2018-09-22 10:00 | 20138.4971 | 815.418 | 61.77 | 19.13 | 21.06 | 27.49 | 3.93 | 1.33 | 2.11 | 4.25
2018-09-22 11:00 | 18623.2005 | 208.369 | 19.61 | 20.44 | 21.47 | 28.35 | 4.87 | 12 | 1 | 4.87
2018-09-22 12:00 | 21256.9534 | 265.771 | 21.4 | 21.4 | 21.58 | 32.21 | 5.85 | 11.41 | 1 | 6.09
2018-09-22 13:00 | 19994.6623 | 739.013 | 33.99 | 28.57 | 21.6 | 35.86 | 20.64 | 20.64 | 0.85 | 20.64
2018-09-22 14:00 | 18537.7243 | 603.394 | 37.83 | 25.85 | 22.61 | 39.8 | 24.4 | 13.2 | 1.36 | 20.24
2018-09-22 15:00 | 17569.8501 | 338.579 | 40.14 | 22.83 | 24.55 | 44.91 | 35.06 | 23.05 | 1.71 | 28.68
2018-09-22 16:00 | 19005.0363 | 62.2524 | 42.6 | 23.08 | 30.88 | 39.41 | 31.67 | 18.08 | 1.65 | 30.37
2018-09-22 17:00 | 16701.2931 | 59.3085 | 35.86 | 23.17 | 31.09 | 32.56 | 17.95 | 8.21 | 2 | 3.86
2018-09-22 18:00 | 16289.6042 | -0.048233 | 31.42 | 22.64 | 22.17 | 26.75 | 5.32 | 1.74 | 2.61 | 2.57
2018-09-22 19:00 | 18118.5191 | -0.048233 | 21.26 | 21.26 | 23.7 | 28.51 | 6.23 | 1.65 | 2.11 | 4.61
2018-09-22 20:00 | 16281.0542 | -0.048233 | 22.08 | 22.08 | 21.42 | 30.48 | 5.5 | 1.37 | 3 | 3
2018-09-22 21:00 | 15949.5042 | -0.048233 | 20.54 | 21.51 | 20.79 | 29.94 | 3.75 | 1 | 17.44 | 3
2018-09-22 22:00 | 17068.7941 | -0.048233 | 18.93 | 20.96 | 18.71 | 21.66 | 2.37 | 0.5 | 30 | 2.37
2018-09-22 23:00 | 14926.3542 | -0.048233 | 18.27 | 20.33 | 17.54 | 21.72 | 2.25 | 0.5 | 20 | 2.25
2018-09-23 | 14946.3042 | -0.048233 | 17.52 | 18.96 | 17.07 | 19.18 | 1.61 | 0.49 | 3.5 | 3.86
2018-09-23 01:00 | 16557.1191 | -0.048233 | 16.95 | 18.53 | 15.94 | 18.34 | 1.61 | 0.49 | 3 | 1.61
2018-09-23 02:00 | 16298.6441 | -0.048233 | 16.7 | 17.97 | 14.82 | 18.2 | 1.51 | 0.97 | 3 | 1.31
2018-09-23 03:00 | 16341.8991 | -0.048233 | 15.81 | 17.7 | 10.34 | 18.34 | 1.49 | 0.97 | 3 | 1.26
2018-09-23 04:00 | 14971.9542 | -0.048233 | 15.24 | 17.5 | 15.08 | 18.33 | 1.58 | 0.97 | 3 | 1.39
2018-09-23 05:00 | 16116.7042 | -0.048233 | 16.19 | 17.58 | 15.38 | 18.27 | 1.76 | 0.97 | 3.46 | 2.11
2018-09-23 06:00 | 19920.4527 | 2.9456 | 17.04 | 17.87 | 16.88 | 21.51 | 2.11 | 0.99 | 3.5 | 3
2018-09-23 07:00 | 20792.6468 | 118.67 | 17.28 | 18.36 | 16.85 | 21.92 | 2.11 | 0.99 | 3.11 | 2.11
2018-09-23 08:00 | 19291.288 | 451.619 | 16.3 | 17.74 | 17.25 | 22.72 | 2.49 | 0.99 | 7.25 | 2.72
2018-09-23 09:00 | 19448.9149 | 264.542 | 18.39 | 19.06 | 18.39 | 23.09 | 2.61 | 0.99 | 16.8 | 3
2018-09-23 10:00 | 19712.1618 | 337.644 | 18.47 | 19.12 | 18.75 | 23.83 | 2.72 | 6.79 | 2.19 | 4.35
2018-09-23 11:00 | 22673.1137 | 928.103 | 19.39 | 20.7 | 19.48 | 25.32 | 4.05 | 6.79 | 2.11 | 5.27
2018-09-23 12:00 | 22489.6776 | 1015.23 | 21 | 21 | 22.1 | 30.5 | 7.11 | 10 | 1 | 6.76
2018-09-23 13:00 | 21797.4964 | 672.134 | 21 | 21 | 22.27 | 31.38 | 18 | 17.79 | 0.66 | 17.79
2018-09-23 14:00 | 19828.8516 | 730.12 | 21.52 | 21.52 | 22.14 | 36.89 | 21.15 | 7.76 | 1.24 | 17.01
2018-09-23 15:00 | 18484.2773 | 595.642 | 21.86 | 21.86 | 22.58 | 41.84 | 29.1 | 12 | 1.39 | 23.35
2018-09-23 16:00 | 18074.3739 | 398.108 | 30.88 | 20.98 | 22.44 | 41.5 | 30.76 | 9.98 | 1 | 30.03
2018-09-23 17:00 | 15934.4184 | 132.072 | 19.81 | 19.81 | 22.14 | 33.11 | 15.33 | 0.99 | 2.11 | 5.8
2018-09-23 18:00 | 17336.7641 | -0.048233 | 19.92 | 19.92 | 22.02 | 26.29 | 6.71 | 1.31 | 4 | 3.48
2018-09-23 19:00 | 15558.1042 | -0.048233 | 20.38 | 20.38 | 22.48 | 25.35 | 4.95 | 0.82 | 2.11 | 3.58
2018-09-23 20:00 | 17110.9941 | -0.048233 | 20.3 | 20.3 | 21.68 | 25.63 | 3.88 | 0.82 | 2.61 | 2.86
2018-09-23 21:00 | 15126.8042 | -0.048233 | 19.5 | 21.19 | 20.79 | 26.04 | 2.61 | 0.82 | 17.01 | 3
2018-09-23 22:00 | 16038.0591 | -0.048233 | 17.77 | 19.65 | 18.65 | 21.6 | 2.33 | 0.5 | 20 | 2.33
2018-09-23 23:00 | 15627.6641 | -0.048233 | 17.37 | 19.84 | 17.34 | 20.34 | 2.11 | 0.5 | 20 | 2.11
2018-09-24 | 15399.7841 | -0.048233 | 16.97 | 19.13 | 11.5 | 21.04 | 1.79 | 0.5 | 9.08 | 2.1
2018-09-24 01:00 | 15350.1991 | -0.048233 | 16.59 | 18.2 | 12.39 | 17.98 | 1.49 | 0.5 | 3.01 | 1.29
2018-09-24 02:00 | 15118.0991 | -0.048233 | 16.16 | 17.68 | 6.96 | 17.55 | 1.49 | 0.89 | 2.11 | 1.29
2018-09-24 03:00 | 13564.0542 | -0.048233 | 15.69 | 17.42 | 10.53 | 17.42 | 1.46 | 0.89 | 2 | 1.25
2018-09-24 04:00 | 15216.2141 | -0.048233 | 16.28 | 17.9 | 7.76 | 17.36 | 1.49 | 0.89 | 2 | 1.29
2018-09-24 05:00 | 14045.7042 | -0.048233 | 17.01 | 17.91 | 11.02 | 17.37 | 2.01 | 0.86 | 3.72 | 2.01
2018-09-24 06:00 | 14590.3715 | 4.2858 | 17.15 | 17.15 | 13.93 | 20.26 | 2.22 | 1 | 3.5 | 87.2162
2018-09-24 07:00 | 14508.5007 | 153.106 | 17.55 | 17.55 | 15.33 | 19.86 | 2.22 | 0.99 | 3.5 | 2.1
2018-09-24 08:00 | 14679.8484 | 327.472 | 17.59 | 18.32 | 17.87 | 21.68 | 2.52 | 0.99 | 8.61 | 2.73
2018-09-24 09:00 | 16910.5823 | 641.988 | 18.38 | 19.13 | 19.3 | 23.9 | 3.31 | 1.11 | 17.84 | 3.11
2018-09-24 10:00 | 15020.7103 | 948.274 | 18.28 | 18.28 | 17.25 | 25.83 | 4 | 1.14 | 2.78 | 4.68
2018-09-24 11:00 | 15204.37 | 1051.6 | 19.3 | 19.3 | 18.17 | 24.75 | 5.01 | 7.27 | 2 | 5.68
2018-09-24 12:00 | 15644.7235 | 1018.13 | 20.19 | 20.19 | 16.8 | 26.62 | 5.61 | 8.77 | 1 | 5.61
2018-09-24 13:00 | 17337.774 | 979.909 | 39.89 | 20.57 | 15.54 | 31.05 | 13.19 | 11 | 0.87 | 13.19
2018-09-24 14:00 | 15437.5646 | 817.068 | 28.65 | 22.49 | 13.3 | 36.61 | 19.62 | 1 | 1.49 | 17.94
2018-09-24 15:00 | 15030.7119 | 536.802 | 30.26 | 22.6 | 14.11 | 45.38 | 27.4 | 2.5 | 1.73 | 23.4
2018-09-24 16:00 | 15036.942 | 400.36 | 50.54 | 23.99 | 14.52 | 40.23 | 30.56 | 1 | 1 | 29.31
2018-09-24 17:00 | 14821.748 | 118.84 | 32.17 | 22.74 | 16.05 | 31.66 | 14.49 | 0.99 | 2.11 | 4.67
2018-09-24 18:00 | 16245.8941 | -0.048233 | 21.64 | 21.64 | 23.38 | 27.28 | 7.11 | 1 | 3.03 | 4.5
2018-09-24 19:00 | 16107.6891 | -0.048233 | 21.22 | 21.22 | 28.68 | 26.39 | 5.56 | 0.97 | 1 | 4.22
2018-09-24 20:00 | 14451.3542 | -0.048233 | 21.63 | 21.63 | 17.04 | 27.31 | 4.42 | 0.97 | 2.61 | 2.85
2018-09-24 21:00 | 14344.0042 | -0.048233 | 20.37 | 20.37 | 14.49 | 25.59 | 2.61 | 0.97 | 11.68 | 3
2018-09-24 22:00 | 14021.9542 | -0.048233 | 20.3 | 20.3 | 10.75 | 22.21 | 2.36 | 0.5 | 15 | 2.65
2018-09-24 23:00 | 15305.8891 | -0.048233 | 333.8357 | 19.75 | 11.8 | 21.16 | 2.11 | 0.5 | 15 | 2.11
2018-09-25 | 15129.7041 | -0.048233 | 19.46 | 20.36 | 10.27 | 19.2 | 1.86 | 0.5 | 3.5 | 2.92
2018-09-25 01:00 | 13548.8542 | -0.048233 | 18.83 | 18.83 | 7.42 | 18.21 | 1.61 | 0.5 | 2.61 | 1.61
2018-09-25 02:00 | 13338.9042 | -0.048233 | 17.87 | 17.87 | 6.98 | 17.62 | 1.61 | 0.89 | 2.11 | 1.41
2018-09-25 03:00 | 14734.0791 | -0.048233 | 18.21 | 18.48 | 5.18 | 18.09 | 1.51 | 0.89 | 2 | 1.31
2018-09-25 04:00 | 14479.8241 | -0.048233 | 18.17 | 19.11 | 5.66 | 18.34 | 1.61 | 0.89 | 2 | 1.41
2018-09-25 05:00 | 14341.6191 | -0.048233 | 18.48 | 18.58 | 5.7 | 20 | 2.01 | 0.89 | 2.87 | 2.11
2018-09-25 06:00 | 13908.089 | 2.0228 | 18.91 | 18.92 | 8.83 | 27.35 | 2.22 | 0.99 | 3.11 | 25
2018-09-25 07:00 | 12209.2585 | 87.8511 | 19.47 | 19.94 | 7.23 | 23.72 | 2.11 | 1 | 3.11 | 2.1
2018-09-25 08:00 | 12548.1396 | 203.568 | 18.43 | 19.62 | 12.15 | 25.2 | 2.22 | 0.99 | 3.5 | 2.5
2018-09-25 09:00 | 13155.144 | 652.52 | 19.91 | 19.91 | 13.3 | 23.67 | 2.61 | 1.22 | 4.62 | 2.61
2018-09-25 10:00 | 12908.5962 | 236.996 | 19.63 | 19.63 | 13.44 | 25.02 | 3.34 | 1.18 | 1.45 | 3.94
2018-09-25 11:00 | 12889.7985 | 511.209 | 20.02 | 20.02 | 13.49 | 29.37 | 4.58 | 1.2 | 2 | 4.58
2018-09-25 12:00 | 14861.3609 | 783.598 | 21.31 | 21.93 | 32.93 | 32.72 | 5.5 | 7.14 | 1 | 5.3
2018-09-25 13:00 | 14436.2296 | 192.63 | 34.13 | 25.84 | 36.77 | 37.92 | 13.52 | 13.51 | 1 | 13.52
2018-09-25 14:00 | 14841.7062 | 162.968 | 33.13 | 27.73 | 37.29 | 42.35 | 15.52 | 0.99 | 1.34 | 15.32
2018-09-25 15:00 | 15726.1317 | 676.286 | 31.02 | 28.44 | 39.6 | 47.59 | 21.17 | 1.47 | 2 | 19.96
2018-09-25 16:00 | 13841.9588 | 433.483 | 29.72 | 29.72 | 43.19 | 45.52 | 23.23 | 1.38 | 1 | 23.03
2018-09-25 17:00 | 15145.6655 | 108.081 | 18.96 | 27.72 | 42.16 | 34.24 | 5.67 | 0.99 | 2.11 | 4.29
2018-09-25 18:00 | 13758.8042 | -0.048233 | 18.13 | 25.04 | 38.66 | 31.63 | 3 | 1.24 | 4 | 3
2018-09-25 19:00 | 15413.4991 | -0.048233 | 19.66 | 24.16 | 37.83 | 30.83 | 3 | 0.82 | 2.11 | 3
2018-09-25 20:00 | 13679.9542 | -0.048233 | 21.6 | 24.28 | 33.98 | 30.88 | 2.33 | 0.82 | 8.61 | 2.11
2018-09-25 21:00 | 13515.6042 | -0.048233 | 20.52 | 20.52 | 14.49 | 24.94 | 3 | 0.82 | 28.28 | 3
2018-09-25 22:00 | 13092.8542 | -0.048233 | 22.89 | 23.49 | 11.1 | 23.99 | 2.25 | 0.5 | 15 | 2.25
2018-09-25 23:00 | 12771.7542 | -0.048233 | 19.19 | 21.21 | 11.11 | 21.95 | 2 | 0.5 | 22 | 2
2018-09-26 | 12660.6042 | -0.048233 | 18.31 | 20.03 | 4.73 | 20.5 | 1.95 | 0.5 | 24.27 | 2.7
2018-09-26 01:00 | 13753.9841 | -0.048233 | 17.72 | 18.82 | 3.98 | 19.24 | 1.71 | 0.5 | 2 | 1.71
2018-09-26 02:00 | 11897.7542 | -0.048233 | 17.31 | 18.32 | 2.7 | 18.5 | 1.71 | 0.97 | 2 | 1.51
2018-09-26 03:00 | 11667.8542 | -0.048233 | 16.5 | 18.45 | 2.68 | 18.24 | 1.64 | 0.97 | 2 | 1.44
2018-09-26 04:00 | 12995.4391 | -0.048233 | 16.61 | 18.57 | 2.81 | 18.43 | 1.71 | 0.97 | 2 | 1.71
2018-09-26 05:00 | 14225.5691 | -0.048233 | 12.33 | 19.56 | 10.45 | 19.11 | 2 | 0.97 | 9.82 | 2.11
2018-09-26 06:00 | 16826.6949 | 5.4738 | 17.34 | 21.37 | 13.08 | 23.36 | 2.11 | 0.97 | 3.11 | 32
2018-09-26 07:00 | 16698.7998 | 228.684 | 17.38 | 21.06 | 13.04 | 22.62 | 2.01 | 0.97 | 3.46 | 2.1
2018-09-26 08:00 | 17520.6049 | 533.742 | 16.75 | 20.47 | 15.75 | 22.8 | 2.11 | 0.97 | 5.1 | 2.21
2018-09-26 09:00 | 18702.6177 | 804.966 | 18.12 | 21.06 | 15.77 | 23.98 | 3 | 0.97 | 110.2834 | 3
2018-09-26 10:00 | 20989.7926 | 984.538 | 19.41 | 20.56 | 18.82 | 25.38 | 2.61 | 0.97 | 2.28 | 3.5
2018-09-26 11:00 | 20634.2386 | 1099.52 | 68.95 | 20.5 | 20.01 | 32.58 | 3.6 | 10.53 | 2.11 | 4
2018-09-26 12:00 | 19196.8115 | 1112.17 | 163.74 | 22.21 | 32.77 | 31.48 | 5 | 8.5 | 1 | 4.45
2018-09-26 13:00 | 21067.7064 | 1091.39 | 151.29 | 23.27 | 37.27 | 39.87 | 12.48 | 13.96 | 2 | 12.28
2018-09-26 14:00 | 19510.9548 | 941.796 | 74.42 | 22.47 | 38.29 | 43.87 | 17.24 | 0.99 | 1.5 | 16.88
2018-09-26 15:00 | 17653.009 | 743.71 | 21.73 | 21.73 | 43.2 | 49.46 | 25.95 | 0.99 | 1.1 | 24.7
2018-09-26 16:00 | 17035.181 | 447.091 | 21.8 | 21.8 | 46.64 | 43.81 | 29.75 | 0.99 | 1 | 29.49
2018-09-26 17:00 | 14752.9794 | 128.452 | 20.87 | 20.87 | 45.02 | 33.86 | 15.69 | 0.99 | 2.37 | 5
2018-09-26 18:00 | 15953.6591 | -0.048233 | 22.21 | 22.24 | 38.54 | 28.8 | 5.87 | 0.97 | 8.11 | 3.35
2018-09-26 19:00 | 16091.8641 | -0.048233 | 19.97 | 22.17 | 38.3 | 28.56 | 5.76 | 0.97 | 3.11 | 3.79
2018-09-26 20:00 | 15877.6991 | -0.048233 | 21.04 | 22.77 | 34.34 | 29.32 | 4.32 | 0.97 | 8.61 | 3
2018-09-26 21:00 | 14004.8542 | -0.048233 | 18.84 | 22.2 | 14 | 26.98 | 3 | 0.97 | 25 | 3
2018-09-26 22:00 | 14973.5641 | -0.048233 | 19.18 | 22.74 | 13.78 | 24.05 | 2.6 | 0.5 | 17.44 | 2.6
2018-09-26 23:00 | 13024.4542 | -0.048233 | 19.54 | 20.14 | 13.05 | 22.37 | 2 | 0.5 | 15 | 2
2018-09-27 | 12715.7042 | -0.048233 | 18.22 | 19.87 | 11.16 | 20 | 2 | 0.5 | 2.61 | 2.01
2018-09-27 01:00 | 12344.2542 | -0.048233 | 17.91 | 19.01 | 5.13 | 19.29 | 1.94 | 0.5 | 2 | 1
2018-09-27 02:00 | 13632.6591 | -0.048233 | 17.6 | 18.65 | 4.97 | 18.5 | 1.71 | 0.61 | 2 | 1
2018-09-27 03:00 | 13520.8291 | -0.048233 | 17.15 | 18.3 | 5.06 | 18.59 | 1.52 | 0.61 | 2 | 0.91
2018-09-27 04:00 | 13832.0541 | -0.048233 | 16.75 | 18.13 | 5.08 | 18.42 | 1.61 | 0.61 | 2 | 1
2018-09-27 05:00 | 14879.6691 | -0.048233 | 16.61 | 18.95 | 5.75 | 19.56 | 2 | 0.61 | 2.11 | 2
2018-09-27 06:00 | 15255.9713 | 5.9172 | 16.81 | 19.77 | 11.2 | 25.17 | 2.11 | 0.97 | 2.61 | 25
2018-09-27 07:00 | 18661.0204 | 238.171 | 884.2211 | 616.61 | 9.76 | 23.69 | 2 | 0.97 | 2.61 | 1.73
2018-09-27 08:00 | 17015.4852 | 510.037 | 16.44 | 19.04 | 12.81 | 23.5 | 2.11 | 0.97 | 3.46 | 2.5
2018-09-27 09:00 | 19224.6709 | 99.4369 | 17.95 | 19.38 | 12.77 | 28.16 | 3 | 0.97 | 4.29 | 2.1
2018-09-27 10:00 | 18582.8407 | 881.885 | 18.85 | 19.99 | 13.89 | 29.68 | 3 | 0.97 | 3.09 | 3.45
2018-09-27 11:00 | 17561.5385 | 1081.83 | 19.12 | 21.97 | 13.86 | 34.45 | 3.72 | 0.85 | 0.13 | 4
2018-09-27 12:00 | 19339.834 | 1058.72 | 20.21 | 29.16 | 34.12 | 36.66 | 5.03 | 6.68 | 0.55 | 5
2018-09-27 13:00 | 17974.912 | 1075.96 | 21.22 | 28.52 | 38.15 | 44.92 | 7.98 | 10.15 | 0.89 | 10.15
2018-09-27 14:00 | 18536.4639 | 760.108 | 173.95 | 173.95 | 39.65 | 48.35 | 17.94 | 0.97 | 1 | 14.46
2018-09-27 15:00 | 15851.5907 | 536.885 | 24.23 | 24.78 | 44.27 | 46.22 | 22.62 | 0.97 | 2 | 22.31
2018-09-27 16:00 | 15273.1813 | 431.033 | 21.82 | 21.82 | 45.8 | 41.46 | 26.87 | 0.99 | 1 | 26.67
2018-09-27 17:00 | 16392.4317 | 124.85 | 22.21 | 22.21 | 43.33 | 32.88 | 17.02 | 0.97 | 2.11 | 4.39
2018-09-27 18:00 | 14503.6042 | -0.048233 | 22.04 | 22.04 | 40.07 | 28.84 | 5 | 1 | 2.61 | 3.1
2018-09-27 19:00 | 16311.3041 | -0.048233 | 21.85 | 23.42 | 40 | 31.74 | 4.06 | 0.97 | 1.5 | 3.1
2018-09-27 20:00 | 14516.9042 | -0.048233 | 20.35 | 23.71 | 30.65 | 31.78 | 3.5 | 0.97 | 3.01 | 3
2018-09-27 21:00 | 15802.7941 | -0.048233 | 19.07 | 21.89 | 16.67 | 27.53 | 3 | 0.97 | 4 | 2.61
2018-09-27 22:00 | 13718.9042 | -0.048233 | 19.22 | 20.61 | 13.76 | 23.53 | 2.09 | 0.5 | 12 | 2.11
2018-09-27 23:00 | 13129.9042 | -0.048233 | 17.33 | 22.7 | 13.87 | 23 | 2 | 0.5 | 12 | 2
2018-09-28 | 14322.6291 | -0.048233 | 15.7 | 18.83 | 12.62 | 22.57 | 2 | 0.5 | 2.61 | 2.21
2018-09-28 01:00 | 14256.1641 | -0.048233 | 12.18 | 18.03 | 12.21 | 21.51 | 1.83 | 0.5 | 2.5 | 1
2018-09-28 02:00 | 14101.0791 | -0.048233 | 5.23 | 18.16 | 6.86 | 20.19 | 1.61 | 0.61 | 2.5 | 1
2018-09-28 03:00 | 13909.0691 | -0.048233 | 5.58 | 18.92 | 6.56 | 20.72 | 1.61 | 0.61 | 2.5 | 0.8
2018-09-28 04:00 | 14252.9991 | -0.048233 | 14.77 | 18.65 | 9.91 | 20.88 | 1.97 | 0.61 | 2.5 | 1
2018-09-28 05:00 | 15175.0691 | -0.048233 | 16.73 | 18.72 | 14.78 | 21.69 | 2.11 | 0.89 | 2.61 | 2.21
2018-09-28 06:00 | 15706.5277 | 5.1871 | 17.75 | 20.2 | 19.22 | 28.79 | 2.3 | 0.97 | 3.01 | 24.17
2018-09-28 07:00 | 19712.2963 | 231.641 | 18.48 | 20.14 | 19.89 | 27.45 | 2.25 | 0.97 | 3.01 | 1.61
2018-09-28 08:00 | 18982.1613 | 554.57 | 18.41 | 19.97 | 20.31 | 27.15 | 2.7 | 0.97 | 3.5 | 2.8
2018-09-28 09:00 | 18989.1596 | 783.589 | 18.77 | 19.99 | 18.88 | 27.48 | 3.5 | 0.97 | 3.11 | 2.21
2018-09-28 10:00 | 22401.9544 | 970.08 | 19.13 | 19.9 | 20.65 | 28.07 | 3.2 | 0.97 | 2 | 3.45
2018-09-28 11:00 | 20288.0604 | 983.389 | 20.27 | 20.27 | 20.69 | 33.69 | 5 | 0.97 | 0.08 | 5.05
2018-09-28 12:00 | 21760.3751 | 987.948 | 21.87 | 23.39 | 20.58 | 34.74 | 5 | 7.51 | 0.5 | 4.76
2018-09-28 13:00 | 18794.686 | 1043.88 | 23.14 | 23.14 | 21.35 | 43.06 | 8.97 | 9 | 1 | 7.81
2018-09-28 14:00 | 17624.0019 | 903.581 | 28.23 | 24.22 | 19.66 | 48.92 | 15.66 | 0.99 | 1 | 12.01
2018-09-28 15:00 | 16566.403 | 649.319 | 31.53 | 24.75 | 18.97 | 50.51 | 21.52 | 1.18 | 1.68 | 18.42
2018-09-28 16:00 | 17637.4299 | 402.943 | 59.29 | 24.16 | 20.11 | 42.23 | 31.24 | 0.99 | 1 | 27.24
2018-09-28 17:00 | 17083.9326 | 109.301 | 78.86 | 22.38 | 20.48 | 33.6 | 14.78 | 1.15 | 2.11 | 2.93
2018-09-28 18:00 | 14922.5542 | -0.048233 | 32.7 | 21.72 | 21.24 | 31.55 | 7.86 | 1.27 | 10 | 4.33
2018-09-28 19:00 | 14946.3042 | -0.048233 | 21.53 | 21.53 | 21.18 | 31.13 | 6 | 0.97 | 1.5 | 3.09
2018-09-28 20:00 | 16289.1491 | -0.048233 | 35.8 | 21.51 | 18.65 | 30.37 | 4.76 | 0.97 | 3.01 | 2.5
2018-09-28 21:00 | 14391.5042 | -0.048233 | 57.93 | 20.83 | 16.55 | 28.44 | 2.94 | 0.97 | 3.5 | 2.94
2018-09-28 22:00 | 15511.6141 | -0.048233 | 19.4 | 21.05 | 14.51 | 24.62 | 2.11 | 0.5 | 15 | 2.11
2018-09-28 23:00 | 13484.2542 | -0.048233 | 17.92 | 20.89 | 12.28 | 24.34 | 2 | 0.5 | 15 | 2
2018-09-29 | 13171.7042 | -0.048233 | 17.51 | 20.03 | 15.91 | 24.54 | 2 | 0.49 | 3.5 | 2.01
2018-09-29 01:00 | 13165.0542 | -0.048233 | 16.63 | 19.78 | 12.87 | 20.26 | 1.52 | 0.49 | 3.5 | 1.52
2018-09-29 02:00 | 13026.3542 | -0.048233 | 16.06 | 18.99 | 12.83 | 19.43 | 1.52 | 0.5 | 2.99 | 1.32
2018-09-29 03:00 | 14324.7391 | -0.048233 | 16.1 | 18.66 | 12.46 | 19.24 | 1.52 | 0.5 | 1 | 1.32
2018-09-29 04:00 | 14611.6991 | -0.048233 | 16.37 | 18.49 | 12.07 | 18.85 | 1.52 | 0.5 | 2.49 | 1.52
2018-09-29 05:00 | 15910.4041 | -0.048233 | 16.85 | 18.89 | 13.79 | 19.52 | 2.1 | 0.6 | 3.92 | 2.25
2018-09-29 06:00 | 16363.4739 | 4.7094 | 18.19 | 19.59 | 18.18 | 25.14 | 2.46 | 1 | 3.11 | 21.38
2018-09-29 07:00 | 19092.1208 | 223.797 | 18.62 | 20.18 | 19.55 | 27.26 | 2.25 | 0.99 | 3.01 | 2.1
2018-09-29 08:00 | 19715.8273 | 567.988 | 18.36 | 20.03 | 20.24 | 24.65 | 2.96 | 0.99 | 3.5 | 2.61
2018-09-29 09:00 | 20877.2072 | 808.822 | 19.02 | 21.3 | 20.23 | 24.83 | 4.15 | 1 | 3.01 | 2.21
2018-09-29 10:00 | 21425.7112 | 974.731 | 20.87 | 21.2 | 19.86 | 29.64 | 3.51 | 2 | 1 | 3.37
2018-09-29 11:00 | 18642.439 | 1031.62 | 20.56 | 21.26 | 20.56 | 32.19 | 5.16 | 2 | 1 | 5.16
2018-09-29 12:00 | 19172.8715 | 1113.97 | 21.11 | 24.23 | 20.13 | 34.07 | 5.59 | 2.5 | 0.3 | 4.95
2018-09-29 13:00 | 18811.786 | 1047.88 | 31.12 | 31.12 | 21.1 | 36.77 | 8.98 | 6.76 | 0.66 | 5.62
2018-09-29 14:00 | 19978.5983 | 913.06 | 31.09 | 31.09 | 21.1 | 43.52 | 13.63 | 0.99 | 0.71 | 12.71
2018-09-29 15:00 | 18264.3531 | 650.183 | 72.21 | 20.92 | 20.48 | 46.61 | 19.94 | 10 | 0.95 | 17.82
2018-09-29 16:00 | 15522.7786 | 399.767 | 64.15 | 20.77 | 20.97 | 39.16 | 28.68 | 17.54 | 0.88 | 25.94
2018-09-29 17:00 | 14918.6831 | 107.877 | 69.43 | 23.52 | 21.78 | 30.45 | 16.02 | 1 | 2.11 | 4.45
2018-09-29 18:00 | 15865.0391 | -0.048233 | 32.77 | 23.1 | 21.94 | 27.44 | 4.9 | 8.58 | 10 | 3
2018-09-29 19:00 | 14223.3542 | -0.048233 | 22.89 | 23.29 | 23.06 | 27.56 | 5.61 | 0.61 | 2.01 | 3.56
2018-09-29 20:00 | 14023.8542 | -0.048233 | 29.34 | 27.21 | 21.76 | 30.55 | 4.36 | 0.61 | 3.01 | 3
2018-09-29 21:00 | 13980.1542 | -0.048233 | 20.48 | 22.82 | 18.71 | 27.74 | 3 | 0.61 | 3.5 | 2.46
2018-09-29 22:00 | 15234.1491 | -0.048233 | 19.98 | 22.87 | 15.64 | 24.53 | 2.41 | 0.49 | 16.05 | 2.41
2018-09-29 23:00 | 13130.8542 | -0.048233 | 18.37 | 26.6 | 15.09 | 24.15 | 2.11 | 0.49 | 14.02 | 2.11
2018-09-30 | 12789.8042 | -0.048233 | 18.25 | 24.1 | 10 | 25.38 | 2 | 0.5 | 2.61 | 2.52
2018-09-30 01:00 | 14046.2191 | -0.048233 | 17.81 | 20.06 | 9.69 | 21.56 | 1.52 | 0.49 | 2 | 1.52
2018-09-30 02:00 | 12416.4542 | -0.048233 | 17.08 | 20.01 | 6.22 | 20.75 | 1.52 | 0.5 | 2 | 1.01
2018-09-30 03:00 | 12219.8042 | -0.048233 | 16.52 | 19.71 | 6.15 | 20.17 | 1.51 | 0.5 | 2 | 1
2018-09-30 04:00 | 12409.8042 | -0.048233 | 16.86 | 18.91 | 6.97 | 19.78 | 1.52 | 0.5 | 2 | 1.01
2018-09-30 05:00 | 13567.8542 | -0.048233 | 17.47 | 18.5 | 9.77 | 20.02 | 2.11 | 0.61 | 2.6 | 2.11
2018-09-30 06:00 | 15054.7097 | 4.0629 | 17.96 | 18.57 | 14 | 25.61 | 2 | 0.97 | 3.01 | 25
2018-09-30 07:00 | 17705.0142 | 227.004 | 18.58 | 18.58 | 14.11 | 25.69 | 2.11 | 0.97 | 2.75 | 2.11
2018-09-30 08:00 | 16324.4476 | 519.629 | 18.23 | 19.64 | 14.84 | 23.59 | 2.28 | 0.97 | 3.95 | 2.71
2018-09-30 09:00 | 19154.1158 | 802.56 | 39.13 | 39.13 | 15.03 | 23.34 | 3.5 | 0.99 | 3.98 | 3
2018-09-30 10:00 | 18911.2864 | 980.39 | 20.24 | 20.92 | 16.41 | 26.09 | 4.31 | 2.5 | 1 | 4.31
2018-09-30 11:00 | 16578.8395 | 1092.41 | 20.21 | 20.41 | 16.49 | 26.99 | 4.01 | 2.61 | 2.61 | 4.01
2018-09-30 12:00 | 16975.721 | 1129.18 | 21.97 | 21.97 | 15.02 | 30.51 | 6.21 | 3 | 0.26 | 4.57
2018-09-30 13:00 | 17177.2825 | 1073.35 | 27.24 | 27.24 | 14.15 | 35.47 | 7.06 | 5.5 | 2 | 6.08
2018-09-30 14:00 | 15381.791 | 888.359 | 28.47 | 28.47 | 14.12 | 38.98 | 18.41 | 15.21 | 2 | 18.21
2018-09-30 15:00 | 16071.1631 | 704.33 | 53.09 | 30.28 | 14.12 | 49.17 | 31.48 | 25 | 2 | 30.91
2018-09-30 16:00 | 14752.0977 | 427.031 | 77.25 | 31 | 14.69 | 48.28 | 36.07 | 0.97 | 1 | 34.73
2018-09-30 17:00 | 12876.5394 | 107.252 | 42.45 | 30.57 | 17.44 | 34.77 | 17.49 | 0.97 | 2.11 | 4.58
2018-09-30 18:00 | 12906.6542 | -0.048233 | 35.37 | 29.99 | 18.43 | 28.29 | 4.45 | 0.99 | 8 | 3
2018-09-30 19:00 | 12783.1542 | -0.048233 | 30.45 | 28.36 | 18.59 | 26.93 | 4.74 | 0.97 | 3.11 | 3
2018-09-30 20:00 | 13961.8191 | -0.048233 | 30.65 | 26.78 | 18.24 | 27.43 | 3.33 | 0.97 | 8.61 | 2.79
2018-09-30 21:00 | 12229.3042 | -0.048233 | 20.64 | 25.51 | 15 | 26.46 | 3.11 | 0.62 | 3.5 | 3
2018-09-30 22:00 | 13129.4241 | -0.048233 | 91.82 | 91.82 | 14.58 | 26.27 | 2.65 | 0.5 | 12 | 2.65
2018-09-30 23:00 | 12652.5641 | -0.048233 | 18.3 | 25.35 | 12.32 | 23.5 | 2.54 | 0.5 | 12 | 2.54
2018-10-01 | 12283.3141 | -0.048233 | 1309.9311 | 1042.32 | 10.11 | 26.63 | 3 | 0.5 | 3.01 | 2.8
2018-10-01 01:00 | 10953.4542 | -0.048233 | 16.97 | 26.85 | 8.3 | 22.32 | 2.36 | 0.5 | 2.5 | 1.11
2018-10-01 02:00 | 11980.5291 | -0.048233 | 16.27 | 26.92 | 5.08 | 22.47 | 2.11 | 0.97 | 2.5 | 1.11
2018-10-01 03:00 | 11926.7241 | -0.048233 | 15.14 | 20.36 | 4.32 | 20.53 | 2.11 | 0.97 | 2.5 | 1
2018-10-01 04:00 | 10861.3042 | -0.048233 | 15.04 | 19.16 | 4.47 | 20.18 | 2.12 | 0.97 | 2.5 | 1.11
2018-10-01 05:00 | 10887.9042 | -0.048233 | 15.44 | 19.01 | 4.49 | 20.57 | 2.61 | 0.97 | 14.11 | 2.61
2018-10-01 06:00 | 12464.4641 | 12.6579 | 16.24 | 17.68 | 9.18 | 21.47 | 2.21 | 12 | 8.56 | 25
2018-10-01 07:00 | 12817.6233 | 224.406 | 17.11 | 41.45 | 10.28 | 21.68 | 2.11 | 0.85 | 8.61 | 2
2018-10-01 08:00 | 11902.6222 | 560.076 | 55.49 | 55.49 | 10.55 | 22.02 | 2.95 | 0.85 | 3.5 | 2.61
2018-10-01 09:00 | 12385.0046 | 826.847 | 43.76 | 43.76 | 13.28 | 20.62 | 3 | 0.85 | 20 | 2.81
2018-10-01 10:00 | 13939.0767 | 968.395 | 75.24 | 75.24 | 13.25 | 22.61 | 4 | 2 | 2.11 | 2.85
2018-10-01 11:00 | 14184.4433 | 1137.97 | 76.13 | 76.13 | 13.4 | 26.99 | 5.92 | 2.5 | 1 | 3.73
2018-10-01 12:00 | 12890.151 | 1085.58 | 114.83 | 75.26 | 13.49 | 29.4 | 6.11 | 2.71 | 1 | 3.89
2018-10-01 13:00 | 14546.6776 | 1132.32 | 23.56 | 24.28 | 11.23 | 34.95 | 8.5 | 6.57 | 2.11 | 10.44
2018-10-01 14:00 | 13081.9588 | 956.483 | 34.8 | 29.68 | 12.28 | 43.8 | 20.29 | 14.41 | 1 | 18.26
2018-10-01 15:00 | 12642.5401 | 617.937 | 44.92 | 40.95 | 11.73 | 55.4 | 34.62 | 26 | 1.36 | 32
2018-10-01 16:00 | 13656.0677 | 451.14 | 68.92 | 68.92 | 13.22 | 46.79 | 30.01 | 18.85 | 2 | 27.25
2018-10-01 17:00 | 13243.7748 | 125.341 | 69.01 | 69.01 | 14.56 | 38.9 | 14.17 | 0.99 | 2.61 | 3.94
2018-10-01 18:00 | 11770.4542 | -0.048233 | 76.87 | 76.87 | 17.4 | 29.85 | 8 | 0.99 | 3.5 | 3.09
2018-10-01 19:00 | 13137.8641 | -0.048233 | 76.94 | 76.94 | 16.13 | 29.08 | 7.29 | 1.15 | 8.61 | 3.21
2018-10-01 20:00 | 11801.8042 | -0.048233 | 76.64 | 76.64 | 13.96 | 30.37 | 4.02 | 1.09 | 9.11 | 2.74
2018-10-01 21:00 | 11690.6542 | -0.048233 | 38.88 | 38.88 | 13.32 | 25.79 | 3.6 | 0.97 | 4 | 3
2018-10-01 22:00 | 12742.2391 | -0.048233 | 18.52 | 19.79 | 10.85 | 23.56 | 3 | 0.5 | 15 | 3
2018-10-01 23:00 | 12578.7141 | -0.048233 | 16.71 | 17.98 | 8.8 | 21.82 | 3.2 | 0.5 | 13.27 | 3
2018-10-02 | 11280.2542 | -0.048233 | 16.06 | 17.56 | 10.3 | 27.42 | 3 | 0.45 | 3.32 | 2.97
2018-10-02 01:00 | 11350.5542 | -0.048233 | 60.45 | 60.45 | 7.99 | 21.9 | 2.51 | 0.45 | 8 | 1.26
2018-10-02 02:00 | 11353.4042 | -0.048233 | 14.55 | 14.55 | 5.79 | 20.44 | 2.26 | 0.97 | 10.37 | 1
2018-10-02 03:00 | 11336.3042 | -0.048233 | 1.75 | 13.15 | 5.42 | 19.33 | 2.26 | 0.97 | 2.5 | 1
2018-10-02 04:00 | 11335.3542 | -0.048233 | 13.67 | 14.33 | 5.75 | 19.92 | 2.26 | 0.97 | 2.5 | 1
2018-10-02 05:00 | 11343.9042 | -0.048233 | 15.82 | 17.33 | 10.65 | 21.93 | 3 | 0.97 | 10.69 | 2.8
2018-10-02 06:00 | 12755.6611 | 9.674 | 16.13 | 18.96 | 8.78 | 27.04 | 2.95 | 0.85 | 9.71 | 25.09
2018-10-02 07:00 | 11416.7323 | 135.613 | 16.72 | 19.85 | 8.07 | 27.7 | 2.95 | 0.85 | 8.25 | 2.34
2018-10-02 08:00 | 12877.3068 | 486.978 | 17.03 | 20.16 | 11.24 | 27.18 | 3.11 | 0.85 | 4.27 | 2.11
2018-10-02 09:00 | 11984.4742 | 804.236 | 18.2 | 19.54 | 14.91 | 27.39 | 3.43 | 0.85 | 21.05 | 3.11
2018-10-02 10:00 | 13803.4618 | 1006.85 | 18.31 | 20.75 | 13.29 | 34.1 | 5 | 2 | 8.11 | 3
2018-10-02 11:00 | 12485.5175 | 1038.65 | 18.73 | 20.35 | 15.07 | 36.34 | 4.73 | 2.15 | 2.7 | 3.65
2018-10-02 12:00 | 14534.3657 | 1158.65 | 18.98 | 20.64 | 15 | 41.19 | 4.86 | 8.12 | 1 | 3.61
2018-10-02 13:00 | 13297.017 | 1123.86 | 19.9 | 21.18 | 15.04 | 49.44 | 6.39 | 11.49 | 2.11 | 2.06
2018-10-02 14:00 | 13130.976 | 923.08 | 21.7 | 22.34 | 14.95 | 58.03 | 17.77 | 1.39 | 1.06 | 13.32
2018-10-02 15:00 | 14620.7481 | 716.529 | 34.02 | 23.87 | 15 | 60.89 | 27.77 | 14.94 | 1.24 | 23.58
2018-10-02 16:00 | 14632.4459 | 442.617 | 37.39 | 28.2 | 14.99 | 62.29 | 26.86 | 13.78 | 9.54 | 22.86
2018-10-02 17:00 | 12969.0523 | 110.634 | 33 | 22.72 | 17.96 | 46.64 | 15.34 | 0.99 | 9.05 | 11.35
2018-10-02 18:00 | 14299.4191 | -0.048233 | 19.63 | 22.01 | 19.4 | 35.29 | 6.94 | 0.99 | 8 | 2.12
2018-10-02 19:00 | 14316.2991 | -0.048233 | 18.65 | 23.48 | 19.09 | 37.67 | 5.49 | 0.97 | 3.5 | 4.33
2018-10-02 20:00 | 12972.2042 | -0.048233 | 18.97 | 24.95 | 17.07 | 37.73 | 4.49 | 0.97 | 9.11 | 2.69
2018-10-02 21:00 | 14155.9391 | -0.048233 | 17.87 | 21.68 | 12.01 | 34.48 | 3.4 | 0.97 | 10.03 | 2.95
2018-10-02 22:00 | 12535.2042 | -0.048233 | 40.26 | 22.36 | 9.99 | 29.74 | 3.85 | 0.5 | 110.0234 | 3.5
2018-10-02 23:00 | 13808.8441 | -0.048233 | 18.13 | 21.17 | 8.32 | 27.13 | 3.38 | 0.5 | 15 | 3
2018-10-03 | 12310.0542 | -0.048233 | 15.92 | 19.93 | 12.54 | 27.68 | 3 | 0.45 | 10 | 3.11
2018-10-03 01:00 | 13516.6091 | -0.048233 | 11.25 | 18.91 | 10.29 | 26.24 | 3 | 0.45 | 7.87 | 1
2018-10-03 02:00 | 13511.3341 | -0.048233 | 0 | 18.43 | 6.03 | 23.95 | 3 | 0.97 | 8.98 | 1
2018-10-03 03:00 | 13507.1141 | -0.048233 | 12.93 | 18.39 | 6.01 | 23.99 | 3 | 0.97 | 2.5 | 1
2018-10-03 04:00 | 12419.3042 | -0.048233 | 10.22 | 18.58 | 6.09 | 24.73 | 3 | 0.97 | 2.5 | 1.01
2018-10-03 05:00 | 14948.2441 | -0.048233 | 15.01 | 19.92 | 11.5 | 24.12 | 3 | 0.97 | 14.5 | 2.91
2018-10-03 06:00 | 17366.1679 | 9.8226 | 15.62 | 21.4 | 15.08 | 31.06 | 2.76 | 0.85 | 8.59 | 26.91
2018-10-03 07:00 | 18740.4303 | 230.441 | 16.79 | 25.18 | 13.25 | 31.15 | 2.51 | 0.85 | 4.15 | 2.11
2018-10-03 08:00 | 17236.3906 | 547.569 | 17 | 20.93 | 17.11 | 31.5 | 3.11 | 0.85 | 3.11 | 2.61
2018-10-03 09:00 | 21103.6978 | 830.505 | 17.83 | 21.59 | 18.12 | 32.15 | 4.89 | 0.85 | 12.64 | 3
2018-10-03 10:00 | 19770.089 | 1002.62 | 275.7157 | 231.39 | 19.34 | 36 | 5.2 | 1.79 | 2.91 | 2.61
2018-10-03 11:00 | 19329.8305 | 1063.19 | 18.07 | 31.28 | 19.58 | 40.3 | 5.13 | 2 | 2.61 | 3.76
2018-10-03 12:00 | 20322.989 | 1147.62 | 270.6357 | 24.69 | 18.01 | 39.36 | 5.95 | 2.61 | 2 | 5.07
2018-10-03 13:00 | 21463.1173 | 862.187 | 18.91 | 29.04 | 18.01 | 52.43 | 7.45 | 10.5 | 2.11 | 5.39
2018-10-03 14:00 | 17700.5529 | 919.161 | 37.34 | 28.94 | 18 | 57.05 | 22.43 | 1.41 | 1.5 | 15.57
2018-10-03 15:00 | 18613.5 | 730.128 | 115.27 | 30.15 | 17.46 | 49.89 | 25.44 | 15.73 | 2 | 18.19
2018-10-03 16:00 | 17788.5322 | 455.168 | 188.87 | 40.7 | 19.55 | 43.06 | 26.74 | 13.92 | 10 | 20.74
2018-10-03 17:00 | 17123.7831 | 109.074 | 117.79 | 45.62 | 20.51 | 32.65 | 13.61 | 0.99 | 10 | 3.04
2018-10-03 18:00 | 15099.2542 | -0.048233 | 36.76 | 29.67 | 20.65 | 30.76 | 7.43 | 0.99 | 10 | 2.2
2018-10-03 19:00 | 15254.1042 | -0.048233 | 36.77 | 36.77 | 20.68 | 34.44 | 6.56 | 1.27 | 8.11 | 3
2018-10-03 20:00 | 16456.8941 | -0.048233 | 17.76 | 27.94 | 20.32 | 32.95 | 5.21 | 0.97 | 8.61 | 1.93
2018-10-03 21:00 | 14488.4042 | -0.048233 | 52.59 | 52.59 | 13.7 | 32.87 | 3.85 | 0.97 | 20 | 3
2018-10-03 22:00 | 14013.4042 | -0.048233 | 19.44 | 20.03 | 12.71 | 27.65 | 4.4 | 0.5 | 36.61 | 4.2
2018-10-03 23:00 | 15226.7641 | -0.048233 | 17.93 | 18.91 | 9.33 | 27.33 | 4.4 | 0.5 | 20 | 3.55
2018-10-04 | 13583.0542 | -0.048233 | 16.9 | 18.95 | 14.35 | 25.08 | 3 | 0.5 | 10 | 2.73
2018-10-04 01:00 | 13462.4042 | -0.048233 | 14.75 | 18.1 | 12.62 | 21.54 | 2.95 | 0.5 | 10 | 1
2018-10-04 02:00 | 13352.2042 | -0.048233 | 7.64 | 18.04 | 10.09 | 20.75 | 3 | 0.97 | 10.31 | 1
2018-10-04 03:00 | 14831.1391 | -0.048233 | 14.03 | 17.94 | 9.28 | 20.56 | 2.95 | 0.97 | 10 | 1
2018-10-04 04:00 | 13584.9542 | -0.048233 | 15.47 | 18.84 | 10.31 | 21.18 | 3 | 0.97 | 2 | 1.11
2018-10-04 05:00 | 16463.2241 | -0.048233 | 16.99 | 19.16 | 13.26 | 21.22 | 3 | 0.97 | 57.6962 | 3.11
2018-10-04 06:00 | 18667.6096 | 11.4167 | 17.58 | 22.52 | 12.1 | 27.59 | 2.26 | 0.85 | 10 | 50
2018-10-04 07:00 | 18001.7656 | 170.227 | 17.12 | 29.79 | 14.62 | 26.65 | 2.7 | 0.85 | 3.5 | 2.5
2018-10-04 08:00 | 18256.644 | 510.52 | 17.67 | 24.17 | 16.56 | 27.95 | 3.4 | 0.85 | 2.67 | 3
2018-10-04 09:00 | 19636.8619 | 779.381 | 48.23 | 48.23 | 19.09 | 30.3 | 4 | 0.85 | 14.57 | 4.98
2018-10-04 10:00 | 20046.4155 | 1015.49 | 18.18 | 24.01 | 19.08 | 32.54 | 4 | 1 | 2.89 | 4.23
2018-10-04 11:00 | 21711.593 | 857.709 | 50.23 | 24.07 | 18.74 | 38.54 | 6.82 | 2 | 2.61 | 4.44
2018-10-04 12:00 | 22347.6957 | 1158.65 | 164.29 | 25.99 | 18.88 | 43.55 | 6.44 | 15.13 | 2.11 | 5.24
2018-10-04 13:00 | 22684.2408 | 1158.65 | 39.33 | 28.24 | 19.16 | 58.11 | 20.84 | 20.84 | 2.11 | 7.13
2018-10-04 14:00 | 18080.0466 | 917.628 | 123.46 | 37.32 | 18.82 | 74.02 | 32.64 | 14.41 | 2.11 | 18.97
2018-10-04 15:00 | 19463.8332 | 786.131 | 340.5757 | 296.25 | 18.72 | 92 | 43.56 | 21.7 | 1 | 21.71
2018-10-04 16:00 | 16514.5084 | 450.693 | 355.6457 | 311.32 | 18.55 | 76.15 | 36.79 | 16.9 | 10.19 | 28.07
2018-10-04 17:00 | 15831.3063 | 117.533 | 78.81 | 78.81 | 19 | 41.42 | 13.05 | 8.12 | 10 | 6.18
2018-10-04 18:00 | 17135.2591 | -0.048233 | 45.97 | 36.64 | 21.71 | 33.47 | 8.5 | 1.09 | 10.5 | 3.66
2018-10-04 19:00 | 17243.9241 | -0.048233 | 63.05 | 42.81 | 21.7 | 32.69 | 8.35 | 1.3 | 8.11 | 3.16
2018-10-04 20:00 | 16963.2941 | -0.048233 | 30.49 | 28.96 | 18.27 | 32.08 | 5.31 | 0.99 | 10.03 | 1.42
2018-10-04 21:00 | 16776.5591 | -0.048233 | 20.06 | 22.08 | 16.79 | 29.65 | 4.38 | 1.19 | 20 | 4.18
2018-10-04 22:00 | 16120.3491 | -0.048233 | 19.59 | 19.59 | 15.21 | 27.2 | 5.36 | 0.5 | 99.3534 | 11.36
2018-10-04 23:00 | 15544.3191 | -0.048233 | 18.54 | 19.05 | 13.46 | 25.44 | 6.99 | 0.5 | 36.02 | 10.21
2018-10-05 | 13770.2042 | -0.048233 | 18.8 | 18.8 | 13.12 | 24.28 | 2.95 | 0.45 | 10 | 2.61
2018-10-05 01:00 | 15140.2541 | -0.048233 | 17.56 | 17.56 | 11.6 | 22.33 | 2.95 | 0.45 | 2 | 1
2018-10-05 02:00 | 15019.9841 | -0.048233 | 17.39 | 17.39 | 11.76 | 21.27 | 2.81 | 0.97 | 2 | 1
2018-10-05 03:00 | 14966.1791 | -0.048233 | 16.43 | 16.43 | 11.06 | 19.87 | 2.81 | 0.97 | 2 | 1
2018-10-05 04:00 | 13706.5542 | -0.048233 | 16.15 | 16.15 | 11.07 | 19.81 | 2.81 | 0.97 | 2 | 1.11
2018-10-05 05:00 | 14743.0042 | -0.048233 | 16.87 | 16.87 | 13.02 | 21.11 | 2.95 | 0.97 | 29.57 | 26.3
2018-10-05 06:00 | 18844.2986 | 8.8944 | 18.48 | 18.48 | 17.11 | 26.99 | 4.71 | 0.85 | 3.5 | 23.21
2018-10-05 07:00 | 19824.7382 | 160.221 | 18.96 | 19.03 | 17.69 | 29.21 | 3.81 | 0.85 | 3.5 | 2.61
2018-10-05 08:00 | 18649.3255 | 544.869 | 18.24 | 19.16 | 17.46 | 25.65 | 3.45 | 0.85 | 2 | 3
2018-10-05 09:00 | 22794.7024 | 773.353 | 46.2 | 20.13 | 18.14 | 28.48 | 5.71 | 0.85 | 9 | 5.51
2018-10-05 10:00 | 22117.1519 | 976.125 | 19.23 | 20.92 | 18.32 | 30.93 | 6.49 | 2 | 2.61 | 5.37
2018-10-05 11:00 | 21680.5454 | 1096.28 | 18.94 | 23.05 | 19.27 | 32.76 | 5.5 | 2 | 2.21 | 4.58
2018-10-05 12:00 | 22144.7982 | 1024.33 | 30.04 | 29.32 | 18.18 | 36.37 | 5.17 | 2.5 | 2 | 4.92
2018-10-05 13:00 | 20170.6755 | 1084.29 | 46.59 | 32.06 | 18.46 | 49.82 | 21.88 | 17.97 | 2 | 16.83
2018-10-05 14:00 | 18485.3574 | 921.271 | 115.21 | 29.64 | 18.76 | 64.62 | 35.93 | 10 | 2.11 | 25.12
2018-10-05 15:00 | 19345.6447 | 569.104 | 45.73 | 31.64 | 18.71 | 86.15 | 53.9 | 16.11 | 2 | 42.38
2018-10-05 16:00 | 18939.5594 | 367.189 | 120.42 | 33.13 | 19.62 | 66.56 | 80.1941 | 20.22 | 2 | 42.94
2018-10-05 17:00 | 16470.7257 | 95.606 | 41.09 | 38 | 22.85 | 41.67 | 24.85 | 10 | 2.11 | 17.87
2018-10-05 18:00 | 17693.3541 | -0.048233 | 31.55 | 30.45 | 23.21 | 31.23 | 12.56 | 2 | 10 | 2.84
2018-10-05 19:00 | 15912.4542 | -0.048233 | 31.33 | 31.33 | 31 | 33.8 | 7.82 | 1 | 3.43 | 2.11
2018-10-05 20:00 | 17506.6191 | -0.048233 | 30.54 | 30.54 | 20.26 | 33.53 | 7.49 | 1.25 | 14.47 | 1.78
2018-10-05 21:00 | 17298.7841 | -0.048233 | 18.77 | 28.64 | 16.58 | 32.57 | 6.55 | 1.35 | 12.43 | 3.92
2018-10-05 22:00 | 14903.5542 | -0.048233 | 18.69 | 20.12 | 14.22 | 25.89 | 6.86 | 0.5 | 35.25 | 10.76
2018-10-05 23:00 | 14572.9542 | -0.048233 | 16.77 | 19.22 | 12.95 | 26.45 | 8 | 0.5 | 14.11 | 11.9
2018-10-06 | 15942.0541 | -0.048233 | 18.43 | 18.76 | 16.91 | 21.59 | 2.95 | 0.45 | 2.5 | 2.2
2018-10-06 01:00 | 14109.3542 | -0.048233 | 16.72 | 16.72 | 15.91 | 19.11 | 2.95 | 0.45 | 2.11 | 1
2018-10-06 02:00 | 13955.4542 | -0.048233 | 16.09 | 17.75 | 13.25 | 18.62 | 2.95 | 0.99 | 2 | 1
2018-10-06 03:00 | 13942.1542 | -0.048233 | 15.26 | 17.16 | 13.03 | 18.41 | 2.95 | 0.99 | 2.11 | 1
2018-10-06 04:00 | 15784.8591 | -0.048233 | 15.28 | 16.48 | 11.6 | 18.74 | 2.95 | 0.99 | 2.11 | 1.26
2018-10-06 05:00 | 17088.8391 | -0.048233 | 16.35 | 17.19 | 17.02 | 19.96 | 2.61 | 1 | 23.08 | 2.7
2018-10-06 06:00 | 19286.5986 | 7.1361 | 16.05 | 19.34 | 19.81 | 26.04 | 3.3 | 0.85 | 3.44 | 12
2018-10-06 07:00 | 20551.9423 | 191.514 | 17.48 | 19.92 | 20.15 | 26.62 | 2.81 | 0.85 | 3.5 | 2.61
2018-10-06 08:00 | 18703.4603 | 521.853 | 15.26 | 19.26 | 18.52 | 25.37 | 3.3 | 0.95 | 2.11 | 3.1
2018-10-06 09:00 | 22394.6105 | 793.119 | 16.54 | 20.17 | 19.9 | 28.74 | 7 | 0.95 | 16 | 3.61
2018-10-06 10:00 | 20620.187 | 1039.46 | 17.57 | 20.54 | 19.86 | 31.85 | 6.03 | 2.5 | 2.61 | 4.58
2018-10-06 11:00 | 22215.0928 | 1072.96 | 21.23 | 21.23 | 19.87 | 32.78 | 5.41 | 2.5 | 2.61 | 5.21
2018-10-06 12:00 | 23030.6078 | 1149.96 | 32.65 | 28.22 | 20.69 | 35.1 | 18.93 | 5.59 | 2 | 15.78
2018-10-06 13:00 | 20796.6685 | 1099.23 | 49.83 | 24.69 | 21.01 | 42.98 | 29.1 | 17 | 1 | 24.32
2018-10-06 14:00 | 19332.3888 | 963.883 | 40.39 | 27.32 | 20.44 | 56.56 | 36.97 | 12.35 | 1 | 24.03
2018-10-06 15:00 | 19912.9731 | 705.856 | 50.67 | 29.81 | 21.1 | 73.28 | 89.6641 | 25 | 2.11 | 50.17
2018-10-06 16:00 | 17000.6917 | 374.465 | 41.71 | 29.41 | 21.16 | 54.19 | 96.4541 | 53.3073 | 2.61 | 82.2262
2018-10-06 17:00 | 16345.8819 | 82.1915 | 36.78 | 28.33 | 21.46 | 38.12 | 23.94 | 15.38 | 2.11 | 20
2018-10-06 18:00 | 15821.2542 | -0.048233 | 28.49 | 25.35 | 22.21 | 32.11 | 17.63 | 9.73 | 3.5 | 13.26
2018-10-06 19:00 | 17902.2441 | -0.048233 | 40.36 | 40.36 | 22.24 | 31.61 | 19.97 | 0.97 | 2.11 | 13.71
2018-10-06 20:00 | 17798.8541 | -0.048233 | 20.74 | 20.74 | 19.85 | 29.55 | 6.14 | 0.97 | 3.5 | 3.83
2018-10-06 21:00 | 17464.4191 | -0.048233 | 19.17 | 19.17 | 19.01 | 29.31 | 5 | 0.97 | 8.61 | 4.11
2018-10-06 22:00 | 15165.7542 | -0.048233 | 18.02 | 19.88 | 16.54 | 26.98 | 4.35 | 0.61 | 14.61 | 4.15
2018-10-06 23:00 | 16390.4291 | -0.048233 | 16.86 | 19.2 | 14.84 | 24.52 | 5 | 0.5 | 11.87 | 4.8
2018-10-07 | 16145.6691 | -0.048233 | 15.02 | 18.2 | 14 | 25.07 | 2.88 | 0.5 | 8.59 | 2.2
2018-10-07 01:00 | 14415.2542 | -0.048233 | 9.07 | 17.81 | 11.76 | 21.82 | 2.75 | 0.5 | 2.5 | 1
2018-10-07 02:00 | 15894.5791 | -0.048233 | 13.33 | 18 | 10.96 | 19.79 | 2.75 | 0.97 | 12.04 | 1
2018-10-07 03:00 | 14220.5042 | -0.048233 | 9.95 | 17.9 | 9.75 | 19.67 | 2.75 | 0.97 | 2.5 | 1
2018-10-07 04:00 | 16079.2041 | -0.048233 | 13.5 | 17.99 | 12.32 | 19.16 | 2.9 | 0.97 | 2.5 | 1.26
2018-10-07 05:00 | 17288.2341 | -0.048233 | 15.05 | 18.02 | 15.71 | 19.69 | 3 | 0.97 | 10 | 2.61
2018-10-07 06:00 | 19211.5314 | 9.9824 | 17.17 | 17.39 | 18.63 | 20.28 | 2.87 | 0.85 | 8.61 | 3.25
2018-10-07 07:00 | 20433.0575 | 210.827 | 17.84 | 17.84 | 19.45 | 22.41 | 2.5 | 0.85 | 10.03 | 2.5
2018-10-07 08:00 | 18894.8701 | 575.337 | 17.77 | 18.3 | 19.3 | 21.23 | 2.9 | 0.85 | 3.5 | 2.9
2018-10-07 09:00 | 21781.2473 | 514.732 | 18.39 | 19.14 | 20.03 | 23.13 | 3.75 | 0.85 | 18.2 | 3.55
2018-10-07 10:00 | 19265.0253 | 712.974 | 19.69 | 20.49 | 19.97 | 26.95 | 3.5 | 1.21 | 3.5 | 3.5
2018-10-07 11:00 | 20691.6823 | 751.969 | 20.11 | 22.14 | 19.35 | 28.56 | 4.38 | 2.5 | 2.61 | 4.38
2018-10-07 12:00 | 21051.0174 | 829.571 | 44.98 | 27.83 | 19.51 | 32 | 5.77 | 10 | 1 | 5.57
2018-10-07 13:00 | 20949.979 | 1039.8 | 42.18 | 28.75 | 19.5 | 38.46 | 15 | 10 | 1.48 | 12.85
2018-10-07 14:00 | 17431.8787 | 819.346 | 33.13 | 29.67 | 20.8 | 51.05 | 20.96 | 12.67 | 1.64 | 16.45
2018-10-07 15:00 | 16384.6652 | 298.016 | 33.73 | 33.73 | 20.85 | 73.64 | 41.94 | 28.75 | 2 | 35
2018-10-07 16:00 | 17318.4506 | 233.593 | 42.5 | 42.5 | 22.21 | 75.73 | 44.03 | 30 | 2 | 35
2018-10-07 17:00 | 16896.9952 | 79.1092 | 34.26 | 34.26 | 20.01 | 44.9 | 19.41 | 14.37 | 2.21 | 16.42
2018-10-07 18:00 | 16596.1541 | -0.048233 | 310.2157 | 265.89 | 22.65 | 34.14 | 7 | 9.09 | 8.11 | 4
2018-10-07 19:00 | 16609.8691 | -0.048233 | 21.93 | 29.71 | 22.95 | 32.68 | 8 | 1.25 | 3.5 | 4.98
2018-10-07 20:00 | 14496.0042 | -0.048233 | 21.15 | 29.46 | 18.26 | 32.3 | 5.65 | 1.15 | 9.11 | 4.02
2018-10-07 21:00 | 15840.7741 | -0.048233 | 19.03 | 27.24 | 17.62 | 31.23 | 3.88 | 1.16 | 8.61 | 3
2018-10-07 22:00 | 15240.4791 | -0.048233 | 17.9 | 22.83 | 15.8 | 25.84 | 3.25 | 0.5 | 10.43 | 3.25
2018-10-07 23:00 | 14951.4091 | -0.048233 | 16.39 | 21.43 | 13.95 | 26.29 | 3.75 | 0.5 | 10.53 | 3.75
2018-10-08 | 14554.7291 | -0.048233 | 17.9 | 21.01 | 11.52 | 24.92 | 2.5 | 0.5 | 2.5 | 2.5
2018-10-08 01:00 | 12603.6042 | -0.048233 | 16.76 | 20.3 | 11.41 | 20.74 | 2.26 | 0.5 | 2.05 | 1
2018-10-08 02:00 | 13477.5741 | -0.048233 | 17 | 18.44 | 9.78 | 19.2 | 2.25 | 0.97 | 2 | 1
2018-10-08 03:00 | 13146.3041 | -0.048233 | 16.54 | 16.54 | 8.74 | 18.53 | 2.25 | 0.97 | 2 | 0.95
2018-10-08 04:00 | 12985.9441 | -0.048233 | 15.86 | 15.86 | 9.1 | 17.91 | 2.25 | 0.97 | 2 | 1.02
2018-10-08 05:00 | 12853.0141 | -0.048233 | 16.09 | 16.09 | 11.01 | 18.59 | 2.61 | 0.97 | 11.68 | 2.61
2018-10-08 06:00 | 11593.2358 | 4.4061 | 16.07 | 16.07 | 11.43 | 19.9 | 2.5 | 0.85 | 9.11 | 3.5
2018-10-08 07:00 | 12863.2092 | 53.6154 | 12.2 | 12.2 | 13.85 | 20.52 | 2.5 | 0.85 | 8 | 2.31
2018-10-08 08:00 | 12770.4617 | 132.703 | 15.5 | 15.5 | 15.79 | 21.45 | 2.25 | 0.85 | 3.72 | 2.25
2018-10-08 09:00 | 11659.6977 | 170.366 | 16.75 | 16.75 | 15.97 | 22.1 | 3.5 | 0.85 | 27.76 | 3.5
2018-10-08 10:00 | 13108.9869 | 214.58 | 19.45 | 19.45 | 15.23 | 28.45 | 2.61 | 1.85 | 3.11 | 2.61
2018-10-08 11:00 | 11976.726 | 241.08 | 19.96 | 22.35 | 16.05 | 27.72 | 5.39 | 2.5 | 3.11 | 4.96
2018-10-08 12:00 | 12269.7459 | 246.522 | 21.2 | 23.24 | 15.7 | 31.37 | 6.34 | 9.82 | 1 | 6.13
2018-10-08 13:00 | 12371.5232 | 234.656 | 22.28 | 26.16 | 14.58 | 36.92 | 15 | 2.5 | 1 | 12.75
2018-10-08 14:00 | 13932.0114 | 198.698 | 33.6 | 33.6 | 14.05 | 53.75 | 21.3 | 10.64 | 1.36 | 14.54
2018-10-08 15:00 | 14103.3022 | 146.059 | 191.51 | 191.51 | 11.7 | 74.47 | 40.32 | 24.24 | 1.53 | 33.15
2018-10-08 16:00 | 14151.4419 | 79.689 | 57.27 | 57.27 | 14 | 73.36 | 43.46 | 28.95 | 1.77 | 34.22
2018-10-08 17:00 | 14220.7827 | 50.4149 | 41.36 | 41.36 | 30.39 | 51.8 | 27.5 | 15 | 2.11 | 19.73
2018-10-08 18:00 | 12736.6042 | -0.048233 | 37.29 | 37.29 | 31.6 | 36.25 | 14.07 | 1 | 8.11 | 6.85
2018-10-08 19:00 | 12751.8042 | -0.048233 | 30.14 | 30.14 | 32.67 | 31.63 | 8.31 | 0.97 | 3.5 | 2.75
2018-10-08 20:00 | 14125.3441 | -0.048233 | 23.44 | 24.87 | 15.57 | 31.49 | 6.29 | 0.97 | 10 | 2.6
2018-10-08 21:00 | 12598.8542 | -0.048233 | 21.54 | 24.14 | 12.95 | 26.65 | 3.8 | 0.97 | 28.75 | 2.95
2018-10-08 22:00 | 13740.2691 | -0.048233 | 21.37 | 22.04 | 14.41 | 25.69 | 4 | 0.5 | 30 | 4
2018-10-08 23:00 | 12076.3542 | -0.048233 | 19.12 | 22.76 | 11.67 | 27.11 | 3.75 | 0.5 | 12 | 3.55
2018-10-09 | 12017.4542 | -0.048233 | 18.31 | 18.63 | 4.93 | 19.71 | 2.5 | 0.5 | 21.73 | 22.23
2018-10-09 01:00 | 13242.3091 | -0.048233 | 17.74 | 18.26 | 4.69 | 17.65 | 2.2 | 0.5 | 3 | 1
2018-10-09 02:00 | 12993.3291 | -0.048233 | 17.73 | 17.73 | 4.08 | 15.54 | 2.11 | 0.97 | 9.84 | 1
2018-10-09 03:00 | 12855.1241 | -0.048233 | 16.88 | 16.88 | 3.95 | 17.35 | 2.11 | 0.97 | 2.5 | 1
2018-10-09 04:00 | 12855.1241 | -0.048233 | 16.51 | 16.51 | 4.06 | 17.9 | 2 | 0.97 | 2.61 | 1.8
2018-10-09 05:00 | 11692.5542 | -0.048233 | 17.16 | 17.16 | 4.02 | 20.12 | 2.25 | 0.97 | 32.21 | 30
2018-10-09 06:00 | 11703.8945 | 6.8889 | 13.67 | 13.67 | 4.05 | 27.99 | 2.26 | 0.97 | 9.67 | 32
2018-10-09 07:00 | 12834.0212 | 119.949 | 18.15 | 18.36 | 4.77 | 26.1 | 2.11 | 0.97 | 3.11 | 2.11
2018-10-09 08:00 | 12965.8983 | 264.951 | 17.94 | 18.51 | 8.88 | 25.64 | 2.25 | 0.97 | 1 | 2.25
2018-10-09 09:00 | 13377.2945 | 410.9 | 18.35 | 19.01 | 11.36 | 32.13 | 3.5 | 0.97 | 12 | 3.5
2018-10-09 10:00 | 13782.1423 | 806.642 | 19.09 | 25.16 | 12.64 | 36.15 | 3.94 | 2 | 3.11 | 3.94
2018-10-09 11:00 | 12717.1275 | 981.45 | 19.4 | 23.78 | 13.11 | 44.36 | 5.36 | 10 | 2.11 | 11.71
2018-10-09 12:00 | 12702.3607 | 924.906 | 19.56 | 29.54 | 12.79 | 52.38 | 16.21 | 11.37 | 1.18 | 13.29
2018-10-09 13:00 | 13741.125 | 571.763 | 106.25 | 106.25 | 12.57 | 80.85 | 34.24 | 20.68 | 2.61 | 20.68
2018-10-09 14:00 | 14051.161 | 735.636 | 411.8357 | 367.51 | 12.52 | 106.81 | 80.8141 | 23.46 | 2.11 | 32.85
2018-10-09 15:00 | 13723.0908 | 313.669 | 824.4911 | 556.88 | 12.01 | 129.79 | 93.5541 | 25.95 | 2 | 31.61
2018-10-09 16:00 | 13970.5938 | 335.269 | 763.2811 | 495.67 | 30.59 | 125.86 | 91.6041 | 27.15 | 3.5 | 32.53
2018-10-09 17:00 | 12208.2815 | 53.8226 | 128.97 | 128.97 | 34.32 | 81.08 | 36.47 | 10.98 | 3.2 | 19.5
2018-10-09 18:00 | 13248.6391 | -0.048233 | 21.05 | 27.81 | 40.65 | 48.83 | 16.89 | 0.99 | 10.03 | 10.36
2018-10-09 19:00 | 11647.9042 | -0.048233 | 20.53 | 27.92 | 37.51 | 46.86 | 5.61 | 0.97 | 1 | 5.61
2018-10-09 20:00 | 12896.2691 | -0.048233 | 19.71 | 24.1 | 30.55 | 38.68 | 4.26 | 0.97 | 25 | 3.16
2018-10-09 21:00 | 12904.7091 | -0.048233 | 19.47 | 23.25 | 12.07 | 33.44 | 3.01 | 0.97 | 30.17 | 3.01
2018-10-09 22:00 | 12764.3941 | -0.048233 | 19.6 | 25.51 | 11.24 | 29.38 | 3.5 | 0.5 | 109.7434 | 3.5
2018-10-09 23:00 | 12690.5441 | -0.048233 | 17.54 | 23.72 | 6.72 | 26.43 | 3.01 | 0.5 | 57.1062 | 22
2018-10-10 | 12433.1241 | -0.048233 | 16.68 | 19.26 | 3.6 | 22.45 | 2.61 | 0.5 | 9.63 | 2.61
2018-10-10 01:00 | 12157.7691 | -0.048233 | 10.95 | 18.91 | 3.15 | 20.48 | 2.25 | 0.5 | 9.74 | 1.26
2018-10-10 02:00 | 12057.5441 | -0.048233 | 0 | 18.64 | 3.11 | 19.11 | 2.25 | 0.97 | 8.84 | 1.11
2018-10-10 03:00 | 10885.0542 | -0.048233 | 2.45 | 17.93 | 3.1 | 18.59 | 2.25 | 0.97 | 8 | 1
2018-10-10 04:00 | 10819.5042 | -0.048233 | 11.12 | 18.3 | 3.07 | 18.59 | 2.11 | 0.97 | 2.61 | 1.11
2018-10-10 05:00 | 10958.2042 | -0.048233 | 12.98 | 18.94 | 4.28 | 19.98 | 2.26 | 0.97 | 11.91 | 2.11
2018-10-10 06:00 | 11136.0646 | 9.1733 | 17.01 | 21.05 | 12.55 | 29.29 | 2.25 | 0.96 | 8.61 | 33.33
2018-10-10 07:00 | 11102.3688 | 229.704 | 17.5 | 23.12 | 12.59 | 29.38 | 2 | 0.95 | 8.25 | 2
2018-10-10 08:00 | 11311.5198 | 600.863 | 17.01 | 21.24 | 12.57 | 25.32 | 2.11 | 0.95 | 4 | 2.11
2018-10-10 09:00 | 12777.623 | 810.491 | 17.94 | 20.71 | 13.28 | 28.23 | 3.25 | 0.95 | 12.76 | 3.25
2018-10-10 10:00 | 12974.7909 | 1009.38 | 18.47 | 19.94 | 12.52 | 32.15 | 2.5 | 1.82 | 2.16 | 2.5
2018-10-10 11:00 | 11730.2675 | 1158.65 | 47.38 | 18.71 | 13.34 | 32.05 | 3.62 | 1.62 | 1 | 3.47
2018-10-10 12:00 | 11515.2017 | 723.265 | 17.06 | 17.06 | 12.17 | 32.75 | 4.62 | 1.62 | 0.51 | 4.49
2018-10-10 13:00 | 11907.5755 | 1044.29 | 17.97 | 17.97 | 12.71 | 37.64 | 18.68 | 10 | 3.08 | 16.18
2018-10-10 14:00 | 11894.5462 | 817.575 | 18.44 | 18.44 | 12.51 | 42.4 | 20.24 | 10.74 | 2.61 | 16.49
2018-10-10 15:00 | 12931.1065 | 514.973 | 18.57 | 18.57 | 12.12 | 37.91 | 37.98 | 14.22 | 1.81 | 28.88
2018-10-10 16:00 | 11485.7736 | 253.288 | 33.44 | 19.9 | 37.9 | 33.82 | 35.41 | 24.06 | 2 | 30.61
2018-10-10 17:00 | 11413.2173 | 78.9129 | 35.58 | 19.6 | 39.02 | 32.74 | 16.36 | 10.62 | 3.5 | 12.61
2018-10-10 18:00 | 11475.9542 | -0.048233 | 21.04 | 21.04 | 39.68 | 33.27 | 8.01 | 0.99 | 8.24 | 8.01
2018-10-10 19:00 | 13387.8991 | -0.048233 | 21.76 | 23.13 | 38.4 | 36.92 | 14.5 | 0.99 | 1 | 5.66
2018-10-10 20:00 | 12083.0042 | -0.048233 | 18.6 | 22.99 | 31.49 | 31.38 | 4.01 | 1 | 25 | 2.61
2018-10-10 21:00 | 11943.3542 | -0.048233 | 18.55 | 20.67 | 12.59 | 30.07 | 2.67 | 0.97 | 26 | 2.67
2018-10-10 22:00 | 13173.7341 | -0.048233 | 18.17 | 19.21 | 11.29 | 28.86 | 3.01 | 0.5 | 109.7434 | 3.01
2018-10-10 23:00 | 11533.9042 | -0.048233 | 16.27 | 18.8 | 8.89 | 26.71 | 3 | 0.5 | 30 | 22
2018-10-11 | 12638.8491 | -0.048233 | 16.55 | 18.26 | 8.93 | 19.94 | 3 | 0.5 | 9.93 | 2.8
2018-10-11 01:00 | 11220.4042 | -0.048233 | 14.47 | 17.67 | 9.17 | 19.41 | 3 | 0.5 | 12.72 | 1.01
2018-10-11 02:00 | 11086.4542 | -0.048233 | 5.65 | 17.45 | 9.17 | 18.78 | 3 | 0.97 | 13.06 | 1
2018-10-11 03:00 | 11000.0042 | -0.048233 | -0.44 | 17.16 | 9.09 | 18.5 | 3 | 0.97 | 9.66 | 0.95
2018-10-11 04:00 | 12459.4991 | -0.048233 | -0.16 | 17.25 | 9.08 | 18.5 | 3 | 0.97 | 8.72 | 1.26
2018-10-11 05:00 | 13848.9341 | -0.048233 | 1.51 | 17.54 | 13.58 | 19.54 | 5.75 | 0.97 | 28 | 16
2018-10-11 06:00 | 15079.3834 | 10.0352 | 8.74 | 18.49 | 16.82 | 24.6 | 2.11 | 0.85 | 9.99 | 50.02
2018-10-11 07:00 | 18125.0076 | 264.102 | 13.12 | 19.9 | 16.37 | 24.15 | 2.11 | 0.85 | 8.56 | 2.11
2018-10-11 08:00 | 18630.5425 | 646.282 | -7.02 | 18.79 | 18.88 | 25.37 | 3.11 | 0.85 | 3.5 | 3.11
2018-10-11 09:00 | 19884.5313 | 944.897 | 16.36 | 18.37 | 16.67 | 27.11 | 3 | 0.85 | 14.2 | 3
2018-10-11 10:00 | 20048.5975 | 1154.41 | 17.19 | 18.78 | 18.08 | 27.01 | 3 | 1.73 | 2.61 | 3
2018-10-11 11:00 | 19516.0757 | 1158.65 | 17.95 | 18.78 | 17.77 | 28.94 | 3.46 | 1.32 | 2.22 | 3.46
2018-10-11 12:00 | 20556.3057 | 1158.65 | 18.82 | 18.82 | 16.51 | 29.65 | 4.42 | 8.48 | 1 | 4.42
2018-10-11 13:00 | 17998.3675 | 1158.65 | 19.02 | 19.02 | 16.51 | 34.1 | 18.51 | 18.3 | 2.11 | 16.58
2018-10-11 14:00 | 18424.5411 | 1031.02 | 19.46 | 19.46 | 16.51 | 37.06 | 17.24 | 11.23 | 1 | 12.39
2018-10-11 15:00 | 17457.0185 | 786.937 | 19.91 | 19.91 | 16.5 | 43.85 | 25.44 | 16.51 | 1.48 | 20.88
2018-10-11 16:00 | 17265.44 | 455.346 | 34.42 | 21.93 | 18.49 | 39.61 | 33.07 | 26.39 | 2 | 32.87
2018-10-11 17:00 | 15076.5816 | 98.0859 | 19.71 | 19.71 | 20.06 | 32.2 | 19.71 | 17.96 | 3.5 | 17.96
2018-10-11 18:00 | 16398.8691 | -0.048233 | 19.82 | 19.82 | 21.87 | 27.74 | 12.09 | 11.64 | 9 | 4.92
2018-10-11 19:00 | 14838.0042 | -0.048233 | 20.06 | 20.06 | 21.75 | 28.49 | 7.26 | 0.97 | 1.24 | 3.49
2018-10-11 20:00 | 16219.5191 | -0.048233 | 19.56 | 19.63 | 20.84 | 28.1 | 4.49 | 0.97 | 12.38 | 2.03
2018-10-11 21:00 | 15867.1491 | -0.048233 | 18.77 | 18.78 | 16.51 | 26.47 | 3.23 | 0.97 | 17.71 | 3.23
2018-10-11 22:00 | 15278.4591 | -0.048233 | 17.4 | 17.4 | 15.54 | 24.35 | 4 | 0.5 | 109.7434 | 34
2018-10-11 23:00 | 14703.4841 | -0.048233 | 17.24 | 17.24 | 13.58 | 21.15 | 3.25 | 0.5 | 30 | 14
2018-10-12 | 14457.6691 | -0.048233 | 16.96 | 16.96 | 13.3 | 20.21 | 3 | 0.5 | 15.96 | 80.1262
2018-10-12 01:00 | 14528.3541 | -0.048233 | 16.25 | 16.25 | 11.67 | 19.45 | 3 | 0.5 | 9.97 | 1.61
2018-10-12 02:00 | 13131.8042 | -0.048233 | 13.35 | 14.35 | 10.84 | 18.75 | 3 | 2 | 12.5 | 1.26
2018-10-12 03:00 | 13221.1042 | -0.048233 | 9.28 | 9.28 | 6.6 | 18.5 | 3 | 2 | 9.11 | 1.26
2018-10-12 04:00 | 14929.2541 | -0.048233 | 12.71 | 12.71 | 8.48 | 18.76 | 3 | 2 | 8 | 1.61
2018-10-12 05:00 | 14366.8042 | -0.048233 | 11.63 | 11.63 | 14.49 | 19.42 | 7.11 | 2 | 31.33 | 34.1
2018-10-12 06:00 | 16192.7213 | 7.9697 | 15.69 | 17.68 | 20.11 | 28.2 | 2.11 | 8.89 | 8.61 | 80.1262
2018-10-12 07:00 | 19390.9591 | 242.056 | 16.08 | 18.48 | 21 | 26.67 | 1.61 | 8.62 | 3.83 | 1.61
2018-10-12 08:00 | 19611.9974 | 608.571 | 16 | 16.56 | 21.17 | 23.86 | 2 | 0.97 | 0.51 | 2
2018-10-12 09:00 | 21610.5926 | 908.974 | 18.18 | 19.28 | 21.11 | 24.68 | 2.44 | 7.4 | 30.07 | 2.44
2018-10-12 10:00 | 22285.0182 | 1106.24 | 18.3 | 18.3 | 20.13 | 28.44 | 3.11 | 7.1 | 2.11 | 3.11
2018-10-12 11:00 | 19208.6675 | 1158.65 | 18.28 | 18.28 | 19.92 | 32.45 | 3.55 | 9.39 | 3.5 | 3.35
2018-10-12 12:00 | 20180.5175 | 1158.65 | 20.38 | 20.41 | 19.51 | 35.04 | 4.54 | 11.42 | 1 | 4.54
2018-10-12 13:00 | 19667.698 | 1037.84 | 32.74 | 22.87 | 20.81 | 44.48 | 24.28 | 24.18 | 2.11 | 16.12
2018-10-12 14:00 | 18148.8636 | 995.067 | 265.8357 | 27.41 | 19.76 | 56.45 | 24.73 | 14.18 | 2 | 14.19
2018-10-12 15:00 | 17098.5902 | 735.516 | 681.5011 | 31.34 | 20.02 | 75.23 | 91.9141 | 25 | 2 | 44.1
2018-10-12 16:00 | 18217.9584 | 341.207 | 869.6011 | 37.45 | 20.96 | 84.77 | 53.22 | 56.9773 | 2.31 | 42.17
2018-10-12 17:00 | 17745.9502 | 80.8059 | 268.3457 | 31.84 | 22.08 | 60.4 | 24.96 | 16.98 | 2.31 | 15.77
2018-10-12 18:00 | 15558.1042 | -0.048233 | 30.12 | 28.21 | 30.13 | 37.95 | 11.44 | 10.07 | 9 | 6.66
2018-10-12 19:00 | 17347.3141 | -0.048233 | 52.57 | 28.04 | 23.15 | 33.39 | 7.82 | 1 | 2.31 | 2.31
2018-10-12 20:00 | 16903.1591 | -0.048233 | 41.03 | 22.96 | 20.47 | 33.19 | 5.31 | 1.14 | 2.61 | 2.31
2018-10-12 21:00 | 14927.3042 | -0.048233 | 21.74 | 21.74 | 18.19 | 30.95 | 3.65 | 0.97 | 10.53 | 3.44
2018-10-12 22:00 | 14278.4542 | -0.048233 | 21.58 | 21.95 | 15.78 | 27.52 | 4.18 | 0.5 | 57.6962 | 24
2018-10-12 23:00 | 15372.3541 | -0.048233 | 72.79 | 18.93 | 14.94 | 23.8 | 3.11 | 0.5 | 15.82 | 28.72
2018-10-13 | 15055.8541 | -0.048233 | 18.76 | 19.9 | 16.59 | 21.25 | 3 | 0.5 | 2.5 | 2.8
2018-10-13 01:00 | 13448.1542 | -0.048233 | 18.02 | 21.25 | 15.5 | 19.77 | 2.5 | 0.5 | 2.5 | 2
2018-10-13 02:00 | 14878.6141 | -0.048233 | 17.21 | 19.47 | 14.86 | 18.85 | 2.5 | 0.97 | 2.5 | 1.26
2018-10-13 03:00 | 13400.6542 | -0.048233 | 17.67 | 19.09 | 14.77 | 18.64 | 2.5 | 0.97 | 2.5 | 1.26
2018-10-13 04:00 | 13667.6042 | -0.048233 | 17.71 | 19.06 | 14.79 | 18.85 | 2.5 | 0.97 | 2.5 | 1.26
2018-10-13 05:00 | 14648.9542 | -0.048233 | 18.54 | 18.54 | 16.11 | 19.91 | 2.9 | 0.97 | 14 | 13.99
2018-10-13 06:00 | 18267.8146 | 5.464 | 71.68 | 21.85 | 19.7 | 29.67 | 2.5 | 0.95 | 8.11 | 32
2018-10-13 07:00 | 17706.8405 | 99.7795 | 46.17 | 27.93 | 22.27 | 27.86 | 2.25 | 0.95 | 3.76 | 2.05
2018-10-13 08:00 | 17885.7355 | 333.09 | 18.7 | 21.01 | 19.04 | 26.88 | 2.5 | 0.95 | 2.61 | 2.5
2018-10-13 09:00 | 20751.179 | 476.364 | 672.8611 | 21.22 | 18.73 | 27.28 | 3.75 | 0.95 | 11.15 | 3.25
2018-10-13 10:00 | 19509.5876 | 632.408 | 20.98 | 20.98 | 19.31 | 30.07 | 3.94 | 2.39 | 2 | 3.59
2018-10-13 11:00 | 20996.0255 | 804.446 | 20.85 | 21.61 | 19.35 | 32.54 | 5 | 6.79 | 1 | 4.38
2018-10-13 12:00 | 19572.3693 | 720.494 | 886.1911 | 27.34 | 19.27 | 37.12 | 5 | 6.89 | 0.71 | 4.27
2018-10-13 13:00 | 21576.6311 | 669.783 | 903.0311 | -3.66 | 19.95 | 50.61 | 20.18 | 20 | 1.66 | 13.99
2018-10-13 14:00 | 20158.8345 | 650.9 | 913.8311 | 32.54 | 20.37 | 67.34 | 30 | 14.79 | 2.1 | 22
2018-10-13 15:00 | 16671.6117 | 408.065 | 39.64 | 39.64 | 20.47 | 91.63 | 79.9741 | 53.5773 | 2 | 37.34
2018-10-13 16:00 | 16092.4309 | 168.401 | 43.37 | 42.5 | 20.47 | 86.31 | 51.95 | 59.4873 | 2.11 | 36.18
2018-10-13 17:00 | 17567.8622 | 50.0021 | 33.01 | 28.34 | 21.88 | 42.3 | 15.45 | 12.73 | 2 | 12.35
2018-10-13 18:00 | 15370.9542 | -0.048233 | 29.21 | 28.28 | 33.04 | 33.36 | 8.23 | 1 | 2.21 | 5.12
2018-10-13 19:00 | 17230.2091 | -0.048233 | 31.92 | 27 | 32.56 | 34.2 | 7.59 | 0.97 | 2.31 | 4.86
2018-10-13 20:00 | 16698.4891 | -0.048233 | 31.9 | 22.73 | 21.88 | 30.7 | 6.5 | 0.97 | 8.61 | 3.17
2018-10-13 21:00 | 14877.9042 | -0.048233 | 21.24 | 21.24 | 18.78 | 28.35 | 3.75 | 0.97 | 10.08 | 3.21
2018-10-13 22:00 | 14398.1542 | -0.048233 | 20.38 | 20.38 | 16.99 | 26.87 | 4.31 | 0.5 | 52.6962 | 19
2018-10-13 23:00 | 14002.9542 | -0.048233 | 17.9 | 18.95 | 15.44 | 24.26 | 5 | 0.5 | 15 | 15.11
2018-10-14 | 15181.3991 | -0.048233 | 17.31 | 20.85 | 15.56 | 21.37 | 3 | 0.5 | 7.15 | 3
2018-10-14 01:00 | 13504.2042 | -0.048233 | 15.28 | 20.37 | 14.11 | 19.03 | 3 | 0.5 | 2.83 | 2
2018-10-14 02:00 | 14838.5241 | -0.048233 | 14.39 | 19.39 | 12.1 | 18.61 | 3 | 0.97 | 9.11 | 1.26
2018-10-14 03:00 | 13355.0542 | -0.048233 | 13.77 | 17.82 | 9.27 | 17.92 | 3 | 10 | 2.22 | 1.11
2018-10-14 04:00 | 15196.1691 | -0.048233 | 14.29 | 16.69 | 13.57 | 17.5 | 3 | 0.97 | 2.11 | 1.26
2018-10-14 05:00 | 14876.0042 | -0.048233 | 15.63 | 16.72 | 18.12 | 18.17 | 3.72 | 0.97 | 14 | 20
2018-10-14 06:00 | 16854.8682 | 6.9666 | 374.3157 | 17.17 | 20.27 | 20.28 | 3.11 | 0.95 | 10.66 | 87.1162
2018-10-14 07:00 | 17746.5728 | 210.603 | 17.11 | 17.11 | 21.2 | 20.07 | 2.87 | 0.97 | 7.58 | 2.87
2018-10-14 08:00 | 18023.609 | 571.22 | 17.37 | 17.88 | 21.32 | 21.59 | 3.11 | 0.97 | 3.5 | 3.11
2018-10-14 09:00 | 19675.2704 | 707.811 | 17.87 | 19.18 | 23.1 | 23.47 | 7 | 0.97 | 15.98 | 5
2018-10-14 10:00 | 21775.5777 | 258.358 | 18.66 | 21.11 | 27.55 | 24.59 | 6.05 | 2.65 | 3.11 | 5
2018-10-14 11:00 | 18319.9349 | 347.142 | 18.92 | 23.48 | 25.06 | 26.68 | 5.19 | 8.39 | 2.61 | 4.57
2018-10-14 12:00 | 19073.644 | 792.52 | 20.08 | 22.39 | 23.25 | 31.87 | 6.06 | 7.1 | 1.64 | 4.42
2018-10-14 13:00 | 19013.49 | 1022.2 | 22.01 | 22.76 | 19.28 | 36.11 | 12.74 | 10 | 1.01 | 10.58
2018-10-14 14:00 | 17196.2398 | 532.305 | 23.37 | 24.08 | 18.32 | 49.88 | 23.83 | 15.72 | 2 | 18.66
2018-10-14 15:00 | 16500.2498 | 538.684 | 27.26 | 26.31 | 19.27 | 74.01 | 46.51 | 64.4473 | 2.11 | 41.14
2018-10-14 16:00 | 15572.8436 | 165.467 | 96.87 | 28.29 | 23.46 | 54.7 | 86.4641 | 73.7873 | 2.31 | 80.0162
2018-10-14 17:00 | 17035.5141 | 21.4067 | 28.64 | 28.64 | 23.98 | 40.73 | 18.95 | 15.59 | 2.06 | 16.36
2018-10-14 18:00 | 14838.9542 | -0.048233 | 24.09 | 27.15 | 36.16 | 30.91 | 8.5 | 9.85 | 9 | 6.53
2018-10-14 19:00 | 16481.1591 | -0.048233 | 22.39 | 25.89 | 36.63 | 30.31 | 8.34 | 0.97 | 3.5 | 6.2
2018-10-14 20:00 | 16095.0291 | -0.048233 | 20.66 | 23.54 | 23.03 | 26.49 | 5.23 | 0.97 | 9.24 | 3.11
2018-10-14 21:00 | 14317.4042 | -0.048233 | 19.84 | 20.6 | 18.41 | 25.72 | 3.75 | 0.97 | 10.03 | 3.27
2018-10-14 22:00 | 13754.0542 | -0.048233 | 17.91 | 19.57 | 18.06 | 24.12 | 7 | 0.5 | 30.43 | 24
2018-10-14 23:00 | 13410.1542 | -0.048233 | 17.32 | 19.23 | 17.22 | 24.5 | 31.75 | 0.5 | 15 | 31.55
2018-10-15 | 14578.9941 | -0.048233 | 17 | 19.89 | 18.93 | 25.68 | 6.5 | 0.5 | 14.31 | 20
2018-10-15 01:00 | 12968.4042 | -0.048233 | 15.43 | 19.11 | 17.22 | 22.58 | 3 | 0.5 | 13.35 | 2.11
2018-10-15 02:00 | 12718.5542 | -0.048233 | 5.49 | 18.78 | 16.88 | 19.01 | 3 | 0.97 | 15 | 1
2018-10-15 03:00 | 13720.2241 | -0.048233 | 4.35 | 17.71 | 16.74 | 17.54 | 3 | 0.97 | 14.05 | 1
2018-10-15 04:00 | 12604.5542 | -0.048233 | 4.15 | 16.81 | 15.76 | 14.86 | 3 | 0.97 | 11.5 | 2
2018-10-15 05:00 | 12959.8542 | -0.048233 | 14.58 | 16.24 | 17.21 | 17.61 | 7.11 | 0.97 | 57.6962 | 35
2018-10-15 06:00 | 14741.4915 | 4.9777 | 16.12 | 16.12 | 18.6 | 19.29 | 3.25 | 0.95 | 30.21 | 1249.3306
2018-10-15 07:00 | 13597.0099 | 166.642 | 16.51 | 16.51 | 19.11 | 20.42 | 2.47 | 0.95 | 13.67 | 3
2018-10-15 08:00 | 15240.3317 | 395.812 | 16.58 | 17.19 | 19.34 | 20.63 | 2.85 | 0.97 | 9.36 | 3.32
2018-10-15 09:00 | 16049.8068 | 742.087 | 17.93 | 17.93 | 19.36 | 21.7 | 8.28 | 10 | 26.81 | 12
2018-10-15 10:00 | 16518.7406 | 968.574 | 18.75 | 19.71 | 16.17 | 23.45 | 5 | 2.32 | 8.26 | 4.8
2018-10-15 11:00 | 16607.5884 | 1073.79 | 19.33 | 21.31 | 12.74 | 25.55 | 7.2 | 9.02 | 3.5 | 7
2018-10-15 12:00 | 16683.3902 | 1124.64 | 21.39 | 22.13 | 12.79 | 27.93 | 5.17 | 10.5 | 2.11 | 4.93
2018-10-15 13:00 | 15064.3685 | 1051.23 | 21.84 | 21.84 | 12.4 | 31.55 | 7.31 | 13.64 | 2.61 | 13.22
2018-10-15 14:00 | 14659.3626 | 893.908 | 32.17 | 32.17 | 11.58 | 42.06 | 18.84 | 13.89 | 2 | 17.82
2018-10-15 15:00 | 14359.0486 | 615.788 | 29.48 | 22.44 | 11.59 | 40.41 | 33.78 | 30 | 2 | 30
2018-10-15 16:00 | 14126.2644 | 318.752 | 31.02 | 22.5 | 31.49 | 30.49 | 43.01 | 64.3973 | 1 | 42.16
2018-10-15 17:00 | 15435.6527 | 31.9504 | 29.03 | 20.95 | 35.95 | 25.79 | 17.45 | 14.87 | 2 | 16.87
2018-10-15 18:00 | 15492.6241 | -0.048233 | 20.11 | 20.11 | 52.38 | 25.16 | 14 | 11.79 | 3.5 | 11.28
2018-10-15 19:00 | 15369.1891 | -0.048233 | 21.14 | 21.14 | 39.95 | 28.45 | 14.1 | 0.97 | 2 | 12.15
2018-10-15 20:00 | 15166.6291 | -0.048233 | 19.8 | 20.39 | 33.36 | 25.59 | 6.52 | 0.97 | 10 | 3.11
2018-10-15 21:00 | 13468.1042 | -0.048233 | 19.14 | 19.14 | 12.76 | 22.59 | 3.75 | 0.97 | 57.6962 | 3.02
2018-10-15 22:00 | 13234.4042 | -0.048233 | 18.39 | 18.65 | 12.04 | 21.16 | 7 | 0.5 | 52.6962 | 29.53
2018-10-15 23:00 | 13078.6042 | -0.048233 | 16.66 | 18.25 | 9.33 | 19.97 | 7 | 0.5 | 18 | 22
2018-10-16 | 12906.6542 | -0.048233 | 16.61 | 17.98 | 10.44 | 18.12 | 3.97 | 0.5 | 9.56 | 3.11
2018-10-16 01:00 | 14236.1191 | -0.048233 | 15.76 | 17.19 | 10.33 | 17.07 | 3 | 0.5 | 9.2 | 1
2018-10-16 02:00 | 14007.1841 | -0.048233 | 14.85 | 16.73 | 6.79 | 15.84 | 2.51 | 15 | 11.72 | 1.15
2018-10-16 03:00 | 12530.4542 | -0.048233 | 16.08 | 16.54 | 4.4 | 16.5 | 2.51 | 15 | 10.03 | 1.17
2018-10-16 04:00 | 12530.4542 | -0.048233 | 16.6 | 16.6 | 4.4 | 16.92 | 3 | 0.97 | 2.11 | 2.61
2018-10-16 05:00 | 13951.2691 | -0.048233 | 16.61 | 16.89 | 4.42 | 18.17 | 3 | 1 | 13.88 | 6
2018-10-16 06:00 | 12412.7063 | 3.0066 | 16.58 | 17.69 | 9.69 | 22.24 | 3.5 | 0.85 | 14.11 | 50.01
2018-10-16 07:00 | 12277.3822 | 47.5602 | 11.37 | 11.37 | 10.54 | 24.3 | 2.37 | 0.85 | 4.19 | 2.5
2018-10-16 08:00 | 12560.1694 | 276.231 | 12.3 | 12.3 | 11.61 | 21.71 | 2.59 | 0.95 | 3.11 | 3.26
2018-10-16 09:00 | 14151.8206 | 193.048 | 13.43 | 13.43 | 15.61 | 22.16 | 7.31 | 14 | 35 | 15
2018-10-16 10:00 | 12959.3148 | 244.384 | 11.4 | 11.4 | 10.5 | 24.13 | 4.45 | 12.11 | 3.51 | 4.25
2018-10-16 11:00 | 14881.676 | 621.854 | 18.7 | 18.95 | 10.36 | 24.79 | 5 | 16 | 3.5 | 15.91
2018-10-16 12:00 | 13279.1019 | 279.002 | 19.18 | 19.18 | 11.23 | 27.07 | 5 | 11.24 | 2.11 | 4.34
2018-10-16 13:00 | 13399.2417 | 259.465 | 19.42 | 19.42 | 11.1 | 28.42 | 6.75 | 12.61 | 2.61 | 12.1
2018-10-16 14:00 | 13483.3082 | 220.956 | 20.01 | 20.01 | 11.42 | 32.68 | 17.07 | 12.12 | 2 | 13.76
2018-10-16 15:00 | 15474.146 | 673.437 | 30.46 | 20.29 | 11.52 | 35.75 | 33.91 | 22.65 | 2 | 25.27
2018-10-16 16:00 | 13561.098 | 215.84 | 31.82 | 21.41 | 12.85 | 31.22 | 43.48 | 30 | 2 | 37.33
2018-10-16 17:00 | 14997.192 | 68.3479 | 31.59 | 20.72 | 33.03 | 28.34 | 16 | 10.81 | 3.5 | 12.38
2018-10-16 18:00 | 13318.0042 | -0.048233 | 21.32 | 21.32 | 39.3 | 29.65 | 7.61 | 1.25 | 2.31 | 6.47
2018-10-16 19:00 | 13392.1042 | -0.048233 | 29.11 | 29.11 | 36.15 | 27.28 | 6.09 | 0.97 | 17.49 | 5.75
2018-10-16 20:00 | 13328.4542 | -0.048233 | 21.03 | 21.03 | 15.27 | 25.68 | 4.42 | 0.97 | 21.86 | 3.5
2018-10-16 21:00 | 14758.3441 | -0.048233 | 19.93 | 19.93 | 15.09 | 24.86 | 3.75 | 0.97 | 21.44 | 2.61
2018-10-16 22:00 | 13166.9542 | -0.048233 | 19.15 | 19.52 | 12.75 | 21.99 | 7.62 | 0.5 | 36.57 | 16.83
2018-10-16 23:00 | 13057.7042 | -0.048233 | 18 | 18.93 | 11.53 | 20.79 | 5.75 | 0.5 | 25.38 | 3.75
2018-10-17 | 14474.5491 | -0.048233 | 18.32 | 18.51 | 9.91 | 18.15 | 3.83 | 0.5 | 59.7562 | 3.63
2018-10-17 01:00 | 12896.2042 | -0.048233 | 17.71 | 17.82 | 13.57 | 15.69 | 3.01 | 0.5 | 10.06 | 1.51
2018-10-17 02:00 | 14159.1041 | -0.048233 | 17.24 | 17.27 | 12.85 | 12.52 | 3 | 1.15 | 8.9 | 1
2018-10-17 03:00 | 12668.2042 | -0.048233 | 16.68 | 16.77 | 12.4 | 13.03 | 3 | 1 | 8.61 | 1
2018-10-17 04:00 | 12980.7542 | -0.048233 | 16.7 | 16.72 | 13.56 | 15.75 | 3 | 1 | 8.61 | 1
2018-10-17 05:00 | 15602.3441 | -0.048233 | 16.57 | 17.1 | 14.43 | 17.65 | 3.01 | 1 | 30 | 12.85
2018-10-17 06:00 | 18111.2397 | 4.0519 | 17.05 | 17.4 | 20.8 | 22.16 | 4 | 0.95 | 14 | 22
2018-10-17 07:00 | 17710.8937 | 171.046 | 17.56 | 18.54 | 25.48 | 23.75 | 2.45 | 0.85 | 8.11 | 2.25
2018-10-17 08:00 | 18123.302 | 418.16 | 17.75 | 17.75 | 28.75 | 22.91 | 2.8 | 0.97 | 3.5 | 3
2018-10-17 09:00 | 21469.7163 | 745.442 | 17.83 | 17.83 | 22.64 | 20.03 | 4.9 | 0.97 | 12.95 | 3.25
2018-10-17 10:00 | 19556.3057 | 758.585 | 19.14 | 19.14 | 23.27 | 21.43 | 4.32 | 1.78 | 3.5 | 3.25
2018-10-17 11:00 | 21108.8936 | 700.43 | 18.99 | 18.99 | 22.38 | 23.07 | 4.28 | 9.25 | 2.61 | 3.87
2018-10-17 12:00 | 22436.3158 | 1158.65 | 19.43 | 19.5 | 20.76 | 24.16 | 4.71 | 9.79 | 1.28 | 3.64
2018-10-17 13:00 | 21405.8816 | 930.507 | 20.16 | 20.35 | 20.92 | 25.62 | 5.03 | 10 | 2.11 | 4.07
2018-10-17 14:00 | 20372.3749 | 699.308 | 19.99 | 20.4 | 20.76 | 28.49 | 29.91 | 7.87 | 2.11 | 19.31
2018-10-17 15:00 | 19069.0459 | 621.925 | 21.13 | 23.77 | 21.37 | 36.37 | 43.43 | 13.66 | 1 | 21.71
2018-10-17 16:00 | 18023.5156 | 108.901 | 21.59 | 22.48 | 21.74 | 31.82 | 44.48 | 14.69 | 10 | 34.16
2018-10-17 17:00 | 16129.2805 | 27.19 | 35.54 | 21.75 | 29.23 | 26.64 | 21.15 | 9.83 | 2.88 | 3.11
2018-10-17 18:00 | 15667.3542 | -0.048233 | 35.52 | 21.37 | 36.82 | 25.5 | 15.15 | 1 | 14.61 | 4.64
2018-10-17 19:00 | 17632.1641 | -0.048233 | 21.51 | 21.94 | 34.59 | 27.86 | 5.85 | 0.99 | 17.18 | 4.62
2018-10-17 20:00 | 17060.3541 | -0.048233 | 43.29 | 21.4 | 23.47 | 24.38 | 4.21 | 0.97 | 13.54 | 3.01
2018-10-17 21:00 | 15226.5542 | -0.048233 | 18.83 | 18.83 | 22.98 | 22.51 | 3.25 | 0.97 | 52.6962 | 2.63
2018-10-17 22:00 | 16345.0641 | -0.048233 | 18.64 | 18.64 | 15.6 | 19.22 | 5.75 | 0.5 | 58.2462 | 39.65
2018-10-17 23:00 | 15909.3491 | -0.048233 | 17.16 | 17.16 | 14.3 | 16.46 | 5.75 | 0.5 | 52.6962 | 15
2018-10-18 | 15848.1591 | -0.048233 | 15 | 15 | 14.05 | 11.52 | 3 | 0.5 | 25 | 2.8
2018-10-18 01:00 | 14091.3042 | -0.048233 | 2.45 | 2.45 | 13.27 | 9.69 | 3 | 0.5 | 16.22 | 1.51
2018-10-18 02:00 | 15470.4691 | -0.048233 | 1.97 | 1.97 | 12.28 | 7.92 | 3 | 1 | 15.34 | 1.51
2018-10-18 03:00 | 13842.4042 | -0.048233 | 0.67 | 0.67 | 13.61 | 10.66 | 3 | 1.17 | 12.97 | 1.51
2018-10-18 04:00 | 15686.7441 | -0.048233 | 6.44 | 6.44 | 15.38 | 13.34 | 3 | 1.16 | 13.34 | 1.51
2018-10-18 05:00 | 15235.1042 | -0.048233 | 12.94 | 15.62 | 15.6 | 17 | 3.01 | 1.15 | 32.03 | 2.81
2018-10-18 06:00 | 17602.8712 | 3.3381 | 15.84 | 18.24 | 17.25 | 24.73 | 4 | 0.85 | 14.11 | 25
2018-10-18 07:00 | 18745.5045 | 108.11 | 17.01 | 20.14 | 22.03 | 26.6 | 2.8 | 0.85 | 13.85 | 2.6
2018-10-18 08:00 | 19152.246 | 344.259 | 15.63 | 22.88 | 21.77 | 25.61 | 2.8 | 0.95 | 2.61 | 3
2018-10-18 09:00 | 19739.2909 | 192.201 | 92.16 | 18.66 | 22.64 | 23.82 | 5 | 0.95 | 25 | 3.25
2018-10-18 10:00 | 22030.6672 | 242.149 | 14.79 | 20.14 | 23.4 | 24.64 | 3.2 | 7 | 3.5 | 3
2018-10-18 11:00 | 21842.6472 | 270.931 | 14.69 | 20.24 | 21.1 | 27.03 | 3.46 | 8.32 | 3.5 | 3.25
2018-10-18 12:00 | 20355.1266 | 570.449 | 16.27 | 20.51 | 21.93 | 27.54 | 25.23 | 10.67 | 2.61 | 23.23
2018-10-18 13:00 | 23719.6895 | 260.118 | 17.76 | 21.16 | 21.79 | 32.94 | 83.7541 | 73.3073 | 2.61 | 79.1162
2018-10-18 14:00 | 21308.0766 | 606.229 | 62.83 | 23.12 | 22.02 | 38.32 | 445.2178 | 73.3073 | 1.5 | 439.4506
2018-10-18 15:00 | 18051.2398 | 490.305 | 48.08 | 24.65 | 21.78 | 42.14 | 539.4178 | 481.7116 | 1.13 | 532.0206
2018-10-18 16:00 | 19345.2101 | 253.692 | 171.33 | 25.32 | 22.19 | 42.16 | 601.4478 | 539.0216 | 2 | 596.2006
2018-10-18 17:00 | 18791.3777 | 35.7324 | 40.37 | 28.63 | 29.47 | 33.35 | 34.78 | 19.02 | 2.96 | 28.35
2018-10-18 18:00 | 15904.8542 | -0.048233 | 42.19 | 25.41 | 38.52 | 27 | 22.9 | 10.91 | 14.61 | 17.73
2018-10-18 19:00 | 17391.6241 | -0.048233 | 20.83 | 20.83 | 38 | 27.86 | 17.88 | 1.3 | 21.43 | 4.79
2018-10-18 20:00 | 17102.5541 | -0.048233 | 19.9 | 20.37 | 33.26 | 30.1 | 3.82 | 0.97 | 21.86 | 3
2018-10-18 21:00 | 17320.9391 | -0.048233 | 18.53 | 19.9 | 18.05 | 27.79 | 3.01 | 1 | 26.99 | 2.79
2018-10-18 22:00 | 15078.3542 | -0.048233 | 18.66 | 19.33 | 16.6 | 22.49 | 5 | 0.5 | 112.7434 | 97.7362
2018-10-18 23:00 | 16285.9841 | -0.048233 | 16.11 | 17.47 | 15.66 | 19.61 | 5 | 0.5 | 30 | 16.33
2018-10-19 | 14498.8542 | -0.048233 | -0.13 | 13.02 | 18.41 | 16.2 | 3.45 | 0.5 | 24.28 | 12
2018-10-19 01:00 | 14500.7542 | -0.048233 | 0 | 15.96 | 17.99 | 14.74 | 3 | 0.5 | 13.18 | 2.5
2018-10-19 02:00 | 15900.9091 | -0.048233 | -0.49 | 14.53 | 16.21 | 13.21 | 3 | 1.2 | 14.65 | 2.25
2018-10-19 03:00 | 14099.8542 | -0.048233 | -0.96 | 15.81 | 16.29 | 14.86 | 3 | 1.2 | 12.18 | 2.25
2018-10-19 04:00 | 15804.9041 | -0.048233 | -0.05 | 16.19 | 17.13 | 17.19 | 3 | 1.18 | 9.3 | 2.61
2018-10-19 05:00 | 15356.7042 | -0.048233 | 15.65 | 16.49 | 32.72 | 18.53 | 3.01 | 1 | 30 | 19
2018-10-19 06:00 | 17487.9427 | 5.3607 | 15.53 | 15.53 | 34.5 | 22.15 | 3.25 | 0.97 | 9.02 | 16.09
2018-10-19 07:00 | 18597.2352 | 130.037 | 17.31 | 18.65 | 36.57 | 22.23 | 2.8 | 0.97 | 8.11 | 2.6
2018-10-19 08:00 | 20534.2679 | 370.761 | 15.6 | 17.45 | 37.16 | 22.43 | 2.8 | 0.97 | 2.99 | 3
2018-10-19 09:00 | 21482.945 | 216.981 | 17.55 | 17.91 | 37.1 | 21.76 | 5.88 | 0.97 | 57.6962 | 3.88
2018-10-19 10:00 | 20161.488 | 987.619 | 17.07 | 18.44 | 36.96 | 23.82 | 4.65 | 8.69 | 8.61 | 3.5
2018-10-19 11:00 | 21665.9864 | 1064.48 | 108.51 | 18.8 | 36.06 | 24.66 | 4.96 | 6.93 | 2.61 | 4.26
2018-10-19 12:00 | 22322.6817 | 1136.94 | 18.02 | 20.53 | 34.22 | 26.58 | 5.15 | 8 | 2 | 3.38
2018-10-19 13:00 | 22380.3343 | 968.587 | 37.37 | 24.51 | 31.33 | 34.49 | 21.9 | 19.74 | 2 | 19.75
2018-10-19 14:00 | 18572.3461 | 894.838 | 44.57 | 26.25 | 29.71 | 40.25 | 34.29 | 9.48 | 1.5 | 25.31
2018-10-19 15:00 | 17329.3775 | 605.45 | 129.43 | 26.57 | 29.34 | 44.02 | 99.5441 | 69.8073 | 1.69 | 88.8962
2018-10-19 16:00 | 18778.4693 | 394.497 | 84.04 | 22.43 | 31.38 | 42.78 | 105.5841 | 22.89 | 15 | 98.5262
2018-10-19 17:00 | 18069.8138 | 48.7856 | 36.58 | 20.88 | 39.67 | 30.5 | 20.89 | 10.19 | 14.11 | 12.09
2018-10-19 18:00 | 15761.4042 | -0.048233 | 41.54 | 19.57 | 42.04 | 25.76 | 7.72 | 0.99 | 25 | 3.11
2018-10-19 19:00 | 17627.9441 | -0.048233 | 53.78 | 21.09 | 38.45 | 24.72 | 5.66 | 0.99 | 2.8 | 5.38
2018-10-19 20:00 | 15514.4042 | -0.048233 | 19.08 | 20.85 | 37.99 | 24.29 | 4.13 | 1 | 8.61 | 3.1
2018-10-19 21:00 | 15293.0542 | -0.048233 | 18.59 | 24.64 | 32.22 | 28.03 | 3.75 | 0.99 | 14.61 | 2.61
2018-10-19 22:00 | 14705.0042 | -0.048233 | 44.16 | 21.93 | 19.1 | 20.84 | 7.11 | 0.5 | 33 | 27.7
2018-10-19 23:00 | 14211.9542 | -0.048233 | 18.38 | 20.59 | 18.41 | 19.78 | 7.61 | 0.5 | 40 | 12
2018-10-20 | 15477.8541 | -0.048233 | 13.29 | 19.41 | 18.06 | 17.69 | 3.01 | 0.49 | 25 | 50
2018-10-20 01:00 | 15373.4091 | -0.048233 | 9.55 | 18.47 | 17.19 | 16.67 | 3 | 0.49 | 14.02 | 2.61
2018-10-20 02:00 | 13744.5542 | -0.048233 | 10.52 | 15.66 | 14.74 | 15.76 | 3 | 0.97 | 14.21 | 2.11
2018-10-20 03:00 | 15028.4241 | -0.048233 | 8.85 | 16.13 | 14.31 | 15.65 | 3 | 0.97 | 9.11 | 1.56
2018-10-20 04:00 | 13769.2542 | -0.048233 | 12.95 | 16.83 | 16.95 | 16.78 | 3 | 0.97 | 5 | 2.61
2018-10-20 05:00 | 14807.6042 | -0.048233 | 15.68 | 18.62 | 18.07 | 18.24 | 3 | 0.97 | 25 | 14.61
2018-10-20 06:00 | 17009.238 | 4.4611 | 18.19 | 22.7 | 32.66 | 23.4 | 4.61 | 0.85 | 14 | 87.1162
2018-10-20 07:00 | 18144.906 | 212.901 | 18.14 | 21.55 | 38.95 | 23.36 | 3.4 | 0.85 | 8.61 | 3
2018-10-20 08:00 | 18380.4309 | 578.822 | 17.41 | 19.17 | 34.03 | 24.07 | 3.45 | 0.95 | 3.5 | 3.45
2018-10-20 09:00 | 19642.6398 | 793.463 | 19.69 | 19.69 | 34.7 | 27.06 | 5.14 | 0.95 | 26.68 | 22
2018-10-20 10:00 | 21819.7948 | 1065.27 | 18.29 | 19.28 | 31.57 | 27.86 | 5.75 | 2 | 28.02 | 4.89
2018-10-20 11:00 | 21528.4355 | 1130.1 | 17.54 | 17.54 | 32.48 | 24.39 | 6.55 | 2 | 18.8 | 5.52
2018-10-20 12:00 | 22631.343 | 1147.51 | 45.74 | 19.23 | 30.57 | 26.97 | 17.39 | 2 | 9.11 | 13.08
2018-10-20 13:00 | 20689.784 | 1125.72 | 57.29 | 19.58 | 28.41 | 28.64 | 25.46 | 16.48 | 3.5 | 20.39
2018-10-20 14:00 | 20912.728 | 963.491 | 20.49 | 20.49 | 20.28 | 36.32 | 23.13 | 1 | 2 | 17.83
2018-10-20 15:00 | 19555.385 | 663.91 | 20.18 | 20.18 | 20.28 | 40.18 | 39.71 | 17.3 | 2 | 18.55
2018-10-20 16:00 | 18584.8663 | 395.987 | 19.59 | 19.59 | 30.28 | 38.36 | 45.01 | 25.07 | 51.9162 | 26.57
2018-10-20 17:00 | 18086.7969 | 56.8833 | 16.88 | 16.88 | 37.31 | 29.01 | 27.46 | 10.89 | 23.55 | 5.76
2018-10-20 18:00 | 17314.6091 | -0.048233 | 17.93 | 17.93 | 40.98 | 29.37 | 20.26 | 0.97 | 31.42 | 11.4
2018-10-20 19:00 | 15507.7542 | -0.048233 | 43.18 | 21.38 | 38.21 | 31.57 | 15.32 | 0.95 | 28.28 | 11.41
2018-10-20 20:00 | 14971.0042 | -0.048233 | 33.97 | 19.69 | 36.62 | 26.89 | 6.75 | 0.95 | 33.71 | 3.1
2018-10-20 21:00 | 16203.6941 | -0.048233 | 368.3957 | 17.78 | 20.52 | 22.56 | 5 | 0.84 | 15 | 3
2018-10-20 22:00 | 14996.7741 | -0.048233 | 409.5557 | 19.6 | 19.43 | 20.92 | 5 | 0.5 | 40 | 25.04
2018-10-20 23:00 | 14196.0291 | -0.048233 | 18.67 | 18.67 | 19.2 | 21.36 | 5 | 0.5 | 33 | 14.15
2018-10-21 | 12395.5542 | -0.048233 | 18.91 | 19.02 | 15.4 | 24.29 | 24.21 | 0.5 | 13.61 | 25
2018-10-21 01:00 | 13441.7041 | -0.048233 | 18.07 | 20 | 13.43 | 19.24 | 8.11 | 0.5 | 15.75 | 2.01
2018-10-21 02:00 | 13005.9891 | -0.048233 | 17.78 | 18.48 | 11.24 | 18.24 | 7.11 | 1 | 15 | 2
2018-10-21 03:00 | 12787.6041 | -0.048233 | 11.95 | 11.95 | 11.26 | 18.12 | 7.2 | 1 | 9.11 | 1.61
2018-10-21 04:00 | 11621.3042 | -0.048233 | 14.79 | 14.79 | 11.24 | 18.02 | 7.11 | 1 | 10.53 | 2.17
2018-10-21 05:00 | 12535.2042 | -0.048233 | 14.11 | 14.11 | 14 | 19.58 | 12.25 | 1 | 31.37 | 25.26
2018-10-21 06:00 | 15746.6513 | 3.7359 | 17.04 | 17.04 | 17.36 | 21.44 | 7.61 | 0.95 | 8 | 87.1162
2018-10-21 07:00 | 15273.871 | 176.759 | 18.92 | 18.92 | 17.84 | 22.18 | 4 | 0.85 | 3.98 | 3.2
2018-10-21 08:00 | 15403.8368 | 509.565 | 17.15 | 17.15 | 18.12 | 23.04 | 4.03 | 0.95 | 2.61 | 3.2
2018-10-21 09:00 | 16017.3486 | 593.367 | 17.74 | 17.74 | 19.65 | 28.04 | 8.54 | 0.97 | 27.56 | 28.07
2018-10-21 10:00 | 17923.7695 | 908.355 | 18.21 | 18.21 | 18.71 | 26.7 | 7.55 | 1.89 | 25 | 3.36
2018-10-21 11:00 | 17540.4405 | 1091.01 | 18.71 | 18.71 | 19.82 | 30.68 | 8.11 | 9.25 | 16.1 | 9.26
2018-10-21 12:00 | 17715.4788 | 940.923 | 20.9 | 21.65 | 18.67 | 36.34 | 6.85 | 9.25 | 2 | 5.21
2018-10-21 13:00 | 17871.1535 | 962.482 | 22.42 | 22.42 | 17.98 | 47.86 | 19.89 | 14.79 | 2.11 | 14.73
2018-10-21 14:00 | 15179.8533 | 880.793 | 34.58 | 23.23 | 18.53 | 42.12 | 18.66 | 11.11 | 1.18 | 12.82
2018-10-21 15:00 | 15128.7 | 630 | 23.09 | 27.15 | 18.4 | 53.64 | 36.81 | 18.46 | 2.11 | 19.84
2018-10-21 16:00 | 13243.2688 | 248.283 | 28.36 | 28.36 | 19.01 | 50.05 | 36.62 | 27.74 | 50.8862 | 28.94
2018-10-21 17:00 | 13110.2902 | 38.3055 | 27.45 | 27.45 | 32.4 | 39.02 | 15 | 14.79 | 27.16 | 13.87
2018-10-21 18:00 | 14124.2891 | -0.048233 | 21.52 | 21.52 | 35.47 | 32.79 | 12 | 9.57 | 32.14 | 10.41
2018-10-21 19:00 | 14111.6291 | -0.048233 | 31.1 | 27 | 33.17 | 33.48 | 9.48 | 0.97 | 28.87 | 4.43
2018-10-21 20:00 | 12325.2542 | -0.048233 | 19.99 | 22.24 | 18.44 | 28.49 | 6 | 0.97 | 112.7434 | 2.11
2018-10-21 21:00 | 11938.6042 | -0.048233 | 19.86 | 20.28 | 15.59 | 25.34 | 5.3 | 0.97 | 15 | 3.2
2018-10-21 22:00 | 12650.4541 | -0.048233 | 17.75 | 27.08 | 15.7 | 26.08 | 15.2 | 0.5 | 52.6962 | 15
2018-10-21 23:00 | 12275.9291 | -0.048233 | 16.5 | 25.47 | 13.78 | 22.98 | 27.85 | 0.5 | 29.16 | 25.85
2018-10-22 | 10862.2542 | -0.048233 | 16.26 | 19.91 | 16.88 | 22.72 | 81.9341 | 0.5 | 17.47 | 81.0362
2018-10-22 01:00 | 10794.8042 | -0.048233 | 15.18 | 19.23 | 16.42 | 18.58 | 30 | 0.5 | 15 | 2.61
2018-10-22 02:00 | 10715.0042 | -0.048233 | 15.18 | 18.62 | 16.05 | 18.03 | 30 | 0.99 | 15 | 2.11
2018-10-22 03:00 | 11852.8741 | -0.048233 | 12.98 | 18.54 | 15.57 | 18.05 | 30 | 0.99 | 13.84 | 1
2018-10-22 04:00 | 10948.7042 | -0.048233 | 13.24 | 17.36 | 15.59 | 18.36 | 30 | 0.99 | 12.62 | 2.61
2018-10-22 05:00 | 12533.3491 | -0.048233 | 15.2 | 17.64 | 16.3 | 19.59 | 100.8241 | 0.99 | 31.83 | 40
2018-10-22 06:00 | 11836.5736 | 4.5511 | 17 | 17.95 | 17.69 | 22.55 | 38 | 0.85 | 35.21 | 87.1162
2018-10-22 07:00 | 12065.4284 | 208.451 | 18.01 | 18.81 | 13.46 | 24.82 | 7.61 | 0.95 | 15 | 3.2
2018-10-22 08:00 | 13715.2416 | 521.229 | 18.09 | 20.36 | 15.03 | 26.26 | 8 | 0.97 | 2.61 | 3.86
2018-10-22 09:00 | 12458.3598 | 671.063 | 20.12 | 20.39 | 17.08 | 24.74 | 7.11 | 0.97 | 26.63 | 13
2018-10-22 10:00 | 12701.8505 | 979.369 | 21.96 | 21.96 | 18.5 | 24.24 | 7.15 | 2.1 | 12.3 | 5.1
2018-10-22 11:00 | 12755.1275 | 1091.45 | 19.81 | 26.22 | 17.66 | 27.16 | 15 | 9.61 | 8.73 | 9.8
2018-10-22 12:00 | 13931.4649 | 1020.18 | 33.38 | 27 | 16.94 | 30.42 | 15 | 9.25 | 2 | 9.98
2018-10-22 13:00 | 12656.261 | 1089.38 | 37.02 | 22.55 | 16.04 | 32.46 | 20 | 10 | 2 | 10
2018-10-22 14:00 | 12396.6573 | 858.113 | 41.55 | 41.55 | 14.81 | 38.34 | 29.43 | 10.21 | 2 | 13.23
2018-10-22 15:00 | 13719.7538 | 649.506 | 36.35 | 22.09 | 14.32 | 39.95 | 20 | 16.84 | 2 | 17.64
2018-10-22 16:00 | 12086.9991 | 343.157 | 21.88 | 21.88 | 15.87 | 32.34 | 33.08 | 25.69 | 24.92 | 30
2018-10-22 17:00 | 13205.3991 | 42.966 | 32.12 | 24.15 | 16.8 | 25.52 | 15 | 13.9 | 2.12 | 14.8
2018-10-22 18:00 | 11896.8042 | -0.048233 | 20.07 | 26.78 | 32.79 | 28.95 | 13.97 | 11.85 | 26.32 | 13.76
2018-10-22 19:00 | 13030.2541 | -0.048233 | 39.07 | 38.73 | 29.76 | 27.85 | 14.43 | 11.87 | 3.5 | 13.98
2018-10-22 20:00 | 12878.3341 | -0.048233 | 183.55 | 183.55 | 16.01 | 25.91 | 8.11 | 0.97 | 53.0662 | 3.2
2018-10-22 21:00 | 12573.4391 | -0.048233 | 98.2 | 98.2 | 17.02 | 29.31 | 8.11 | 0.97 | 26.58 | 5.04
2018-10-22 22:00 | 11150.1042 | -0.048233 | 18.86 | 19.3 | 16.5 | 21.6 | 14.91 | 0.5 | 112.2134 | 98.0262
2018-10-22 23:00 | 11035.1542 | -0.048233 | 16.54 | 18.22 | 15.54 | 20.78 | 31.8 | 0.5 | 37.82 | 29.8
2018-10-23 | 11011.4042 | -0.048233 | 4.3 | 17.21 | 16.91 | 18.53 | 25 | 0.5 | 24.47 | 24.8
2018-10-23 01:00 | 10940.1542 | -0.048233 | 7.66 | 15.97 | 16.97 | 16.4 | 7.57 | 0.5 | 16.67 | 2.51
2018-10-23 02:00 | 12011.1241 | -0.048233 | -0.4 | 13.11 | 14.96 | 11.36 | 27.25 | 0.99 | 15.81 | 2.51
2018-10-23 03:00 | 10756.8042 | -0.048233 | -0.36 | -0.36 | 11.33 | 14.93 | 27.25 | 0.99 | 13.53 | 2.51
2018-10-23 04:00 | 10852.7542 | -0.048233 | -0.11 | 7.59 | 12.43 | 16.04 | 18 | 0.99 | 18.47 | 2.61
2018-10-23 05:00 | 11085.5042 | -0.048233 | 11.05 | 16.12 | 14.25 | 18.15 | 19.08 | 0.99 | 35.46 | 87.1162
2018-10-23 06:00 | 11021.445 | 2.5211 | 419.9157 | 16.49 | 16.72 | 24.83 | 14.65 | 0.97 | 35.62 | 45
2018-10-23 07:00 | 11178.4667 | 137.807 | 16.87 | 16.87 | 16.71 | 23.68 | 7.15 | 0.97 | 15 | 3.2
2018-10-23 08:00 | 12730.7356 | 482.048 | 17.39 | 17.79 | 16.83 | 22.67 | 5.8 | 0.97 | 2 | 4.29
2018-10-23 09:00 | 13180.1561 | 639.039 | 17.55 | 19.19 | 16.88 | 26.47 | 7.15 | 0.97 | 26.66 | 11.86
2018-10-23 10:00 | 13942.5667 | 993.703 | 20.07 | 20.56 | 16.81 | 24.68 | 7.15 | 2.5 | 8.61 | 5.82
2018-10-23 11:00 | 13282.9859 | 323.508 | 18.37 | 18.79 | 16.73 | 26.26 | 7.88 | 7.67 | 2.61 | 6.23
2018-10-23 12:00 | 12968.8395 | 1091.41 | 18.22 | 20.76 | 16.16 | 29.95 | 8.21 | 8 | 2 | 6
2018-10-23 13:00 | 13053.4655 | 1024.49 | -3.88 | 22.53 | 15.76 | 32.39 | 12.68 | 9.25 | 2 | 11.5
2018-10-23 14:00 | 13100.2739 | 833.762 | 20.04 | 21.28 | 14.84 | 36.48 | 19.89 | 13.67 | 1.5 | 14.17
2018-10-23 15:00 | 14553.1564 | 581.461 | 20.87 | 23.86 | 15.04 | 46.37 | 27.49 | 23.66 | 1.5 | 23.67
2018-10-23 16:00 | 12754.7655 | 291.069 | 30.63 | 28.12 | 22.62 | 46.3 | 25.35 | 25.14 | 10 | 25.15
2018-10-23 17:00 | 13949.5165 | 32.2905 | 20.59 | 26.13 | 31.86 | 36.14 | 15.24 | 15.03 | 2 | 15.04
2018-10-23 18:00 | 13891.1341 | -0.048233 | 19.99 | 21.66 | 42.85 | 32 | 15.5 | 14.4 | 8.61 | 15
2018-10-23 19:00 | 12677.7042 | -0.048233 | 19.99 | 20.98 | 38.94 | 29.79 | 14.88 | 13.93 | 3.03 | 14.68
2018-10-23 20:00 | 14058.8791 | -0.048233 | 18.79 | 18.79 | 31.36 | 26.32 | 8.11 | 0.97 | 4.02 | 3.2
2018-10-23 21:00 | 12622.6042 | -0.048233 | 17.43 | 17.43 | 16.36 | 24.67 | 7.43 | 0.97 | 26.64 | 5.96
2018-10-23 22:00 | 12440.2042 | -0.048233 | 17.47 | 17.47 | 13.01 | 21.67 | 25 | 0.5 | 40 | 30
2018-10-23 23:00 | 13841.5491 | -0.048233 | 16.43 | 16.43 | 12.89 | 19.82 | 24.63 | 0.5 | 35.9 | 25.26
2018-10-24 | 12455.4042 | -0.048233 | 16.7 | 16.7 | 9.43 | 18.95 | 39.65 | 0.5 | 15.72 | 39.45
2018-10-24 01:00 | 13749.7641 | -0.048233 | 16.29 | 16.29 | 4.42 | 16.78 | 18 | 0.5 | 10.37 | 2.11
2018-10-24 02:00 | 13591.5141 | -0.048233 | 16.21 | 16.21 | 4.09 | 13.25 | 23.65 | 1.79 | 12.76 | 2.11
2018-10-24 03:00 | 13585.1841 | -0.048233 | 16.15 | 16.15 | 4.08 | 17.31 | 22 | 1.32 | 8.46 | 1.58
2018-10-24 04:00 | 13890.0791 | -0.048233 | 15.43 | 19.05 | 4.42 | 18.12 | 15.62 | 1.32 | 10 | 2.51
2018-10-24 05:00 | 13715.1042 | -0.048233 | 13.97 | 19.39 | 9.32 | 19.42 | 23.65 | 1.42 | 30 | 25.81
2018-10-24 06:00 | 15897.7026 | 2.4237 | 13.33 | 20.4 | 19.76 | 26.54 | 23.65 | 8 | 8.38 | 87.1162
2018-10-24 07:00 | 19654.1309 | 125.508 | 13.74 | 19.68 | 20.07 | 25.36 | 5.68 | 0.97 | 8.8 | 4
2018-10-24 08:00 | 18617.6506 | 400.527 | 16.38 | 18.85 | 24.02 | 21.43 | 5.75 | 0.97 | 2.11 | 4
2018-10-24 09:00 | 18460.8835 | 739.509 | 17.84 | 18.67 | 30.07 | 21.67 | 20 | 0.97 | 20.18 | 20.09
2018-10-24 10:00 | 20387.3791 | 917.53 | 18.1 | 19.44 | 30.87 | 22.4 | 7.46 | 6 | 15 | 6.42
2018-10-24 11:00 | 18144.0975 | 1066.05 | 18.42 | 18.42 | 29.29 | 22.7 | 14 | 10 | 10 | 13.8
2018-10-24 12:00 | 18504.8458 | 969.785 | 18.53 | 18.79 | 23.51 | 23.8 | 7.98 | 10 | 2.11 | 12.87
2018-10-24 13:00 | 18680.99 | 1017.2 | 18.13 | 18.78 | 21.91 | 28.17 | 17.46 | 12.66 | 2.11 | 12.66
2018-10-24 14:00 | 16570.9735 | 838.13 | 18.1 | 18.22 | 20.02 | 27.79 | 33.95 | 9.09 | 2.21 | 27.95
2018-10-24 15:00 | 17461.7238 | 650.397 | 18.05 | 18.39 | 22.41 | 32.76 | 24.99 | 16.2 | 2.31 | 16.2
2018-10-24 16:00 | 16649.8159 | 289.816 | 17.15 | 18.57 | 29.02 | 31.11 | 21.7 | 15 | 15 | 16.5
2018-10-24 17:00 | 14634.6925 | 35.9395 | 18 | 18.84 | 35.2 | 31.75 | 13.61 | 8.81 | 12.42 | 7.64
2018-10-24 18:00 | 15716.2841 | -0.048233 | 18.06 | 20.52 | 44.94 | 38.19 | 20.31 | 10.39 | 15 | 19.84
2018-10-24 19:00 | 15747.9341 | -0.048233 | 345.9557 | 301.63 | 39.02 | 32.9 | 15 | 11.19 | 8.61 | 12.43
2018-10-24 20:00 | 13786.3542 | -0.048233 | 18.29 | 27.98 | 30.54 | 30.84 | 7.21 | 1 | 10.53 | 3.1
2018-10-24 21:00 | 15120.2091 | -0.048233 | 17.99 | 23.19 | 30.41 | 27.55 | 8 | 1 | 15 | 6.08
2018-10-24 22:00 | 14461.8891 | -0.048233 | 16.3 | 22 | 19.29 | 24.49 | 25.65 | 0.5 | 54.3962 | 32
2018-10-24 23:00 | 14000.8541 | -0.048233 | 15.71 | 19.93 | 18.34 | 24.68 | 31.65 | 0.5 | 20 | 29.65
2018-10-25 | 12373.7042 | -0.048233 | 16.78 | 19.31 | 10.8 | 19.33 | 38.23 | 0.5 | 12.13 | 33.23
2018-10-25 01:00 | 13660.0891 | -0.048233 | 11.54 | 18.91 | 10.59 | 18.71 | 24.65 | 0.5 | 8.61 | 2.01
2018-10-25 02:00 | 13656.9241 | -0.048233 | 10.6 | 18.01 | 10.79 | 17.85 | 24.65 | 1 | 8.61 | 2
2018-10-25 03:00 | 13525.0491 | -0.048233 | 13.84 | 17.88 | 10.32 | 17.03 | 19.65 | 1 | 3.5 | 1.03
2018-10-25 04:00 | 12554.2042 | -0.048233 | 13.3 | 17.94 | 10.5 | 17.74 | 19.65 | 1 | 7 | 2.11
2018-10-25 05:00 | 15131.8141 | -0.048233 | 13.28 | 18.05 | 19.15 | 19.25 | 25 | 1 | 21.86 | 25
2018-10-25 06:00 | 17386.2315 | 4.8403 | 11.45 | 19.23 | 21.68 | 24.37 | 32.71 | 0.95 | 8.87 | 35
2018-10-25 07:00 | 17117.1615 | 85.0647 | 12.63 | 20.44 | 19.14 | 25.55 | 7.11 | 10 | 9.11 | 4
2018-10-25 08:00 | 17094.5271 | 129.239 | 13.46 | 19.45 | 20.38 | 24.58 | 7.75 | 10 | 2.86 | 11.8
2018-10-25 09:00 | 19101.0049 | 622.321 | 14.64 | 19.62 | 21.39 | 26.39 | 18.11 | 10 | 16.47 | 18
2018-10-25 10:00 | 21260.5204 | 932.152 | -38.73 | -38.73 | 21.71 | 26.31 | 6.62 | 9.97 | 15 | 4.77
2018-10-25 11:00 | 17684.2339 | 774.983 | 17.73 | 21.41 | 21.72 | 29.32 | 9.27 | 10 | 10 | 11.8
2018-10-25 12:00 | 18676.5478 | 481.524 | 17.73 | 20.6 | 20.62 | 27.56 | 9.78 | 10 | 3.5 | 5
2018-10-25 13:00 | 17779.8067 | 609.586 | 17.85 | 20.41 | 20.48 | 28.28 | 15.09 | 11.79 | 3.5 | 11.55
2018-10-25 14:00 | 18376.9226 | 426.884 | 18.62 | 23.64 | 20.18 | 31.2 | 20.2 | 8.17 | 3.07 | 10.52
2018-10-25 15:00 | 15668.7632 | 360.435 | 18.6 | 25.24 | 20.14 | 37.27 | 29.79 | 10.44 | 2 | 14.84
2018-10-25 16:00 | 15176.591 | 328.359 | 32.81 | 28.57 | 22.17 | 37.21 | 30.67 | 11.02 | 15.11 | 15.56
2018-10-25 17:00 | 14594.874 | 41.0253 | 19.38 | 26.77 | 32.51 | 31.84 | 19.92 | 1 | 15 | 11.18
2018-10-25 18:00 | 14314.5542 | -0.048233 | 19.95 | 27.11 | 37.73 | 29.99 | 20.69 | 1 | 20 | 20.07
2018-10-25 19:00 | 14409.5542 | -0.048233 | 34.06 | 34.06 | 35.42 | 27.2 | 13.66 | 1 | 25.21 | 11.66
2018-10-25 20:00 | 15605.5091 | -0.048233 | 19.12 | 20.48 | 31.48 | 27.13 | 8.75 | 0.97 | 16.95 | 2.61
2018-10-25 21:00 | 13870.9042 | -0.048233 | 17.88 | 19.06 | 20.92 | 24.68 | 19.75 | 0.97 | 20 | 3.2
2018-10-25 22:00 | 13341.7542 | -0.048233 | 15.93 | 18.03 | 20.54 | 20.29 | 39.93 | 0.5 | 51.3462 | 40
2018-10-25 23:00 | 12971.2542 | -0.048233 | 7.52 | 7.52 | 19.23 | 17.84 | 31.65 | 0.5 | 33.2 | 29.65
2018-10-26 | 12823.0542 | -0.048233 | 5.74 | 14.2 | 19.2 | 12.21 | 41.64 | 0.49 | 30.28 | 41.64
2018-10-26 01:00 | 14161.2141 | -0.048233 | 0 | 0 | 17.83 | 7 | 26.65 | 0.5 | 19.59 | 2.11
2018-10-26 02:00 | 14152.7741 | -0.048233 | -0.37 | -0.37 | 16.6 | 4.55 | 20 | 0.99 | 20.1 | 2.11
2018-10-26 03:00 | 12639.7042 | -0.048233 | -0.38 | -0.38 | 14.03 | 5.14 | 20 | 0.99 | 20.03 | 2.11
2018-10-26 04:00 | 12803.1042 | -0.048233 | -0.37 | -0.37 | 16.76 | 5.77 | 20 | 1 | 21.18 | 2.61
2018-10-26 05:00 | 15354.4191 | -0.048233 | 10.43 | 10.43 | 19.7 | 13.27 | 30 | 0.99 | 50.2762 | 35
2018-10-26 06:00 | 17442.5839 | 1.2549 | 15.39 | 17.38 | 22.52 | 23.06 | 40 | 0.97 | 3.11 | 100.1162
2018-10-26 07:00 | 16537.9442 | 40.3623 | 17.18 | 17.18 | 32.08 | 25.85 | 5 | 0.97 | 2.61 | 3.32
2018-10-26 08:00 | 18521.9862 | 107.385 | 16.75 | 16.75 | 31.15 | 23.25 | 5 | 0.97 | 2.73 | 3.93
2018-10-26 09:00 | 17760.6319 | 201.402 | 17.65 | 17.68 | 23.2 | 22.08 | 20 | 0.97 | 20.5 | 20.4
2018-10-26 10:00 | 19776.5901 | 253.583 | 18.38 | 18.58 | 31.16 | 23.18 | 5 | 3 | 2.72 | 4.3
2018-10-26 11:00 | 20146.7569 | 744.452 | 17.24 | 17.24 | 31 | 23.62 | 5.6 | 4.89 | 2.31 | 11.96
2018-10-26 12:00 | 20881.1719 | 1023.58 | 16.93 | 16.93 | 20.75 | 25.15 | 7.5 | 8 | 1 | 11.7
2018-10-26 13:00 | 18509.2737 | 814.446 | 17.27 | 17.27 | 20.11 | 26.58 | 12.95 | 8.8 | 2.31 | 10.99
2018-10-26 14:00 | 16401.637 | 461.881 | 37.24 | 17.28 | 19.98 | 28 | 16.27 | 11.26 | 2 | 11.26
2018-10-26 15:00 | 17421.7974 | 379.552 | 38.8 | 17.36 | 19.53 | 30.89 | 27.93 | 17.43 | 1.23 | 22.45
2018-10-26 16:00 | 16802.0038 | 181.07 | 35.51 | 18.56 | 22.6 | 31.85 | 40.79 | 20.01 | 2 | 36.13
2018-10-26 17:00 | 16438.5131 | 38.529 | 18.63 | 18.63 | 34.72 | 28.58 | 20 | 20 | 2.11 | 20
2018-10-26 18:00 | 15866.0941 | -0.048233 | 19.14 | 19.14 | 49.39 | 30.97 | 22.07 | 21.67 | 3.5 | 22.07
2018-10-26 19:00 | 14427.6042 | -0.048233 | 32.68 | 19.04 | 39.74 | 29.55 | 22.21 | 21.56 | 10.18 | 22.01
2018-10-26 20:00 | 13979.2042 | -0.048233 | 18.52 | 18.52 | 33.23 | 26.81 | 15.55 | 13.11 | 10.03 | 2.89
2018-10-26 21:00 | 15487.3491 | -0.048233 | 17.67 | 17.67 | 29.74 | 24.56 | 5 | 0.97 | 12.43 | 3
2018-10-26 22:00 | 14932.4191 | -0.048233 | 18.22 | 18.22 | 19.67 | 19.29 | 37.46 | 0.5 | 40 | 37.46
2018-10-26 23:00 | 12995.0042 | -0.048233 | 14.01 | 14.01 | 19 | 16.15 | 31.38 | 0.5 | 40 | 31.18
2018-10-27 | 12691.0042 | -0.048233 | 14.58 | 14.58 | 18.58 | 12.01 | 45 | 0.49 | 40 | 23.52
2018-10-27 01:00 | 12621.6542 | -0.048233 | 11.88 | 11.88 | 17.97 | 4.73 | 30 | 0.5 | 25.6 | 1.48
2018-10-27 02:00 | 13791.9641 | -0.048233 | 4.74 | 4.74 | 15.33 | 4.52 | 30 | 0.99 | 24.35 | 1.01
2018-10-27 03:00 | 12275.8542 | -0.048233 | 9.34 | 9.34 | 16.77 | 6.6 | 30 | 1 | 20.57 | 1
2018-10-27 04:00 | 13996.6341 | -0.048233 | 6.4 | 6.4 | 17.5 | 6.01 | 30 | 0.99 | 23.57 | 2
2018-10-27 05:00 | 13359.8042 | -0.048233 | 6.65 | 6.65 | 19.29 | 15.39 | 20 | 0.99 | 53.6462 | 36.24
2018-10-27 06:00 | 17041.3091 | 1.8996 | 14.77 | 14.77 | 30.27 | 22.02 | 20 | 1 | 8.11 | 100.1162
2018-10-27 07:00 | 18374.0418 | 42.1534 | 19.52 | 21.19 | 30.36 | 23.96 | 4.72 | 1 | 3.94 | 4.39
2018-10-27 08:00 | 18109.7935 | 112.681 | 17.94 | 20.08 | 23 | 25.74 | 4.77 | 0.97 | 2 | 18
2018-10-27 09:00 | 18891.0505 | 185.209 | 18.49 | 20.18 | 22.57 | 23.23 | 20 | 0.97 | 37.29 | 31.96
2018-10-27 10:00 | 19117.5305 | 239.882 | 20.09 | 20.09 | 30.06 | 27.87 | 5.2 | 3 | 2.11 | 5
2018-10-27 11:00 | 16811.3966 | 269.207 | 21.11 | 21.19 | 24.06 | 26.25 | 7.31 | 5 | 2 | 5.95
2018-10-27 12:00 | 18067.8344 | 274.773 | 20.15 | 20.15 | 19.65 | 24.33 | 7.31 | 6.93 | 2.31 | 12
2018-10-27 13:00 | 17711.4124 | 210.592 | 56.36 | 56.36 | 19.49 | 25.67 | 14.82 | 7.5 | 2.21 | 11.11
2018-10-27 14:00 | 15856.8366 | 173.407 | 19.11 | 19.11 | 19.41 | 26.38 | 14.9 | 10.41 | 2.31 | 12
2018-10-27 15:00 | 15024.0201 | 118.758 | 42.78 | 17.6 | 19.38 | 26.08 | 27.63 | 15 | 2.3 | 22.14
2018-10-27 16:00 | 14490.7035 | 67.3721 | 55.71 | 17.15 | 24.01 | 24.64 | 26.46 | 15.62 | 10 | 21.91
2018-10-27 17:00 | 15914.6372 | 14.9642 | 17.34 | 17.34 | 32.34 | 23.31 | 6.98 | 10.58 | 1.42 | 11.48
2018-10-27 18:00 | 15236.2591 | -0.048233 | 32.34 | 19.12 | 40.93 | 35.4 | 18.86 | 17.72 | 8.61 | 18.72
2018-10-27 19:00 | 15369.1891 | -0.048233 | 52.92 | 24.86 | 34.87 | 34.53 | 15.35 | 12.54 | 21.43 | 13.64
2018-10-27 20:00 | 13421.5542 | -0.048233 | 20.86 | 20.86 | 32.13 | 26.37 | 7.55 | 0.97 | 16.41 | 5
2018-10-27 21:00 | 14948.2441 | -0.048233 | 20.58 | 20.58 | 19.85 | 25.94 | 5.6 | 0.97 | 28.9 | 3.2
2018-10-27 22:00 | 12992.1542 | -0.048233 | 19.3 | 19.3 | 19.98 | 22.75 | 20.59 | 0.5 | 41.58 | 45
2018-10-27 23:00 | 12633.0542 | -0.048233 | 17.27 | 19.04 | 19.03 | 22.13 | 21 | 0.5 | 17.2 | 16
2018-10-28 | 13779.3041 | -0.048233 | 14.97 | 19.23 | 17.66 | 20.19 | 6.46 | 0.5 | 11.67 | 14.8
2018-10-28 01:00 | 13938.6091 | -0.048233 | 14.25 | 19.19 | 15.72 | 19.2 | 3 | 0.5 | 13.94 | 1.61
2018-10-28 02:00 | 13875.3091 | -0.048233 | 8.88 | 18.55 | 11.06 | 18.72 | 3 | 0.99 | 15.05 | 1.61
2018-10-28 03:00 | 13656.9241 | -0.048233 | -0.56 | 17.8 | 12.67 | 18.9 | 3 | 0.99 | 15.38 | 1
2018-10-28 04:00 | 14025.1191 | -0.048233 | -8.36 | 17.81 | 11.15 | 19.44 | 3 | 0.99 | 2.61 | 2.11
2018-10-28 05:00 | 13698.9542 | -0.048233 | -0.95 | 18.9 | 15.33 | 20.69 | 6.7 | 0.99 | 25.11 | 20
2018-10-28 06:00 | 15667.6421 | 1.2548 | 6.32 | 22.06 | 32.65 | 24.02 | 6.26 | 0.97 | 0.51 | 50
2018-10-28 07:00 | 16993.7681 | 161.177 | 15 | 23.43 | 32.51 | 27.02 | 4.56 | 0.97 | 0.25 | 3.28
2018-10-28 08:00 | 19084.7844 | 406.843 | 14.22 | 27.36 | 32.03 | 39.09 | 4.45 | 0.97 | 0.25 | 19.82
2018-10-28 09:00 | 17973.2362 | 779.196 | 16.1 | 31.31 | 32.28 | 39.22 | 4.9 | 0.97 | 23.31 | 21.97
2018-10-28 10:00 | 18151.1018 | 918.423 | 16.84 | 26.64 | 31.07 | 31.06 | 4.3 | 3 | 2.22 | 4.3
2018-10-28 11:00 | 18193.4215 | 1101.97 | 19.62 | 23.91 | 30.48 | 25.45 | 5.1 | 3 | 2.61 | 4.18
2018-10-28 12:00 | 18022.1175 | 1127.65 | 19.55 | 21.34 | 19.32 | 23.14 | 4.52 | 3 | 0.61 | 4.33
2018-10-28 13:00 | 19624.2238 | 1002.16 | 20.37 | 20.37 | 18.64 | 21.22 | 3.15 | 2.94 | 2 | 2.95
2018-10-28 14:00 | 18095.8569 | 920.471 | 270.4057 | 19.17 | 18.03 | 20.24 | 2.31 | 1 | 0.76 | 2.11
2018-10-28 15:00 | 15614.161 | 686.959 | 316.9257 | 18.89 | 16.91 | 19.3 | 24.29 | 18.42 | 0.01 | 18.44
2018-10-28 16:00 | 16661.7638 | 278.141 | 124.29 | 18.97 | 18.8 | 20.19 | 25.7 | 20.28 | 2.31 | 20.29
2018-10-28 17:00 | 14906.5679 | 43.1241 | 19.24 | 19.24 | 27.36 | 23.2 | 15.36 | 14.26 | 2.11 | 15.16
2018-10-28 18:00 | 16127.7341 | -0.048233 | 20.67 | 22.71 | 32.47 | 33 | 19.57 | 15.88 | 9.94 | 17.6
2018-10-28 19:00 | 15847.1041 | -0.048233 | 31.08 | 27.89 | 30.84 | 31.2 | 5.5 | 11.59 | 2 | 11.89
2018-10-28 20:00 | 15475.7441 | -0.048233 | 19.31 | 30.87 | 19.86 | 26.97 | 5.36 | 0.97 | 10.13 | 3.1
2018-10-28 21:00 | 15232.0391 | -0.048233 | 18.01 | 25.25 | 18 | 24.68 | 6.81 | 0.97 | 8.61 | 4.57
2018-10-28 22:00 | 13100.4542 | -0.048233 | 190.58 | 21.43 | 16.65 | 22.22 | 8.24 | 0.5 | 22.91 | 21.86
2018-10-28 23:00 | 14026.1741 | -0.048233 | 14.96 | 21.34 | 17.28 | 23.79 | 15 | 0.5 | 16.6 | 24.32
2018-10-29 | 13685.4091 | -0.048233 | 14.71 | 18.27 | 16.88 | 27.72 | 14 | 0.5 | 16.07 | 13.8
2018-10-29 01:00 | 12254.9542 | -0.048233 | 13.31 | 17.36 | 14.96 | 23.89 | 8 | 0.5 | 17.63 | 2.11
2018-10-29 02:00 | 12149.5042 | -0.048233 | 13.04 | 16.95 | 12.18 | 20.93 | 8 | 0.99 | 15.94 | 2.4
2018-10-29 03:00 | 12057.3542 | -0.048233 | 12.1 | 16.49 | 4.85 | 20.84 | 8 | 0.99 | 12.24 | 2.01
2018-10-29 04:00 | 12023.1542 | -0.048233 | 11.2 | 16.43 | 12.05 | 22.33 | 7.11 | 0.99 | 10 | 2.42
2018-10-29 05:00 | 13923.8391 | -0.048233 | 12.74 | 16.69 | 12.34 | 20.53 | 20 | 0.99 | 27.63 | 22.9
2018-10-29 06:00 | 12820.4938 | 1.2567 | 14.33 | 16.67 | 28.81 | 24.72 | 23.14 | 10 | 11.47 | 88.1762
2018-10-29 07:00 | 13061.2907 | 173.727 | 15.73 | 17.86 | 35.4 | 27.91 | 4.83 | 10.51 | 0.25 | 3.5
2018-10-29 08:00 | 14864.1704 | 527.261 | 14.78 | 18.78 | 31.07 | 33.29 | 4.81 | 12.13 | 0.25 | 3.5
2018-10-29 09:00 | 15161.847 | 770.419 | 39.48 | 19.74 | 30.84 | 36.7 | 20.24 | 15.8 | 29.39 | 23.31
2018-10-29 10:00 | 15279.7507 | 879.176 | 18.07 | 21.63 | 30.83 | 29.45 | 17.72 | 10 | 2.61 | 4.3
2018-10-29 11:00 | 13985.1495 | 1044.21 | 17.71 | 19.32 | 32.72 | 25.11 | 6.36 | 6 | 2 | 3.8
2018-10-29 12:00 | 15792.7064 | 1083.39 | 18.17 | 19.14 | 19.48 | 22.95 | 6.16 | 6 | 0.61 | 5.58
2018-10-29 13:00 | 14077.3441 | 965.257 | 19.06 | 19.06 | 18.72 | 22.91 | 7.42 | 6 | 2 | 5.97
2018-10-29 14:00 | 13918.0253 | 892.553 | 18.85 | 18.85 | 16.95 | 23.08 | 17.13 | 8.64 | 0.71 | 11.13
2018-10-29 15:00 | 13620.0873 | 584.934 | 18.87 | 18.87 | 17.38 | 23.24 | 34.21 | 14.4 | 0 | 22.79
2018-10-29 16:00 | 14879.5934 | 318.88 | 19.22 | 19.22 | 19.55 | 23.21 | 25.28 | 19.78 | 10 | 19.78
2018-10-29 17:00 | 13140.9085 | 29.5353 | 19.65 | 19.65 | 30.48 | 24.42 | 16.08 | 12.08 | 11.99 | 12.08
2018-10-29 18:00 | 12958.9042 | -0.048233 | 18.79 | 24.36 | 33.19 | 32.02 | 18.51 | 12.58 | 15 | 17.3
2018-10-29 19:00 | 12889.5542 | -0.048233 | 19.96 | 23.32 | 32.8 | 31.96 | 14.53 | 0.97 | 15 | 13.87
2018-10-29 20:00 | 14197.0841 | -0.048233 | 18.36 | 19.29 | 19.31 | 23.28 | 4.33 | 0.82 | 18.53 | 3.1
2018-10-29 21:00 | 12526.6542 | -0.048233 | 17.3 | 17.3 | 18.92 | 22.51 | 4.5 | 0.97 | 20.5 | 3.5
2018-10-29 22:00 | 12142.8542 | -0.048233 | 8.34 | 8.34 | 17.72 | 18.72 | 91.2741 | 0.5 | 102.7434 | 90.4762
2018-10-29 23:00 | 13141.0291 | -0.048233 | 12.23 | 12.23 | 17.3 | 19.46 | 45 | 0.5 | 54.2562 | 44.8
2018-10-30 | 11750.5042 | -0.048233 | 6.52 | 6.52 | 14.64 | 12.27 | 45 | 0.49 | 32.77 | 24.01
2018-10-30 01:00 | 13031.3091 | -0.048233 | 7.13 | 7.13 | 16.08 | 9.35 | 50.81 | 0.49 | 14.69 | 2
2018-10-30 02:00 | 11676.4042 | -0.048233 | 6.28 | 6.28 | 14.53 | 9.76 | 45 | 0.99 | 14.08 | 2
2018-10-30 03:00 | 12959.5691 | -0.048233 | 0.01 | 0.01 | 10.91 | 14.74 | 45 | 0.99 | 10.03 | 2
2018-10-30 04:00 | 12997.5491 | -0.048233 | 0.28 | 0.28 | 11.15 | 17.56 | 45 | 0.99 | 14.21 | 2.04
2018-10-30 05:00 | 11817.9542 | -0.048233 | 11.13 | 11.13 | 16.87 | 18.3 | 30 | 0.99 | 35 | 30
2018-10-30 06:00 | 12047.3269 | 1.3968 | 16.96 | 17.21 | 18.04 | 23.89 | 20 | 10 | 0.51 | 50
2018-10-30 07:00 | 13448.3203 | 206.223 | 17.66 | 19.83 | 32.73 | 24.76 | 4.95 | 10 | 0.25 | 3.5
2018-10-30 08:00 | 12430.3443 | 529.573 | 17.58 | 18.57 | 17.23 | 25.46 | 4.71 | 10 | 0.25 | 3.5
2018-10-30 09:00 | 14230.3475 | 676.481 | 18.04 | 19.26 | 19.9 | 25.3 | 20 | 14 | 23.31 | 20
2018-10-30 10:00 | 14574.0696 | 708.284 | 18.25 | 20.43 | 19.3 | 25.5 | 4.66 | 10 | 3.01 | 3.8
2018-10-30 11:00 | 13639.473 | 1089.34 | 18.45 | 18.45 | 19.63 | 23.92 | 5.25 | 10 | 2.11 | 5.05
2018-10-30 12:00 | 14710.8894 | 558.971 | 17.09 | 17.09 | 19.28 | 23.62 | 4.71 | 10 | 0.61 | 4.51
2018-10-30 13:00 | 13626.667 | 835.86 | 16.91 | 16.91 | 17.89 | 25.25 | 16.59 | 10 | 2 | 12.38
2018-10-30 14:00 | 15025.9536 | 521.61 | 16.7 | 16.7 | 16.83 | 27.96 | 29.83 | 6.74 | 1.33 | 25.02
2018-10-30 15:00 | 13718.6583 | 705.693 | 17.16 | 17.16 | 17.4 | 29.94 | 36.51 | 11.2 | 0.01 | 30.06
2018-10-30 16:00 | 13230.4685 | 295.809 | 17.3 | 17.3 | 19.64 | 30.78 | 38.49 | 12.46 | 2.64 | 32.35
2018-10-30 17:00 | 13009.486 | 40.1958 | 17.31 | 17.31 | 30.27 | 27.87 | 23.9 | 8.68 | 2 | 17.34
2018-10-30 18:00 | 12847.7542 | -0.048233 | 17.29 | 17.29 | 32.79 | 30.87 | 17.79 | 11.2 | 2.61 | 16.97
2018-10-30 19:00 | 14305.7491 | -0.048233 | 19.21 | 19.21 | 28.86 | 28.13 | 8.6 | 9.79 | 1 | 6.6
2018-10-30 20:00 | 12690.0542 | -0.048233 | 18.1 | 18.1 | 31.77 | 27.63 | 5.91 | 1 | 11.55 | 2.8
2018-10-30 21:00 | 13977.6441 | -0.048233 | 17.47 | 17.47 | 18 | 24.53 | 4.05 | 1 | 13.63 | 3.5
2018-10-30 22:00 | 13791.9641 | -0.048233 | 16.46 | 16.46 | 17.12 | 19.19 | 42.95 | 0.61 | 40 | 42.75
2018-10-30 23:00 | 12342.3542 | -0.048233 | 16.19 | 16.19 | 17.22 | 18.23 | 38.15 | 0.5 | 40 | 37.95
2018-10-31 | 12197.9542 | -0.048233 | 16.1 | 16.1 | 17.73 | 16.84 | 24.65 | 0.5 | 12.54 | 24.65
2018-10-31 01:00 | 12193.2042 | -0.048233 | 15.82 | 16.27 | 16.73 | 17.72 | 19 | 0.5 | 12 | 1.61
2018-10-31 02:00 | 13372.0741 | -0.048233 | 6.54 | 16.25 | 15.01 | 18.25 | 19 | 1.42 | 12 | 2
2018-10-31 03:00 | 13353.0841 | -0.048233 | 8.93 | 16.58 | 14.85 | 18.87 | 19 | 1.42 | 12 | 1.61
2018-10-31 04:00 | 12466.8042 | -0.048233 | 13.29 | 16.86 | 15.71 | 19.08 | 18 | 1.42 | 12 | 2
2018-10-31 05:00 | 13669.5042 | -0.048233 | 16.29 | 17.03 | 18.04 | 20.95 | 21.45 | 1.48 | 18.21 | 21.45
2018-10-31 06:00 | 17671.3131 | 2.0598 | 14.8 | 20.57 | 21 | 29.14 | 21.45 | 10 | 15.1 | 21.45
2018-10-31 07:00 | 19295.4594 | 179.535 | 17.43 | 20.9 | 21.19 | 27.86 | 5 | 10 | 13.46 | 3.5
2018-10-31 08:00 | 17508.1627 | 156.645 | 59.19 | 59.19 | 20.7 | 28.46 | 14 | 10 | 3.11 | 13
2018-10-31 09:00 | 17974.2992 | 240.315 | 19.01 | 20.25 | 20.7 | 29.12 | 20 | 10 | 18.59 | 19.8
2018-10-31 10:00 | 19990.9492 | 641.767 | 19.15 | 20.16 | 20.57 | 28.25 | 6.36 | 10 | 14.64 | 12.8
2018-10-31 11:00 | 18882.102 | 333.727 | -21.81 | -21.81 | 19.98 | 28.71 | 7.13 | 10 | 13.19 | 12.8
2018-10-31 12:00 | 17042.2552 | 339.216 | 19.2 | 22.32 | 19.37 | 28.61 | 8 | 9.99 | 3.5 | 5.24
2018-10-31 13:00 | 19191.4501 | 316.948 | 20.13 | 20.98 | 19.31 | 28.73 | 17 | 10 | 12.03 | 15
2018-10-31 14:00 | 16423.448 | 657.84 | 18.96 | 32.13 | 18.5 | 28.42 | 19.22 | 11.88 | 10.62 | 13.13
2018-10-31 15:00 | 15638.9655 | 624.069 | 19.02 | 21.06 | 18.85 | 30.67 | 28.81 | 11.98 | 3.5 | 17.34
2018-10-31 16:00 | 16814.2819 | 298.708 | 19.07 | 20.13 | 20.23 | 31.51 | 32 | 15 | 13.66 | 30
2018-10-31 17:00 | 16487.431 | 24.8967 | 18.92 | 19.47 | 22.26 | 33.46 | 16.48 | 10.82 | 11.83 | 11.72
2018-10-31 18:00 | 16159.3841 | -0.048233 | 19.14 | 19.55 | 22.26 | 39.56 | 29.78 | 11.2 | 20 | 29.58
2018-10-31 19:00 | 14474.1542 | -0.048233 | 17.79 | 20.63 | 21.87 | 32.37 | 42.16 | 9 | 15.12 | 41.96
2018-10-31 20:00 | 15835.4991 | -0.048233 | 18.73 | 19.82 | 20.72 | 26.55 | 22.4 | 1 | 17.98 | 20.4
2018-10-31 21:00 | 15607.6191 | -0.048233 | 19.08 | 19.83 | 20.62 | 26.19 | 6 | 1 | 36.48 | 3.5
2018-10-31 22:00 | 13591.6042 | -0.048233 | 18.76 | 23.6 | 18.68 | 22.07 | 35.22 | 0.5 | 54.4162 | 35.02
2018-10-31 23:00 | 13366.4542 | -0.048233 | 18.69 | 20.5 | 18.59 | 22.75 | 28 | 0.5 | 30 | 27.8
2018-11-01 | 14546.2891 | -0.048233 | 13.35 | 18.73 | 19.38 | 19.15 | 35 | 0.5 | 13.35 | 12
2018-11-01 01:00 | 14489.3191 | -0.048233 | 15.48 | 19.74 | 19.38 | 17.59 | 29.71 | 0.5 | 8.74 | 2.11
2018-11-01 02:00 | 12981.7042 | -0.048233 | 13.19 | 17.77 | 19.2 | 16.87 | 29.71 | 2 | 10 | 2.11
2018-11-01 03:00 | 14333.1791 | -0.048233 | 14.43 | 17.05 | 18.98 | 15.55 | 29.71 | 2 | 8.45 | 2.61
2018-11-01 04:00 | 13030.1542 | -0.048233 | 15.41 | 17.52 | 18.97 | 16.28 | 28.83 | 1.75 | 11.6 | 3.78
2018-11-01 05:00 | 14136.9042 | -0.048233 | 42.67 | 18.2 | 20.21 | 18.35 | 45 | 1.49 | 26.18 | 47.9
2018-11-01 06:00 | 16529.3146 | 1.2785 | 17.67 | 18.18 | 21.38 | 28.03 | 25.85 | 18 | 17.71 | 26.75
2018-11-01 07:00 | 21003.2122 | 183.258 | 17.71 | 20.51 | 21.13 | 27.72 | 33.53 | 10 | 8.18 | 33.53
2018-11-01 08:00 | 19666.1041 | 494.857 | 18.61 | 18.61 | 21.57 | 26.46 | 20 | 10.07 | 3.01 | 3
2018-11-01 09:00 | 18554.3312 | 823.875 | 19.18 | 19.18 | 21.65 | 27.83 | 20 | 10.08 | 1.04 | 4.05
2018-11-01 10:00 | 18631.3183 | 668.914 | 19.99 | 21.62 | 20.46 | 27.89 | 20 | 6 | 2.75 | 5.8
2018-11-01 11:00 | 20904.2236 | 1086.43 | 20.13 | 20.49 | 19.95 | 30.64 | 22 | 8 | 3.5 | 5.14
2018-11-01 12:00 | 20763.2756 | 1021.83 | 19.42 | 21.02 | 19.3 | 31.89 | 22 | 9.22 | 1 | 10.22
2018-11-01 13:00 | 18817.0205 | 1079.39 | 19.75 | 21.17 | 18.85 | 36.69 | 22.79 | 10.01 | 1 | 11.8
2018-11-01 14:00 | 17517.6314 | 859.612 | 19.43 | 19.6 | 17.03 | 34.12 | 24.38 | 8.5 | 2.31 | 13.47
2018-11-01 15:00 | 16427.608 | 614.219 | 19.36 | 19.36 | 18.19 | 36.53 | 29.92 | 9.34 | 1 | 19.96
2018-11-01 16:00 | 16034.9768 | 348.923 | 62.82 | 20.51 | 19.95 | 36.38 | 28.03 | 10.01 | 0.71 | 18.33
2018-11-01 17:00 | 15704.5244 | 29.0783 | 19.99 | 19.99 | 23.04 | 39.11 | 22 | 10.82 | 0.61 | 20.51
2018-11-01 18:00 | 17183.7891 | -0.048233 | 18.43 | 18.43 | 22.24 | 36.72 | 24.67 | 10.82 | 2.13 | 24.47
2018-11-01 19:00 | 17439.0991 | -0.048233 | 20.39 | 21.24 | 21.72 | 29.84 | 24.49 | 22.31 | 3.5 | 22.71
2018-11-01 20:00 | 15362.4042 | -0.048233 | 18 | 18 | 20.99 | 25.64 | 15.16 | 12.71 | 2.31 | 2.11
2018-11-01 21:00 | 14953.9042 | -0.048233 | 17.5 | 17.5 | 19.98 | 24.06 | 20 | 7.55 | 3.98 | 5
2018-11-01 22:00 | 14271.8042 | -0.048233 | 17.52 | 17.52 | 17.36 | 22.82 | 40 | 0.5 | 35 | 22
2018-11-01 23:00 | 15370.2441 | -0.048233 | 16.12 | 18.15 | 17.36 | 22.69 | 37.63 | 0.5 | 26.37 | 16.5
2018-11-02 | 13604.9042 | -0.048233 | 13.42 | 18.12 | 12.49 | 17.25 | 24.75 | 0.5 | 27.04 | 2.01
2018-11-02 01:00 | 13346.5042 | -0.048233 | 13.9 | 14.12 | 11.19 | 14.22 | 24.75 | 0.5 | 14.82 | 0.55
2018-11-02 02:00 | 13357.9042 | -0.048233 | 12.77 | 16.95 | 10.19 | 10.5 | 24.75 | 6.9 | 20.05 | 0.73
2018-11-02 03:00 | 13217.3042 | -0.048233 | 11.62 | 16.06 | 8.34 | 13.23 | 24.75 | 2 | 3.5 | 1
2018-11-02 04:00 | 15114.9341 | -0.048233 | 11.98 | 17.84 | 10.5 | 15.56 | 24.75 | 2.18 | 16.89 | 2.01
2018-11-02 05:00 | 16225.8491 | -0.048233 | 13.18 | 15.03 | 13.11 | 18.85 | 24 | 2.16 | 30 | 27
2018-11-02 06:00 | 16586.0042 | -0.048233 | 15.79 | 20.62 | 14.3 | 22.33 | 18.45 | 15.75 | 9.5 | 22.62
2018-11-02 07:00 | 17587.4074 | 76.0604 | 17.74 | 23.75 | 17.17 | 22.38 | 18.45 | 10.15 | 3.5 | 18.45
2018-11-02 08:00 | 19991.4113 | 100.205 | 18.44 | 19.7 | 17.56 | 22.29 | 5.06 | 11.54 | 2.14 | 3
2018-11-02 09:00 | 18468.266 | 449.28 | 19.73 | 21.05 | 17.76 | 21.77 | 13.04 | 12.83 | 1 | 5.04
2018-11-02 10:00 | 21199.8041 | 720.601 | 138.6 | 138.6 | 17.56 | 25.52 | 14 | 8 | 2.31 | 12
2018-11-02 11:00 | 21379.4473 | 721.879 | 19.66 | 22.92 | 17.89 | 27.82 | 8.44 | 7.86 | 2.61 | 7.04
2018-11-02 12:00 | 20849.1655 | 1099.49 | 20 | 20.59 | 15.13 | 35.43 | 8.88 | 10 | 1 | 5.98
2018-11-02 13:00 | 22620.4734 | 983.207 | 21.82 | 22.18 | 15 | 46.47 | 14.05 | 10 | 1 | 9.93
2018-11-02 14:00 | 17769.1211 | 544.338 | 27.73 | 26.26 | 14.86 | 63.22 | 15 | 10.01 | 2.11 | 10.41
2018-11-02 15:00 | 18320.6901 | 262.583 | 30.08 | 30.08 | 14.99 | 74.83 | 26.99 | 10.01 | 1 | 20.23
2018-11-02 16:00 | 17842.8595 | 203.663 | 27.7 | 27.7 | 32.24 | 79.59 | 33.49 | 19.36 | 1 | 28.49
2018-11-02 17:00 | 17601.4796 | 12.8669 | 20.77 | 28.73 | 40.2 | 50.64 | 19.69 | 16.68 | 1 | 18.77
2018-11-02 18:00 | 17285.0691 | -0.048233 | 44.63 | 44.63 | 37.12 | 39.57 | 25.97 | 22.71 | 2.11 | 25.77
2018-11-02 19:00 | 15605.6042 | -0.048233 | 18.03 | 27.97 | 30.5 | 33.66 | 17.2 | 16.6 | 3.32 | 17
2018-11-02 20:00 | 15242.7042 | -0.048233 | 17.31 | 27.53 | 16.69 | 29.82 | 8.42 | 9.22 | 2.31 | 3.7
2018-11-02 21:00 | 16645.7391 | -0.048233 | 15.28 | 28.85 | 12.35 | 27.7 | 8 | 8.06 | 4.39 | 3.94
2018-11-02 22:00 | 15924.1191 | -0.048233 | 16.33 | 26.73 | 10.28 | 25.65 | 20 | 0.5 | 22.56 | 19.8
2018-11-02 23:00 | 13735.0542 | -0.048233 | 12.33 | 22.27 | 10.93 | 21.38 | 28 | 0.5 | 30 | 22.35
2018-11-03 | 15050.5791 | -0.048233 | 3.66 | 20.57 | 8.07 | 23.21 | 3 | 0.5 | 10 | 13.77
2018-11-03 01:00 | 13327.5042 | -0.048233 | 3.01 | 19.84 | 5.97 | 22.12 | 2.51 | 0.5 | 11.69 | 2.09
2018-11-03 02:00 | 14737.2441 | -0.048233 | 3.86 | 19.51 | 5.05 | 21.56 | 2.38 | 1.78 | 2.99 | 2
2018-11-03 03:00 | 14589.5441 | -0.048233 | 1.83 | 19.45 | 4.56 | 20.3 | 2.37 | 1.79 | 2.11 | 2.1
2018-11-03 04:00 | 13358.8542 | -0.048233 | 7.71 | 19.41 | 4.66 | 20.12 | 2.51 | 2.21 | 2.99 | 2.51
2018-11-03 05:00 | 14329.7542 | -0.048233 | 8.01 | 29.02 | 6.38 | 21.15 | 4.01 | 2.54 | 12.6 | 14.93
2018-11-03 06:00 | 18181.6478 | 0.78936 | 60.18 | 60.18 | 12.39 | 28.97 | 25 | 24.99 | 9.86 | 25
2018-11-03 07:00 | 19265.7295 | 124.355 | 13.55 | 27.41 | 13.49 | 29.55 | 15.45 | 12 | 1 | 15.45
2018-11-03 08:00 | 17609.7605 | 303.59 | 17.06 | 24.37 | 12.52 | 28.68 | 5.04 | 12 | 1 | 2.8
2018-11-03 09:00 | 20584.0902 | 681.986 | 18.61 | 27.31 | 14.69 | 29.23 | 7.75 | 12 | 1 | 4.81
2018-11-03 10:00 | 20549.2668 | 508.978 | 18.29 | 24.17 | 15.69 | 33.12 | 7.61 | 8 | 1 | 5.24
2018-11-03 11:00 | 18789.385 | 1091.3 | 18.97 | 24.17 | 14.69 | 45.41 | 8.11 | 10 | 2 | 6.26
2018-11-03 12:00 | 18804.4995 | 625.21 | 17.92 | 24.56 | 13.95 | 60 | 12.77 | 12.56 | 1 | 10.28
2018-11-03 13:00 | 18477.3043 | 654.794 | 34.86 | 25.58 | 13.99 | 73.04 | 16.99 | 20.82 | 1 | 16.21
2018-11-03 14:00 | 17651.7533 | 818.793 | 18.86 | 25.48 | 13.73 | 83.7 | 23.72 | 18.73 | 1 | 18.73
2018-11-03 15:00 | 18672.407 | 655.964 | 19.46 | 25.62 | 13.95 | 94.66 | 31.52 | 25 | 1 | 26.52
2018-11-03 16:00 | 17754.9347 | 251.322 | 19.15 | 25.62 | 15.03 | 82.7 | 34.6 | 21 | 1 | 29.6
2018-11-03 17:00 | 15572.2708 | 28.864 | 18.96 | 22.23 | 35.62 | 41.75 | 17.5 | 13.15 | 0.61 | 17.05
2018-11-03 18:00 | 15194.2542 | -0.048233 | 18.56 | 21.05 | 33.08 | 32.12 | 17.67 | 10.25 | 2.11 | 16.04
2018-11-03 19:00 | 16729.0841 | -0.048233 | 17.26 | 21.69 | 14.49 | 31.54 | 9 | 11.52 | 2 | 3.7
2018-11-03 20:00 | 14706.9042 | -0.048233 | 16 | 20.38 | 12.6 | 27.47 | 6.7 | 8.6 | 2.56 | 3.44
2018-11-03 21:00 | 14405.7542 | -0.048233 | 16.86 | 20.22 | 11.15 | 26.28 | 7.4 | 7.9 | 3.5 | 6.34
2018-11-03 22:00 | 13986.8042 | -0.048233 | 19.2 | 19.2 | 9.16 | 25.32 | 6.07 | 0.5 | 17.5 | 3.23
2018-11-03 23:00 | 15003.1041 | -0.048233 | 14.79 | 17.58 | 9.59 | 23.17 | 16.5 | 0.5 | 20 | 16.5
2018-11-04 | 14723.5291 | -0.048233 | 11.31 | 17.64 | 8.83 | 22.08 | 2.3 | 0.5 | 11.78 | 2.1
2018-11-04 01:00 | 14575.8291 | -0.048233 | 9.35 | 17.68 | 6.5 | 18.97 | 2.11 | 0.5 | 11.45 | 1
2018-11-04 02:00 | 12919.0042 | -0.048233 | 7.31 | 16.96 | 5.68 | 16.48 | 2.1 | 1.7 | 9.3 | 1
2018-11-04 03:00 | 12754.6542 | -0.048233 | 4.84 | 16.46 | 4.66 | 14.75 | 2.1 | 1.63 | 2.19 | 1
2018-11-04 04:00 | 12914.2542 | -0.048233 | 10.1 | 16.52 | 5.77 | 17.89 | 2.11 | 1.9 | 8.53 | 1.91
2018-11-04 05:00 | 14038.1042 | -0.048233 | 16.87 | 17.38 | 6.35 | 18.64 | 4.28 | 2.31 | 30 | 23.62
2018-11-04 06:00 | 17749.2691 | -0.048233 | 15.48 | 17.49 | 7.4 | 20.09 | 6.64 | 11.75 | 23.22 | 40
2018-11-04 07:00 | 17163.432 | 45.7705 | 14.87 | 17.82 | 9.95 | 21.54 | 4.77 | 10.12 | 1 | 3.19
2018-11-04 08:00 | 19649.5712 | 140.186 | 17.35 | 17.81 | 15.59 | 23.34 | 4.08 | 10.02 | 1 | 3
2018-11-04 09:00 | 17856.2029 | 650.003 | 17.73 | 21.8 | 15.68 | 25.08 | 5.13 | 10 | 1 | 3.57
2018-11-04 10:00 | 18558.9663 | 633.754 | 18.3 | 20.23 | 17.54 | 27.18 | 5.14 | 7.46 | 1 | 3.71
2018-11-04 11:00 | 17620.9667 | 724.386 | 17.64 | 22.92 | 17.03 | 29.22 | 7.71 | 7.9 | 2.11 | 5.66
2018-11-04 12:00 | 21633.2519 | 922.452 | 18.25 | 23.33 | 16.68 | 35.17 | 8 | 7.79 | 1 | 6.68
2018-11-04 13:00 | 19706.1984 | 776.861 | 19.44 | 29.42 | 15.66 | 38.95 | 35.43 | 58.7373 | 1 | 35.43
2018-11-04 14:00 | 16649.9337 | 904.246 | 18.29 | 28.87 | 15.12 | 44.21 | 20.22 | 13.55 | 1 | 14
2018-11-04 15:00 | 15565.73 | 546.979 | 46.56 | 46.56 | 15.53 | 53.26 | 24.32 | 9.03 | 1 | 16.83
2018-11-04 16:00 | 16612.2399 | 228.199 | 17.4 | 32.21 | 17.06 | 54.81 | 28.12 | 9.9 | 1 | 21.9
2018-11-04 17:00 | 14489.3257 | 21.9218 | 354.7857 | 310.46 | 32.37 | 36.04 | 12.6 | 10.5 | 0.25 | 11.94
2018-11-04 18:00 | 14132.1542 | -0.048233 | 19.49 | 30.97 | 30.62 | 34.1 | 17.55 | 16.65 | 1 | 17.55
2018-11-04 19:00 | 13982.0542 | -0.048233 | 329.2757 | 284.95 | 18.06 | 27.94 | 12.73 | 12.52 | 2.31 | 3.8
2018-11-04 20:00 | 15111.7691 | -0.048233 | 17.64 | 26.5 | 16.52 | 26.84 | 6.62 | 8.25 | 2.35 | 3.1
2018-11-04 21:00 | 14804.7641 | -0.048233 | 18.44 | 22.77 | 15.03 | 25.66 | 5.52 | 8 | 3.5 | 3.67
2018-11-04 22:00 | 14367.9941 | -0.048233 | 19.37 | 20.72 | 12.6 | 24.78 | 5.42 | 0.5 | 28.99 | 2.2
2018-11-04 23:00 | 12607.4042 | -0.048233 | 12.6 | 18.51 | 9.9 | 23.41 | 4.22 | 0.5 | 26.19 | 2.2
2018-11-05 | 12350.9042 | -0.048233 | 11.56 | 18.1 | 7.65 | 20.06 | 3.54 | 0.5 | 10.51 | 2.21
2018-11-05 01:00 | 13634.7691 | -0.048233 | 13.01 | 16.84 | 9.24 | 15.19 | 2.3 | 0.5 | 10.71 | 0.9
2018-11-05 02:00 | 13594.6791 | -0.048233 | 12.86 | 16.42 | 6.83 | 16.2 | 2.11 | 1.63 | 9.61 | 0.9
2018-11-05 03:00 | 13638.9891 | -0.048233 | 14.61 | 16.22 | 8.33 | 15.34 | 2.11 | 1.48 | 10.14 | 0.9
2018-11-05 04:00 | 13670.6391 | -0.048233 | 15.74 | 16.27 | 10.82 | 16.49 | 2.11 | 1.48 | 10.14 | 1
2018-11-05 05:00 | 14094.7491 | -0.048233 | 15.95 | 16.47 | 8.61 | 16.97 | 3 | 1.55 | 10.14 | 2.61
2018-11-05 06:00 | 14471.3841 | -0.048233 | 16.91 | 16.91 | 7.96 | 17.65 | 4.21 | 2.5 | 35 | 26.13
2018-11-05 07:00 | 14428.115 | 40.9384 | 17.47 | 17.47 | 8.06 | 18.34 | 4.2 | 10.2 | 35 | 40
2018-11-05 08:00 | 14326.7386 | 100.847 | 18.17 | 19.02 | 14.26 | 20.63 | 5.14 | 7.94 | 3.01 | 3.11
2018-11-05 09:00 | 13542.4352 | 675.195 | 184.76 | 184.76 | 17.06 | 23.54 | 7.48 | 7.94 | 3.46 | 4.5
2018-11-05 10:00 | 14059.1678 | 932.124 | 19.98 | 22.6 | 14.5 | 25.48 | 7 | 7.5 | 1 | 5.06
2018-11-05 11:00 | 14044.3725 | 1014.55 | 20.01 | 23.39 | 13.98 | 27.89 | 5.05 | 7.75 | 3.28 | 4.7
2018-11-05 12:00 | 14127.127 | 1005.66 | 20.45 | 23.35 | 11.89 | 33.23 | 7.41 | 7.27 | 1 | 4.94
2018-11-05 13:00 | 14201.93 | 1045.4 | 39.34 | 38.73 | 11.53 | 39.26 | 17.55 | 10.01 | 2.31 | 3.36
2018-11-05 14:00 | 15001.3077 | 485.249 | 33.05 | 33.05 | 11.55 | 53.91 | 29.24 | 9.89 | 1 | 15.99
2018-11-05 15:00 | 13449.3219 | 379.181 | 20.32 | 32.96 | 13.13 | 68.1 | 30.95 | 10 | 2 | 17.19
2018-11-05 16:00 | 12941.793 | 124.94 | 55.68 | 55.68 | 16.65 | 57.36 | 34.93 | 10.25 | 2.11 | 20.96
2018-11-05 17:00 | 12878.252 | 11.0547 | 51.03 | 51.03 | 23.58 | 40.74 | 28.61 | 10.82 | 1 | 22.29
2018-11-05 18:00 | 12843.9542 | -0.048233 | 42.27 | 42.27 | 23.1 | 34.2 | 26.63 | 12.9 | 1 | 26.43
2018-11-05 19:00 | 14289.9241 | -0.048233 | 20.22 | 26.19 | 17.87 | 30.17 | 14.01 | 10.5 | 2.11 | 3.35
2018-11-05 20:00 | 12632.1042 | -0.048233 | 19.67 | 27.69 | 12.79 | 27.87 | 6.62 | 8.87 | 2 | 3
2018-11-05 21:00 | 12461.1042 | -0.048233 | 19.49 | 23.41 | 11.76 | 25.35 | 5.87 | 7.55 | 3.5 | 3.2
2018-11-05 22:00 | 12387.0042 | -0.048233 | 18.5 | 19.29 | 7.63 | 25.04 | 5.98 | 0.5 | 9.11 | 2
2018-11-05 23:00 | 13646.3741 | -0.048233 | 18.3 | 18.3 | 6.02 | 21.49 | 6.44 | 0.5 | 19.96 | 2
2018-11-06 | 13338.3141 | -0.048233 | 17.39 | 18.53 | 10.29 | 19.29 | 7.55 | 0.5 | 20.27 | 2
2018-11-06 01:00 | 11931.9542 | -0.048233 | 16.62 | 18.41 | 7.55 | 19.12 | 4 | 0.5 | 11.81 | 1
2018-11-06 02:00 | 13064.0141 | -0.048233 | 15.76 | 17.87 | 9.63 | 19.01 | 3.01 | 0.97 | 4 | 1
2018-11-06 03:00 | 12986.9991 | -0.048233 | 15.21 | 18.35 | 6.58 | 19.13 | 6.21 | 1.49 | 3.5 | 1.01
2018-11-06 04:00 | 11526.3042 | -0.048233 | 15.36 | 19.2 | 6.63 | 19.66 | 5.75 | 1.58 | 4 | 1
2018-11-06 05:00 | 12803.4291 | -0.048233 | 17.36 | 19.76 | 7.37 | 20.86 | 5.75 | 1.62 | 4 | 1.9
2018-11-06 06:00 | 11624.1542 | -0.048233 | 17.25 | 20.14 | 9.67 | 26.45 | 8 | 2 | 23.33 | 20
2018-11-06 07:00 | 13049.8035 | 142.482 | 17.44 | 21.56 | 12.58 | 25.71 | 7.75 | 10 | 23 | 18.53
2018-11-06 08:00 | 13349.8075 | 484.846 | 19.79 | 22.24 | 14.2 | 28.58 | 7.75 | 7.6 | 1 | 2.21
2018-11-06 09:00 | 12268.7018 | 805.423 | 20.25 | 20.25 | 14.27 | 30.56 | 5 | 9.55 | 0.25 | 3
2018-11-06 10:00 | 14269.086 | 1024.2 | 20.4 | 20.4 | 14.11 | 34.5 | 4.18 | 10 | 1 | 2.51
2018-11-06 11:00 | 14421.0165 | 1143.21 | 21.5 | 22.82 | 13.82 | 50.88 | 5 | 6.94 | 2.11 | 3
2018-11-06 12:00 | 14332.8607 | 1158.65 | 50.47 | 50.47 | 13.22 | 61.84 | 21.32 | 10 | 1 | 3.85
2018-11-06 13:00 | 12886.1506 | 965.369 | 42.9 | 42.9 | 13.18 | 81.83 | 23.6 | 14.61 | 1 | 15.21
2018-11-06 14:00 | 12867.1069 | 858.323 | 44.69 | 44.69 | 13.19 | 99.02 | 40.62 | 25 | 1 | 4.27
2018-11-06 15:00 | 13989.4646 | 431.156 | 32.04 | 32.04 | 14.09 | 109.23 | 52.09 | 20 | 1 | 12
2018-11-06 16:00 | 12547.0158 | 187.385 | 21.91 | 24.83 | 20.78 | 91.34 | 91.7041 | 60.1973 | 1 | 14.74
2018-11-06 17:00 | 13729.0639 | 13.3307 | 22.1 | 22.1 | 22.29 | 55.64 | 82.1141 | 27.75 | 1 | 30.95
2018-11-06 18:00 | 12574.1542 | -0.048233 | 22.77 | 22.77 | 21.79 | 52.66 | 32.9 | 18.52 | 1.99 | 24.86
2018-11-06 19:00 | 12442.1042 | -0.048233 | 21.75 | 21.75 | 21.57 | 40.29 | 30.47 | 19.58 | 2.42 | 12.88
2018-11-06 20:00 | 12367.0542 | -0.048233 | 19.93 | 21.35 | 20.07 | 31.78 | 17.82 | 10 | 2.11 | 3.1
2018-11-06 21:00 | 12365.1542 | -0.048233 | 19.36 | 21.24 | 15.75 | 29.55 | 6 | 8.11 | 2.31 | 3
2018-11-06 22:00 | 13492.3441 | -0.048233 | 15.53 | 20.69 | 15.91 | 25.9 | 5 | 9.81 | 9.11 | 3.2
2018-11-06 23:00 | 13177.9541 | -0.048233 | 15.82 | 19.27 | 13.33 | 22.56 | 15 | 0.5 | 14.08 | 15
2018-11-07 | 13033.4191 | -0.048233 | 397.3657 | 19.05 | 14.84 | 21.45 | 14.72 | 0.5 | 26.19 | 12.8
2018-11-07 01:00 | 12808.7041 | -0.048233 | 14.16 | 19.16 | 14.08 | 20.14 | 3.11 | 0.5 | 10 | 2
2018-11-07 02:00 | 12936.3591 | -0.048233 | 13.99 | 18.74 | 13.58 | 19.52 | 3.11 | 0.5 | 4 | 1.01
2018-11-07 03:00 | 11676.4042 | -0.048233 | 14.32 | 18.38 | 14.24 | 19.6 | 5 | 2.5 | 3.98 | 1.07
2018-11-07 04:00 | 13300.3341 | -0.048233 | 14.85 | 18.63 | 15.1 | 19.68 | 5 | 2.5 | 4.85 | 1.33
2018-11-07 05:00 | 13065.3042 | -0.048233 | 15.83 | 19.43 | 17.36 | 21.62 | 5 | 2.5 | 5 | 2
2018-11-07 06:00 | 16884.8971 | 0.64184 | 18.86 | 18.9 | 20.1 | 26.53 | 5 | 2.5 | 27.4 | 24.62
2018-11-07 07:00 | 16466.7642 | 125.436 | 19.03 | 19.24 | 20.5 | 24.45 | 7.44 | 8.58 | 13.22 | 20.56
2018-11-07 08:00 | 19087.4282 | 106.349 | 19.32 | 19.32 | 21.31 | 26.2 | 5 | 6.41 | 2.25 | 2.41
2018-11-07 09:00 | 19360.3852 | 176.076 | 19.05 | 19.05 | 22.85 | 30.35 | 6.4 | 7.5 | 2.5 | 4.71
2018-11-07 10:00 | 19219.9235 | 226.937 | 316.0557 | 20.33 | 24.82 | 33.37 | 7.41 | 8.41 | 2.14 | 5.83
2018-11-07 11:00 | 18812.5226 | 255.775 | 18.37 | 21.3 | 19.75 | 42.21 | 8 | 8.69 | 2.11 | 5.76
2018-11-07 12:00 | 17895.3733 | 260.235 | 17.52 | 21.97 | 19.78 | 55.36 | 9.11 | 10.48 | 1 | 5.13
2018-11-07 13:00 | 20137.2703 | 560.46 | 17.11 | 22.53 | 19.8 | 61.94 | 12.09 | 10.07 | 2 | 5.84
2018-11-07 14:00 | 18471.6722 | 566.694 | 16.96 | 22.89 | 17.41 | 67.85 | 14.91 | 13.28 | 2 | 9.99
2018-11-07 15:00 | 17260.2083 | 428.387 | 16.91 | 22.61 | 19.85 | 57.16 | 21.75 | 6.03 | 1 | 11.75
2018-11-07 16:00 | 16473.1783 | 239.387 | 17.04 | 21.32 | 30.47 | 42.97 | 19.02 | 7.56 | 1 | 6.17
2018-11-07 17:00 | 15959.125 | 19.1327 | 18.42 | 21.16 | 37.93 | 37.89 | 12 | 8.44 | 1 | 5.5
2018-11-07 18:00 | 14216.7042 | -0.048233 | 21.88 | 21.88 | 31.86 | 35.68 | 30.99 | 15 | 3.11 | 28.54
2018-11-07 19:00 | 14000.1042 | -0.048233 | 19.44 | 21.54 | 24.45 | 34.21 | 15.32 | 10.62 | 10 | 11.62
2018-11-07 20:00 | 15252.0841 | -0.048233 | 18.79 | 20.23 | 22.46 | 30.67 | 8.99 | 8.05 | 3.5 | 4.88
2018-11-07 21:00 | 15101.2191 | -0.048233 | 18.05 | 19.85 | 19.69 | 27.8 | 6.74 | 6.7 | 10.78 | 3.32
2018-11-07 22:00 | 14531.5191 | -0.048233 | 17.7 | 18.77 | 18.2 | 24.99 | 5.31 | 2.99 | 18.64 | 3.4
2018-11-07 23:00 | 12715.7042 | -0.048233 | 17.12 | 18.6 | 16.06 | 24.33 | 4.81 | 0.5 | 20 | 13.5
2018-11-08 | 12574.1542 | -0.048233 | 15.88 | 18.52 | 16.72 | 20.71 | 5 | 0.5 | 26.95 | 2.11
2018-11-08 01:00 | 12402.2042 | -0.048233 | 15.44 | 17.46 | 16.12 | 20.37 | 2.35 | 0.5 | 3.5 | 2.11
2018-11-08 02:00 | 12477.2542 | -0.048233 | 14.99 | 16.76 | 15.04 | 20.05 | 2.35 | 0.5 | 3.4 | 0.83
2018-11-08 03:00 | 12320.5042 | -0.048233 | 14.57 | 16.43 | 15.31 | 20.02 | 3.37 | 1.52 | 3.98 | 0.87
2018-11-08 04:00 | 14053.6041 | -0.048233 | 14.26 | 16.65 | 16.25 | 19.94 | 3.48 | 1.52 | 3.5 | 1.01
2018-11-08 05:00 | 13771.1542 | -0.048233 | 14.89 | 16.83 | 16.94 | 21.01 | 3.11 | 1.52 | 4.65 | 1.98
2018-11-08 06:00 | 18413.9191 | -0.048233 | 15.26 | 18.38 | 21.62 | 29.69 | 4.21 | 1.62 | 13.46 | 13.42
2018-11-08 07:00 | 17335.3155 | 99.7005 | 15.39 | 19.29 | 21.47 | 24.34 | 25 | 19.99 | 12 | 25
2018-11-08 08:00 | 20573.4516 | 425.902 | 15.64 | 19.67 | 19.67 | 24.78 | 5 | 6.99 | 2.25 | 2.15
2018-11-08 09:00 | 18917.483 | 674.14 | 16.52 | 20.61 | 19.2 | 27.32 | 5.18 | 7.5 | 1.28 | 2
2018-11-08 10:00 | 17606.5571 | 976.218 | 16.68 | 21.23 | 30.92 | 28.55 | 7.17 | 7.5 | 1 | 2.06
2018-11-08 11:00 | 17444.5365 | 1082.67 | 17.41 | 22.33 | 30.49 | 29.68 | 8.11 | 25 | 2 | 3.5
2018-11-08 12:00 | 17299.158 | 1039.64 | 17.55 | 21.51 | 18.27 | 30.72 | 8.11 | 15.5 | 1 | 3.07
2018-11-08 13:00 | 16956.702 | 1037.16 | 18.22 | 21.43 | 16.68 | 30.47 | 15 | 17.5 | 1 | 2
2018-11-08 14:00 | 15519.295 | 831.1 | 18.13 | 19.3 | 16.16 | 27.6 | 7.7 | 23.9 | 0.27 | 2.11
2018-11-08 15:00 | 14550.6598 | 499.484 | 13.85 | 13.85 | 17.17 | 28.33 | 6.99 | 2 | 1 | 2.65
2018-11-08 16:00 | 13795.2625 | 302.329 | 9.78 | 9.78 | 32.05 | 28.62 | 8 | 7.4 | 0.53 | 2.32
2018-11-08 17:00 | 13327.7018 | 19.1598 | 10.83 | 10.83 | 38.84 | 45.41 | 8.93 | 8.62 | 1 | 3.61
2018-11-08 18:00 | 13116.6042 | -0.048233 | 21.94 | 21.94 | 33.76 | 45.02 | 30.78 | 16.57 | 1 | 30.58
2018-11-08 19:00 | 14538.9041 | -0.048233 | 20.6 | 20.6 | 29.92 | 34.6 | 23.08 | 15.67 | 2 | 20.78
2018-11-08 20:00 | 14064.1541 | -0.048233 | 19.39 | 27.74 | 28.52 | 27.8 | 6.28 | 9.22 | 20 | 3.11
2018-11-08 21:00 | 13931.2241 | -0.048233 | 17.92 | 23.95 | 17.24 | 26.49 | 5.47 | 2 | 2 | 2.54
2018-11-08 22:00 | 13292.9491 | -0.048233 | 16.85 | 19.81 | 16.49 | 24.21 | 4.67 | 2 | 3.01 | 3.01
2018-11-08 23:00 | 12997.5491 | -0.048233 | 16.3 | 18.94 | 15.4 | 22.66 | 4.06 | 0.5 | 15.02 | 2.2
2018-11-09 | 11750.5042 | -0.048233 | 15.04 | 17.97 | 14.89 | 19.72 | 8 | 0.5 | 12 | 2
2018-11-09 01:00 | 11569.0542 | -0.048233 | 14.02 | 17.67 | 14.17 | 19.17 | 4.25 | 0.5 | 9.67 | 1.01
2018-11-09 02:00 | 11461.7042 | -0.048233 | 13.08 | 17.42 | 13.31 | 18.92 | 4.25 | 0.61 | 1.95 | 0.49
2018-11-09 03:00 | 11437.0042 | -0.048233 | 11.95 | 17.7 | 13.92 | 19.13 | 3.41 | 1.07 | 3.11 | 0.01
2018-11-09 04:00 | 13047.1341 | -0.048233 | 12.67 | 13.38 | 14.88 | 19.39 | 3.41 | 1.07 | 0.01 | 1
2018-11-09 05:00 | 14092.6391 | -0.048233 | 16.08 | 18.7 | 16.02 | 23.63 | 3.41 | 1.22 | 1.18 | 1.48
2018-11-09 06:00 | 16214.2441 | -0.048233 | 17.62 | 17.62 | 31.73 | 46.3 | 6.5 | 2.99 | 12 | 16.29
2018-11-09 07:00 | 15575.4115 | 112.17 | 43.4 | 43.4 | 31.55 | 34.64 | 30.21 | 22.03 | 2.08 | 30.21
2018-11-09 08:00 | 17537.0097 | 440.758 | 40.3 | 40.3 | 30.13 | 32.56 | 13.12 | 10 | 1 | 2.21
2018-11-09 09:00 | 16374.1981 | 734.998 | 19.13 | 28.03 | 22.5 | 30.17 | 8.11 | 9.5 | 0.3 | 11.07
2018-11-09 10:00 | 17216.318 | 1000.44 | 18.73 | 26.35 | 24.77 | 28.01 | 8.11 | 8.61 | 0.73 | 3.11
2018-11-09 11:00 | 18498.3489 | 1061.98 | 19.07 | 23.6 | 23.74 | 26.41 | 7.63 | 8.64 | 1 | 5
2018-11-09 12:00 | 19009.4647 | 1046.45 | 19.02 | 20.58 | 19.21 | 25.85 | 6 | 9.63 | 1 | 2.93
2018-11-09 13:00 | 19701.8138 | 957.705 | 19.25 | 20.25 | 18.7 | 25.03 | 15 | 14.79 | 0.32 | 2
2018-11-09 14:00 | 16533.7712 | 822.821 | 18.79 | 19.98 | 18.31 | 24.29 | 17.71 | 17.5 | 0.4 | 3.17
2018-11-09 15:00 | 15473.512 | 560.836 | 18.72 | 19.44 | 18.39 | 24.22 | 5.56 | 6.23 | 0.57 | 2.61
2018-11-09 16:00 | 15086.7543 | 250.241 | 18.49 | 19.45 | 31.81 | 25.91 | 5.05 | 7.74 | 0.57 | 2
2018-11-09 17:00 | 14750.5393 | 8.5539 | 18.5 | 20.01 | 45.07 | 39.75 | 5.79 | 8 | 0.77 | 4.5
2018-11-09 18:00 | 12998.8042 | -0.048233 | 19.37 | 20.98 | 39.12 | 38.09 | 38.21 | 17.5 | 1.17 | 36.21
2018-11-09 19:00 | 12878.1542 | -0.048233 | 20.15 | 20.15 | 33.56 | 28.21 | 25.83 | 15.23 | 2 | 16.15
2018-11-09 20:00 | 12585.5542 | -0.048233 | 19.71 | 20.05 | 31.13 | 28.97 | 14.48 | 8 | 1.88 | 5
2018-11-09 21:00 | 12416.4542 | -0.048233 | 19.49 | 24.72 | 19.98 | 28.6 | 6.19 | 7.7 | 2 | 4.06
2018-11-09 22:00 | 11951.9042 | -0.048233 | 17.79 | 19.32 | 16.93 | 24.43 | 6.7 | 2 | 19.15 | 3.6
2018-11-09 23:00 | 11711.5542 | -0.048233 | 17.08 | 18.44 | 15.86 | 23.46 | 16.89 | 0.61 | 20 | 16.88
2018-11-10 | 12802.3741 | -0.048233 | 15.45 | 17.26 | 17.79 | 21.13 | 8.11 | 0.61 | 14.34 | 2
2018-11-10 01:00 | 11423.7042 | -0.048233 | 12.95 | 16.95 | 16.1 | 20.65 | 4.47 | 0.61 | 17.51 | 1.01
2018-11-10 02:00 | 11443.6542 | -0.048233 | 13.57 | 17.11 | 16.04 | 20.37 | 3 | 0.61 | 1.38 | 0.32
2018-11-10 03:00 | 12803.4291 | -0.048233 | 13.22 | 17.35 | 14.28 | 20.46 | 3.69 | 1.06 | 2.11 | 0.01
2018-11-10 04:00 | 13003.8791 | -0.048233 | 13.26 | 17.86 | 16.08 | 20.56 | 3 | 1.05 | 1 | 0.7
2018-11-10 05:00 | 13845.7691 | -0.048233 | 14.91 | 18.49 | 20.02 | 22.7 | 3.09 | 1.49 | 2.36 | 1.01
2018-11-10 06:00 | 13780.6542 | -0.048233 | 17.84 | 19.77 | 29.98 | 45.2 | 6.27 | 2.89 | 13.02 | 20
2018-11-10 07:00 | 15961.3886 | 39.2783 | 17.89 | 20.76 | 25.07 | 37.06 | 27 | 17.78 | 2 | 36.46
2018-11-10 08:00 | 16411.5726 | 399.993 | 17.6 | 20.61 | 25.79 | 31.82 | 18.07 | 12.5 | 0.56 | 3.83
2018-11-10 09:00 | 17359.2907 | 467.304 | 17.92 | 24.34 | 23.37 | 31.19 | 8.11 | 10.59 | 0.03 | 11.07
2018-11-10 10:00 | 16371.9856 | 996.669 | 67.47 | 67.47 | 35.44 | 29.48 | 9.19 | 9.55 | 0.6 | 6.07
2018-11-10 11:00 | 17783.4387 | 1041.34 | 18.49 | 26.17 | 33.63 | 28.72 | 7.63 | 12.39 | 0.53 | 6.2
2018-11-10 12:00 | 16489.7675 | 1158.65 | 18.31 | 23.58 | 33.39 | 28.34 | 7.61 | 9.03 | 0.28 | 4.07
2018-11-10 13:00 | 17178.3857 | 1001.83 | 18.71 | 20.06 | 33.09 | 27.53 | 7.61 | 9.68 | 0.33 | 3.5
2018-11-10 14:00 | 14047.8219 | 797.181 | 18.62 | 19.98 | 37.68 | 27.14 | 6.85 | 13.65 | 0.37 | 4.55
2018-11-10 15:00 | 13187.844 | 560.941 | 18.64 | 19.69 | 36.15 | 27.27 | 5.56 | 6.09 | 0.54 | 3.25
2018-11-10 16:00 | 12655.6872 | 325.776 | 18.42 | 19.69 | 40.82 | 27.67 | 5.44 | 6.51 | 0.55 | 2.62
2018-11-10 17:00 | 12158.4153 | 18.3319 | 18.64 | 19.99 | 47.14 | 38.58 | 8 | 8 | 0.99 | 4.13
2018-11-10 18:00 | 11900.6042 | -0.048233 | 19.52 | 20.42 | 44.54 | 29.99 | 24 | 14.22 | 1.01 | 23.8
2018-11-10 19:00 | 13026.0341 | -0.048233 | 18.79 | 19.78 | 42.19 | 26.97 | 18.8 | 15 | 2 | 11.74
2018-11-10 20:00 | 11358.1542 | -0.048233 | 18.17 | 20.26 | 41.74 | 25.66 | 9.28 | 6.77 | 2.11 | 4.82
2018-11-10 21:00 | 12423.6291 | -0.048233 | 17.3 | 19.73 | 39.94 | 24.99 | 6.91 | 2.83 | 3.5 | 3.01
2018-11-10 22:00 | 11914.0641 | -0.048233 | 16.1 | 18.01 | 38.9 | 24.61 | 5.98 | 2.97 | 18 | 14.25
2018-11-10 23:00 | 11641.8741 | -0.048233 | 14.34 | 17.67 | 38.02 | 23.21 | 15 | 0.61 | 20 | 15
2018-11-11 | 11424.5441 | -0.048233 | 13.67 | 16.71 | 42.35 | 22.02 | 13 | 0.61 | 15.11 | 12
2018-11-11 01:00 | 11402.3891 | -0.048233 | 13.09 | 17.24 | 39.45 | 23.59 | 2 | 0.49 | 19 | 1.01
2018-11-11 02:00 | 11346.4741 | -0.048233 | 12.89 | 15.93 | 38.06 | 23.7 | 2 | 0.49 | 13.68 | 1.79
2018-11-11 03:00 | 10158.3042 | -0.048233 | 11.75 | 11.75 | 14.38 | 22.79 | 2.1 | 0.99 | 12.39 | 1.7
2018-11-11 04:00 | 11274.7341 | -0.048233 | 13.5 | 16.09 | 39 | 18.65 | 2 | 0.99 | 14.4 | 1.79
2018-11-11 05:00 | 10154.5042 | -0.048233 | 14.02 | 15.63 | 42.61 | 19.68 | 2.1 | 0.99 | 18.61 | 1.9
2018-11-11 06:00 | 11196.6641 | -0.048233 | 16.16 | 16.16 | 45.93 | 23.8 | 3.11 | 1 | 32 | 87.1162
2018-11-11 07:00 | 10030.0015 | 84.8963 | 16.64 | 16.94 | 46.21 | 24.48 | 26 | 6.55 | 15 | 103.1162
2018-11-11 08:00 | 11342.842 | 368.509 | 16.34 | 17.79 | 41.76 | 27.44 | 5 | 2.61 | 2.25 | 2
2018-11-11 09:00 | 10221.4889 | 320.462 | 17.75 | 20.04 | 40.26 | 30.75 | 19 | 2.99 | 2.25 | 2
2018-11-11 10:00 | 10593.3978 | 821.945 | 18.26 | 19.8 | 38.34 | 27.06 | 22.62 | 6.37 | 2.25 | 2.25
2018-11-11 11:00 | 12066.8157 | 1145.74 | 17.51 | 17.51 | 37.61 | 27.67 | 8.63 | 8.42 | 2.25 | 3.65
2018-11-11 12:00 | 12119.9138 | 1112.07 | 18.62 | 18.62 | 35.07 | 29.26 | 6.71 | 7.37 | 2.25 | 2.24
2018-11-11 13:00 | 12315.3631 | 1046.33 | 18.63 | 18.63 | 32.06 | 27.88 | 10.2 | 10 | 2.25 | 4.33
2018-11-11 14:00 | 12108.0936 | 800.866 | 19.03 | 19.03 | 30.39 | 26.94 | 7.99 | 9.79 | 2.25 | 2.59
2018-11-11 15:00 | 10927.8813 | 427.033 | 18.2 | 18.2 | 31.48 | 26.91 | 8.11 | 7.26 | 1 | 2.44
2018-11-11 16:00 | 11864.4509 | 100.925 | 18.54 | 18.54 | 39.3 | 26.45 | 6.8 | 1 | 1 | 2.48
2018-11-11 17:00 | 10585.9667 | 10.1228 | 19.58 | 19.9 | 48.48 | 34.81 | 8.11 | 9.76 | 1 | 4.19
2018-11-11 18:00 | 11806.4541 | -0.048233 | 58.07 | 20.12 | 48.52 | 27.37 | 28.94 | 10.44 | 1.75 | 28.94
2018-11-11 19:00 | 10612.4042 | -0.048233 | 18.8 | 19.39 | 44.02 | 29.07 | 20.98 | 20.43 | 2.11 | 20.93
2018-11-11 20:00 | 11584.9041 | -0.048233 | 18.37 | 19.47 | 42.11 | 27.1 | 8.11 | 10.37 | 1 | 3.06
2018-11-11 21:00 | 11522.6591 | -0.048233 | 17.29 | 19.4 | 37.49 | 23.59 | 6 | 1 | 2.25 | 2.22
2018-11-11 22:00 | 11384.4541 | -0.048233 | 16.77 | 18.4 | 35.11 | 24.77 | 4.89 | 1 | 13.59 | 2.21
2018-11-11 23:00 | 10145.9542 | -0.048233 | 14.15 | 17.76 | 35.08 | 23.11 | 4.29 | 0.61 | 28.59 | 12.75
2018-11-12 | 10014.8542 | -0.048233 | 16.26 | 16.66 | 34.5 | 19.23 | 8 | 0.5 | 12.26 | 2.21
2018-11-12 01:00 | 9955.9542 | -0.048233 | 13.94 | 16.46 | 16.81 | 18.55 | 6.75 | 0.5 | 10.49 | 2.96
2018-11-12 02:00 | 9904.6542 | -0.048233 | 13.65 | 16.06 | 16.78 | 17.99 | 3.82 | 0.5 | 3.97 | 2.7
2018-11-12 03:00 | 9933.1542 | -0.048233 | 13.21 | 16.69 | 16.78 | 18.52 | 5.51 | 1.11 | 4 | 2.31
2018-11-12 04:00 | 9992.0542 | -0.048233 | 13.08 | 17.04 | 16.87 | 19.65 | 5.4 | 1.15 | 4.82 | 2.45
2018-11-12 05:00 | 11149.1891 | -0.048233 | 13.32 | 18.92 | 17.35 | 20.05 | 6.75 | 1 | 5 | 3.01
2018-11-12 06:00 | 11136.5291 | -0.048233 | 13.76 | 18.49 | 30.5 | 21.65 | 8 | 1.26 | 26.59 | 31.46
2018-11-12 07:00 | 11124.3825 | 36.4384 | 15.05 | 18.59 | 30.64 | 21.87 | 19.5 | 7.5 | 18 | 87.1162
2018-11-12 08:00 | 10195.4535 | 89.0563 | 19.11 | 19.7 | 36.66 | 23.71 | 4.43 | 7.45 | 10 | 4.23
2018-11-12 09:00 | 11419.7241 | 158.383 | 17.8 | 21.91 | 37.96 | 30.85 | 5.97 | 7.45 | 1 | 5.2
2018-11-12 10:00 | 10361.7497 | 211.105 | 19.51 | 26.65 | 36.02 | 24.95 | 5.21 | 7.45 | 1 | 3.37
2018-11-12 11:00 | 11803.053 | 241.728 | 18.45 | 21.71 | 34.32 | 26.55 | 6.21 | 6 | 2.16 | 1.89
2018-11-12 12:00 | 11849.3253 | 246.588 | 18.99 | 20.93 | 15.25 | 28.6 | 6.52 | 7.61 | 1 | 1.5
2018-11-12 13:00 | 10988.0648 | 488.384 | 20.25 | 21.69 | 14.67 | 29.16 | 8.11 | 9.23 | 1 | 3.27
2018-11-12 14:00 | 12362.2822 | 599.803 | 19.4 | 21.47 | 12.67 | 30.2 | 8.11 | 8.48 | 1 | 2.62
2018-11-12 15:00 | 11001.3648 | 602.384 | 19.92 | 21.38 | 13.69 | 28.95 | 8.11 | 2.99 | 1 | 2.45
2018-11-12 16:00 | 10695.5703 | 257.495 | 19.69 | 26.46 | 31.03 | 28.09 | 8.06 | 2.24 | 1 | 1.81
2018-11-12 17:00 | 10536.3398 | 7.8839 | 19.88 | 26.74 | 39.9 | 48.41 | 7.68 | 1.45 | 1 | 3.11
2018-11-12 18:00 | 11798.0141 | -0.048233 | 329.8457 | 285.52 | 38.38 | 44.1 | 29.67 | 11.43 | 1 | 29.47
2018-11-12 19:00 | 11655.5891 | -0.048233 | 19.86 | 26.44 | 34.57 | 32.21 | 25.91 | 24.54 | 2 | 25.25
2018-11-12 20:00 | 11515.2741 | -0.048233 | 754.4211 | 486.81 | 16.75 | 26.74 | 12.83 | 9.31 | 2 | 3.04
2018-11-12 21:00 | 11391.8391 | -0.048233 | 18.66 | 31.49 | 15.86 | 26.4 | 8.11 | 1.45 | 3.5 | 3.1
2018-11-12 22:00 | 10118.4042 | -0.048233 | 17.72 | 32.46 | 15.64 | 24.58 | 5.58 | 1.19 | 16.86 | 3.11
2018-11-12 23:00 | 11136.5291 | -0.048233 | 16.88 | 26.92 | 15.76 | 23.26 | 12 | 0.5 | 22 | 3.01
2018-11-13 | 10109.8542 | -0.048233 | 15.35 | 20.49 | 15.51 | 20.54 | 13 | 0.5 | 10.51 | 2.2
2018-11-13 01:00 | 10107.0042 | -0.048233 | 15.11 | 19.16 | 15.07 | 19.76 | 5.64 | 0.5 | 8 | 2.41
2018-11-13 02:00 | 9996.8042 | -0.048233 | 14.26 | 18.96 | 14.39 | 19.31 | 5.16 | 0.5 | 3.5 | 2.11
2018-11-13 03:00 | 11060.5691 | -0.048233 | 13.61 | 18.55 | 12.56 | 19.38 | 5.25 | 1.36 | 3.98 | 2.11
2018-11-13 04:00 | 11082.7241 | -0.048233 | 13.24 | 18.91 | 15.01 | 20.2 | 5.25 | 1 | 2.61 | 2.51
2018-11-13 05:00 | 9977.8042 | -0.048233 | 13.09 | 19.51 | 15.45 | 22.23 | 5.25 | 1 | 3.5 | 3.51
2018-11-13 06:00 | 11047.9091 | -0.048233 | 13.34 | 21.17 | 33.93 | 32.63 | 5.25 | 1.11 | 10 | 30.58
2018-11-13 07:00 | 10949.1118 | 59.305 | 13.69 | 22.49 | 40.5 | 28.86 | 27.87 | 20.6 | 39.24 | 29.66
2018-11-13 08:00 | 11234.5906 | 198.901 | 13.33 | 31.53 | 41.7 | 28.32 | 5.91 | 9.5 | 12.41 | 3.3
2018-11-13 09:00 | 10678.7087 | 607.746 | 17.01 | 26.65 | 39.63 | 28.52 | 5.81 | 9.5 | 1 | 3.65
2018-11-13 10:00 | 10940.4375 | 752.25 | 16.3 | 29.86 | 40.76 | 30.53 | 7.06 | 9.5 | 1.87 | 4.73
2018-11-13 11:00 | 11108.8725 | 919.55 | 15.82 | 26.17 | 37.98 | 29.43 | 7.28 | 11.15 | 12.5 | 10.13
2018-11-13 12:00 | 10993.761 | 1078.38 | 15.96 | 25.02 | 37.67 | 30.69 | 7.8 | 11.2 | 2 | 4.37
2018-11-13 13:00 | 12243.9607 | 1017.65 | 151.08 | 151.08 | 37.7 | 35.31 | 7.5 | 11.66 | 1 | 2.11
2018-11-13 14:00 | 12036.63 | 723.128 | 16.48 | 29.38 | 12.27 | 35.37 | 7.8 | 9.88 | 1 | 2.62
2018-11-13 15:00 | 10706.9522 | 504.476 | 16.87 | 23.4 | 40.52 | 38.34 | 8.11 | 8.6 | 2 | 2.09
2018-11-13 16:00 | 11624.1736 | 215.174 | 17.04 | 24.48 | 42.06 | 34.04 | 8.11 | 8.82 | 2 | 2.15
2018-11-13 17:00 | 10338.2194 | 8.3362 | 18.03 | 23.19 | 48.23 | 52.3 | 6.44 | 9.01 | 2 | 2.91
2018-11-13 18:00 | 10392.0042 | -0.048233 | 18.03 | 37.09 | 43.48 | 34.8 | 29.52 | 25.23 | 2.11 | 29.32
2018-11-13 19:00 | 10212.4542 | -0.048233 | 17.02 | 32.68 | 40.57 | 28.69 | 25.4 | 25.24 | 2.96 | 25.25
2018-11-13 20:00 | 10125.0542 | -0.048233 | 16.45 | 30.7 | 36.31 | 25.93 | 6.83 | 10.82 | 2 | 1.68
2018-11-13 21:00 | 10142.1542 | -0.048233 | 15.37 | 23.72 | 33.46 | 25.63 | 6 | 10.5 | 3.5 | 2.55
2018-11-13 22:00 | 10008.2042 | -0.048233 | 14.71 | 24.11 | 15.57 | 24.25 | 7.89 | 1.3 | 20.01 | 3.2
2018-11-13 23:00 | 10967.7291 | -0.048233 | 12.47 | 19.3 | 14.75 | 21.31 | 14.55 | 14.54 | 27.74 | 14.55
2018-11-14 | 9746.9542 | -0.048233 | 9.52 | 21 | 11.85 | 18.97 | 13 | 12.79 | 11.01 | 2
2018-11-14 01:00 | 10775.7191 | -0.048233 | 0.37 | 19.17 | 6.62 | 18.12 | 5.15 | 0.5 | 13.96 | 1.76
2018-11-14 02:00 | 9694.7042 | -0.048233 | 8.78 | 19.01 | 5.52 | 16.06 | 4 | 0.5 | 10.31 | 2
2018-11-14 03:00 | 9692.8042 | -0.048233 | 2.23 | 18.78 | 5.57 | 16.43 | 5.15 | 1 | 10.72 | 2
2018-11-14 04:00 | 11086.9441 | -0.048233 | 12.29 | 18.48 | 9.9 | 17.99 | 4.46 | 0.99 | 9.06 | 2
2018-11-14 05:00 | 12386.7041 | -0.048233 | 12.89 | 19.18 | 12.32 | 19.62 | 4.46 | 0.99 | 10.92 | 3.3
2018-11-14 06:00 | 13411.1042 | -0.048233 | 14 | 19.9 | 16.36 | 24.69 | 7.65 | 1.29 | 24.77 | 30.6
2018-11-14 07:00 | 14504.9876 | 129.408 | 15.36 | 21.65 | 34.03 | 24.79 | 29.45 | 10.15 | 3.98 | 87.1162
2018-11-14 08:00 | 14959.3821 | 417.718 | 17.08 | 20.17 | 34.39 | 29.81 | 6.2 | 5 | 2.11 | 3.11
2018-11-14 09:00 | 15364.9219 | 446.602 | 18.07 | 19.73 | 17.8 | 26.58 | 7.75 | 6.25 | 2 | 3.28
2018-11-14 10:00 | 16554.1823 | 691.455 | 17.83 | 20.09 | 17.82 | 30.23 | 11.81 | 9.5 | 2 | 3.13
2018-11-14 11:00 | 14756.3319 | 501.981 | 17.21 | 21.09 | 17.27 | 29.95 | 9.04 | 9.52 | 2 | 4.78
2018-11-14 12:00 | 15605.4619 | 638.802 | 17.34 | 22.08 | 17.04 | 34.12 | 8 | 11.19 | 2 | 5.33
2018-11-14 13:00 | 15603.7158 | 941.964 | 17.3 | 27.02 | 16.86 | 36.63 | 15 | 10.22 | 2 | 5.29
2018-11-14 14:00 | 14771.7865 | 707.249 | 17.23 | 34.9 | 16.37 | 37.83 | 7.21 | 7 | 2 | 4.58
2018-11-14 15:00 | 15732.1589 | 622.999 | 17.71 | 27.82 | 16.45 | 33.96 | 5.77 | 1.45 | 2 | 3.85
2018-11-14 16:00 | 14953.838 | 283.254 | 17.28 | 25.28 | 35.62 | 32.26 | 20 | 1.45 | 2 | 3.48
2018-11-14 17:00 | 14524.1506 | 18.9674 | 17.87 | 23.61 | 42.52 | 39.93 | 7.97 | 0.99 | 2 | 3.54
2018-11-14 18:00 | 14240.3391 | -0.048233 | 94.08 | 22.37 | 37.3 | 33.16 | 28.03 | 17.46 | 2 | 22.96
2018-11-14 19:00 | 12681.5042 | -0.048233 | 17.5 | 19.78 | 34.74 | 30.2 | 20.28 | 20 | 2 | 20.08
2018-11-14 20:00 | 13867.9241 | -0.048233 | 17.66 | 19.2 | 25.55 | 28.5 | 14.29 | 1.51 | 2 | 2.39
2018-11-14 21:00 | 13477.5741 | -0.048233 | 18.19 | 18.29 | 17.79 | 24.61 | 18.84 | 1.45 | 2 | 3.13
2018-11-14 22:00 | 11502.5542 | -0.048233 | 17.83 | 18.62 | 17.07 | 20.52 | 7.5 | 1.45 | 20.01 | 3.2
2018-11-14 23:00 | 11199.5042 | -0.048233 | 16.03 | 18.76 | 16 | 17.23 | 14.73 | 14.28 | 29.28 | 14.73
2018-11-15 | 12255.8841 | -0.048233 | 11.94 | 17.91 | 16.34 | 16.55 | 21 | 12.86 | 20.68 | 13.31
2018-11-15 01:00 | 11995.2991 | -0.048233 | 12.64 | 16.6 | 15.58 | 16.82 | 4.75 | 0.49 | 12 | 2
2018-11-15 02:00 | 11894.0191 | -0.048233 | 12.07 | 16.02 | 14.96 | 16.87 | 3.95 | 0.49 | 10.04 | 0.75
2018-11-15 03:00 | 10638.0542 | -0.048233 | 10.05 | 16.19 | 14.51 | 18.05 | 4.75 | 1.75 | 10.26 | 1
2018-11-15 04:00 | 12039.6091 | -0.048233 | 8.68 | 16.75 | 14.77 | 19.42 | 4.75 | 1.62 | 8.11 | 1
2018-11-15 05:00 | 13098.8291 | -0.048233 | 9.59 | 17.76 | 15.52 | 19.81 | 4.75 | 1.62 | 8.43 | 2
2018-11-15 06:00 | 13565.0042 | -0.048233 | 6.37 | 18.3 | 16.56 | 28.64 | 19.25 | 2 | 12 | 19.25
2018-11-15 07:00 | 15780.7781 | 26.0835 | 10.27 | 20.53 | 16.01 | 29.52 | 27.42 | 7.8 | 3.5 | 27.42
2018-11-15 08:00 | 14554.0585 | 61.0616 | 13.34 | 18.8 | 16.87 | 28.91 | 4.5 | 10 | 2.27 | 1.5
2018-11-15 09:00 | 16739.8781 | 102.183 | 14.22 | 18.66 | 17.65 | 36.51 | 4.94 | 10 | 2 | 2.61
2018-11-15 10:00 | 17696.8707 | 695.285 | 15.17 | 19 | 17.62 | 33.85 | 6.39 | 10 | 2 | 3.05
2018-11-15 11:00 | 15680.1775 | 713.45 | 14.58 | 19.24 | 17.64 | 30.48 | 6.01 | 3.56 | 2 | 3.99
2018-11-15 12:00 | 16492.4104 | 753.432 | 14.52 | 19.35 | 17.01 | 31.39 | 6.01 | 6.33 | 2 | 4.18
2018-11-15 13:00 | 16160.4633 | 648.014 | 14.32 | 20.19 | 16.55 | 35.42 | 6 | 5.7 | 2 | 4.79
2018-11-15 14:00 | 16584.4534 | 423.861 | 15.38 | 21.11 | 16.04 | 38.34 | 4.5 | 7.06 | 2 | 4.3
2018-11-15 15:00 | 16160.0374 | 294.571 | 15.94 | 21.14 | 15.8 | 40.25 | 4 | 6.29 | 2 | 3.8
2018-11-15 16:00 | 14283.3155 | 130.069 | 122.05 | 20.49 | 17.78 | 39.42 | 4.02 | 10.22 | 2 | 3.82
2018-11-15 17:00 | 15633.621 | 7.5981 | 16.66 | 21.18 | 39.5 | 53.69 | 6.49 | 3 | 2 | 6.49
2018-11-15 18:00 | 13598.2542 | -0.048233 | 38.61 | 38.61 | 32.58 | 44.76 | 26.04 | 11.5 | 2 | 24.46
2018-11-15 19:00 | 14718.2541 | -0.048233 | 20.7 | 28.82 | 18.03 | 32.68 | 19.61 | 10.5 | 2 | 12.61
2018-11-15 20:00 | 12978.8542 | -0.048233 | 17.58 | 26.66 | 17.58 | 29.45 | 8 | 7.14 | 2 | 3.3
2018-11-15 21:00 | 13942.8291 | -0.048233 | 17.88 | 27.4 | 17.19 | 27.74 | 4.74 | 2.4 | 2 | 1.5
2018-11-15 22:00 | 11916.7542 | -0.048233 | 17.39 | 20.97 | 15.82 | 26.76 | 5.21 | 2 | 25 | 2.17
2018-11-15 23:00 | 12664.1691 | -0.048233 | 15.2 | 19.25 | 15.79 | 23.66 | 5 | 0.49 | 53.9062 | 1.5
2018-11-16 | 11197.6042 | -0.048233 | 11.72 | 19.03 | 15 | 20.01 | 6.01 | 0.49 | 14.74 | 1.5
2018-11-16 01:00 | 12265.3791 | -0.048233 | 0 | 19.04 | 15 | 19.28 | 4 | 0.5 | 20.01 | 0.5
2018-11-16 02:00 | 12249.5541 | -0.048233 | 0 | 18.18 | 13.71 | 18.92 | 3.31 | 0.51 | 9.74 | 0.01
2018-11-16 03:00 | 10928.7542 | -0.048233 | 0 | 18.02 | 13.58 | 18.96 | 25 | 1.62 | 10.62 | 0.01
2018-11-16 04:00 | 12300.1941 | -0.048233 | 10.67 | 18.08 | 15.12 | 19.5 | 3.31 | 1.62 | 9.11 | 0.01
2018-11-16 05:00 | 13201.1641 | -0.048233 | 14.27 | 18.63 | 15.34 | 20.98 | 4 | 1.62 | 10.88 | 0.5
2018-11-16 06:00 | 15141.3091 | -0.048233 | 74.52 | 19.42 | 18.77 | 26.7 | 5.25 | 2 | 20.01 | 19.25
2018-11-16 07:00 | 14311.466 | 46.7011 | 16.71 | 20.64 | 20.02 | 25.24 | 17.66 | 7.91 | 3.11 | 17.66
2018-11-16 08:00 | 15088.0862 | 196.196 | 16.79 | 21.15 | 19.74 | 28.95 | 5.84 | 7.9 | 2 | 1
2018-11-16 09:00 | 16217.2894 | 174.831 | 16.98 | 23.09 | 19.76 | 29.55 | 5 | 6.75 | 1.55 | 1
2018-11-16 10:00 | 16755.5804 | 437.453 | 18.05 | 21.35 | 20.37 | 31.44 | 4.7 | 6.75 | 1.9 | 1
2018-11-16 11:00 | 15791.755 | 594.9 | 16.65 | 22.51 | 19.41 | 31.3 | 4.56 | 3.75 | 1.59 | 1.99
2018-11-16 12:00 | 18045.4163 | 533.66 | 17.7 | 22.97 | 18.06 | 31.43 | 5.19 | 4.98 | 1.68 | 1.38
2018-11-16 13:00 | 17121.2752 | 345.395 | 69.82 | 69.82 | 17.37 | 33.11 | 5.22 | 7.02 | 1.5 | 1
2018-11-16 14:00 | 15189.4379 | 658.882 | 18.68 | 22.16 | 16.77 | 33.9 | 6.07 | 6.31 | 1.5 | 2.29
2018-11-16 15:00 | 14237.3897 | 516.726 | 18.98 | 22.25 | 17.09 | 32.38 | 5.05 | 3.45 | 1.5 | 1.46
2018-11-16 16:00 | 13751.9644 | 200.752 | 18.17 | 21.61 | 23.37 | 30.21 | 6.58 | 2.48 | 1.5 | 1.36
2018-11-16 17:00 | 14945.1131 | 5.984 | 18.19 | 23.04 | 34.57 | 38.3 | 6.01 | 2.4 | 1.5 | 2.56
2018-11-16 18:00 | 14630.6891 | -0.048233 | 17.71 | 21.32 | 23.74 | 29.32 | 27.28 | 7.5 | 1.5 | 27.28
2018-11-16 19:00 | 13217.3042 | -0.048233 | 17.17 | 20.45 | 20.29 | 28.49 | 20 | 12.3 | 1.5 | 1
2018-11-16 20:00 | 14380.6541 | -0.048233 | 16.93 | 20.87 | 18.57 | 26.05 | 5 | 2.4 | 2 | 1
2018-11-16 21:00 | 12605.5042 | -0.048233 | 16.58 | 20.85 | 18.33 | 24.62 | 5.18 | 2 | 2.99 | 1
2018-11-16 22:00 | 12156.1542 | -0.048233 | 14.76 | 19.18 | 17.34 | 20.65 | 6.01 | 2 | 11.63 | 5.33
2018-11-16 23:00 | 11753.3542 | -0.048233 | 3.73 | 14.73 | 16.34 | 19.31 | 8 | 0.48 | 25.29 | 2.25
2018-11-17 | 11513.0042 | -0.048233 | -0.02 | 9.97 | 15.93 | 15.88 | 16.16 | 0.48 | 25 | 3.11
2018-11-17 01:00 | 11407.5542 | -0.048233 | -0.01 | 11.12 | 15.2 | 12.42 | 6.3 | 0.5 | 25 | 5.2
2018-11-17 02:00 | 11390.4542 | -0.048233 | -0.56 | 7.4 | 14.52 | 10.8 | 6.3 | 0.5 | 14.72 | 2.51
2018-11-17 03:00 | 12632.5191 | -0.048233 | -0.69 | 7.55 | 14.53 | 12.46 | 25 | 1 | 20.12 | 2.51
2018-11-17 04:00 | 11451.2542 | -0.048233 | -0.56 | 8.56 | 15.23 | 14.98 | 25 | 1 | 16.28 | 2.51
2018-11-17 05:00 | 12339.5042 | -0.048233 | -0.1 | 14.39 | 17.01 | 18.19 | 25 | 1 | 20.37 | 5.2
2018-11-17 06:00 | 16384.0991 | -0.048233 | 10.41 | 18.91 | 20.45 | 24.4 | 25 | 1.03 | 51.7762 | 31.6
2018-11-17 07:00 | 18665.655 | 128.564 | 14.73 | 19.15 | 21.62 | 23.83 | 29.46 | 2 | 36.4 | 32
2018-11-17 08:00 | 16307.832 | 420.139 | 15.96 | 19.15 | 21.14 | 23.1 | 6 | 1.75 | 9.32 | 3.34
2018-11-17 09:00 | 20503.4175 | 770.519 | 16.56 | 20.81 | 19.55 | 22.69 | 7.15 | 1 | 3.95 | 3.2
2018-11-17 10:00 | 18911.4426 | 933.538 | 15.2 | 20.07 | 17.47 | 24.28 | 15.86 | 1.75 | 9.11 | 3.2
2018-11-17 11:00 | 16893.9165 | 1074.07 | 15.13 | 22.89 | 18.13 | 27.78 | 6 | 2 | 20.2 | 4
2018-11-17 12:00 | 18713.9171 | 825.31 | 14.93 | 22.06 | 17.39 | 30.15 | 6.55 | 2.4 | 17.79 | 3.1
2018-11-17 13:00 | 19064.1348 | 1067.27 | 14.05 | 25.89 | 17.2 | 36.62 | 6.46 | 2 | 3.11 | 3
2018-11-17 14:00 | 17912.3998 | 811.578 | 47.33 | 47.33 | 17.19 | 39.3 | 19.59 | 6 | 1.9 | 4
2018-11-17 15:00 | 17139.8349 | 643.289 | 13.13 | 25.49 | 17.75 | 39.8 | 20.77 | 1.61 | 1.9 | 4.27
2018-11-17 16:00 | 16407.3041 | 307.947 | 14.48 | 22.89 | 22.25 | 32.29 | 23.25 | 2 | 1.9 | 3.1
2018-11-17 17:00 | 15805.3726 | 15.3958 | 15.47 | 20.7 | 34.2 | 36.98 | 22 | 2 | 1.9 | 4.94
2018-11-17 18:00 | 13965.9042 | -0.048233 | 18.19 | 20.73 | 28.77 | 25.61 | 27.1 | 2 | 1 | 26.9
2018-11-17 19:00 | 13703.7042 | -0.048233 | 18.11 | 19.93 | 22.9 | 25.51 | 6.96 | 9.27 | 3.11 | 2.5
2018-11-17 20:00 | 14822.6991 | -0.048233 | 16.91 | 21.92 | 22.37 | 25 | 5.68 | 1.97 | 15.69 | 3.1
2018-11-17 21:00 | 13190.7042 | -0.048233 | 17.32 | 19.78 | 18.08 | 21.75 | 5.81 | 1.59 | 15.48 | 3.2
2018-11-17 22:00 | 14013.5141 | -0.048233 | 17.28 | 20.78 | 17.47 | 19.99 | 3.95 | 1.19 | 15.29 | 3.3
2018-11-17 23:00 | 13665.3641 | -0.048233 | 16.04 | 17.11 | 15.97 | 17.86 | 8 | 0.5 | 25 | 11.8
2018-11-18 | 13644.2641 | -0.048233 | 12.62 | 12.62 | 15.72 | 13.77 | 7.5 | 0.5 | 22 | 4.94
2018-11-18 01:00 | 13335.1491 | -0.048233 | 12.81 | 12.81 | 12.58 | 10.49 | 4 | 0.5 | 22 | 3.8
2018-11-18 02:00 | 11867.3542 | -0.048233 | 12.29 | 12.29 | 11.27 | 8.04 | 16.25 | 0.5 | 18.74 | 2.61
2018-11-18 03:00 | 13150.5241 | -0.048233 | 13.45 | 13.45 | 11.46 | 8.12 | 18 | 1.22 | 22.99 | 2.11
2018-11-18 04:00 | 13601.0091 | -0.048233 | 13.45 | 15.38 | 14.09 | 10.29 | 5 | 1.18 | 18.44 | 2.61
2018-11-18 05:00 | 14488.2641 | -0.048233 | 13.95 | 15.68 | 14.83 | 12.31 | 5.55 | 1 | 22 | 3.79
2018-11-18 06:00 | 14902.6042 | -0.048233 | 17.56 | 17.7 | 18.9 | 19.11 | 30.01 | 1 | 50.6662 | 32.91
2018-11-18 07:00 | 17972.7383 | 34.7709 | 17.02 | 17.1 | 18.89 | 19.57 | 25 | 6 | 21.34 | 25
2018-11-18 08:00 | 16699.0848 | 289.984 | 16.94 | 16.94 | 19.89 | 21.81 | 8 | 3.25 | 10.5 | 4
2018-11-18 09:00 | 17505.459 | 547.799 | 17.72 | 18.81 | 19.47 | 24.04 | 8.25 | 3 | 10.5 | 4.79
2018-11-18 10:00 | 19344.3502 | 732.877 | 16.58 | 16.58 | 19.54 | 24.24 | 12.88 | 2.86 | 12 | 3.86
2018-11-18 11:00 | 19184.2572 | 982.13 | 17.28 | 21.74 | 18.18 | 28.5 | 6.52 | 3.11 | 12 | 4
2018-11-18 12:00 | 20435.9281 | 975.548 | 15.7 | 24.5 | 17.98 | 32.41 | 7.62 | 2.65 | 3.5 | 3.24
2018-11-18 13:00 | 20261.8584 | 942.553 | 15.67 | 22.16 | 17.48 | 33.69 | 7.7 | 6.5 | 4.01 | 3.24
2018-11-18 14:00 | 17927.8165 | 767.191 | 63.11 | 63.11 | 17.06 | 32.58 | 18.5 | 5.72 | 7.81 | 3.24
2018-11-18 15:00 | 16476.3464 | 463.39 | 16.01 | 24.22 | 16.76 | 27.61 | 21.82 | 1.61 | 3.5 | 3.24
2018-11-18 16:00 | 13895.7051 | 119.058 | 15.71 | 17.83 | 21.06 | 25.76 | 20.78 | 2 | 3.5 | 3.24
2018-11-18 17:00 | 13669.9879 | 6.4609 | 16.39 | 19.16 | 29.96 | 41.46 | 6.57 | 2 | 3.5 | 4
2018-11-18 18:00 | 14255.1091 | -0.048233 | 18.69 | 19.01 | 21.16 | 28.02 | 35 | 10 | 1 | 35
2018-11-18 19:00 | 13218.0441 | -0.048233 | 16.92 | 19.27 | 19.8 | 25.16 | 19.93 | 16.7 | 2.11 | 18.93
2018-11-18 20:00 | 11455.0542 | -0.048233 | 14.7 | 19.22 | 17.02 | 24.52 | 6.14 | 1.68 | 1 | 3.12
2018-11-18 21:00 | 10912.6042 | -0.048233 | 14.4 | 20.33 | 16.42 | 22.71 | 6.2 | 1.62 | 12 | 3.1
2018-11-18 22:00 | 10264.7042 | -0.048233 | 14.92 | 18.51 | 16.55 | 21.54 | 5.25 | 1.22 | 12 | 4.6
2018-11-18 23:00 | 11052.1291 | -0.048233 | 10.37 | 17.96 | 15.79 | 21.1 | 19.64 | 0.62 | 14.67 | 2.97
2018-11-19 | 9728.9042 | -0.048233 | 13.43 | 19.92 | 15.68 | 19.49 | 18.04 | 0.61 | 12 | 2.93
2018-11-19 01:00 | 10701.8691 | -0.048233 | 13.19 | 18.03 | 13.08 | 19.3 | 3 | 0.61 | 9.29 | 2.11
2018-11-19 02:00 | 9527.5042 | -0.048233 | 13.27 | 18.46 | 8.4 | 18.38 | 2.5 | 0.61 | 3.53 | 1
2018-11-19 03:00 | 9534.1542 | -0.048233 | 12.7 | 18.26 | 7.74 | 18.69 | 3 | 1 | 3.5 | 1
2018-11-19 04:00 | 10667.0541 | -0.048233 | -0.99 | 18.5 | 9.92 | 18.49 | 3 | 1 | 3.76 | 1
2018-11-19 05:00 | 10957.1791 | -0.048233 | 7.52 | 18.3 | 15.47 | 19.2 | 3 | 1 | 4 | 2.11
2018-11-19 06:00 | 10253.3042 | -0.048233 | 14.91 | 19.39 | 15.99 | 20.76 | 6.94 | 1 | 12 | 13.95
2018-11-19 07:00 | 10420.5832 | 111.035 | 11.42 | 19.38 | 16.04 | 21.45 | 24.01 | 2.5 | 20 | 24.01
2018-11-19 08:00 | 10567.6148 | 438.805 | 16.41 | 20.24 | 15.67 | 23.76 | 4.89 | 2.5 | 2 | 4.39
2018-11-19 09:00 | 10615.7883 | 765.514 | 12.19 | 20.28 | 15.99 | 25.02 | 5.49 | 2.01 | 2 | 5.39
2018-11-19 10:00 | 10652.1182 | 847.756 | 18.28 | 19.31 | 18.53 | 22.46 | 7.68 | 6 | 1.9 | 5.68
2018-11-19 11:00 | 10752.974 | 1049.92 | 19.2 | 19.2 | 17.02 | 22.29 | 5.85 | 1.11 | 2.86 | 4
2018-11-19 12:00 | 12053.5122 | 1046.13 | 19.19 | 19.19 | 15.03 | 22.12 | 6.54 | 2.4 | 2 | 3.85
2018-11-19 13:00 | 10724.1795 | 1001.61 | 19.05 | 19.05 | 14.26 | 21.9 | 4.6 | 2.25 | 2 | 2.3
2018-11-19 14:00 | 11426.3579 | 715.671 | 18.26 | 18.98 | 14.36 | 21.67 | 3.89 | 1.62 | 2 | 2.21
2018-11-19 15:00 | 11274.824 | 640.037 | 58.28 | 18.83 | 15.95 | 21.6 | 3.85 | 1 | 2 | 1.61
2018-11-19 16:00 | 10005.836 | 269.459 | 17.82 | 19.02 | 19.08 | 21.61 | 4 | 0.99 | 2 | 2
2018-11-19 17:00 | 10823.8479 | 11.5715 | 18.7 | 19.49 | 30 | 35.14 | 5.47 | 1 | 2 | 3.6
2018-11-19 18:00 | 9806.8042 | -0.048233 | 49.64 | 20.54 | 21.55 | 27.96 | 30 | 9.01 | 1.9 | 30
2018-11-19 19:00 | 9663.3542 | -0.048233 | 19.27 | 19.27 | 20.61 | 25.17 | 16.21 | 15.01 | 2.11 | 16.01
2018-11-19 20:00 | 10645.9541 | -0.048233 | 18.19 | 19.14 | 18.04 | 22.63 | 7.85 | 2 | 2.11 | 3.85
2018-11-19 21:00 | 10576.3241 | -0.048233 | 17.28 | 19.22 | 14.68 | 22.38 | 6.01 | 1.54 | 3.46 | 3.02
2018-11-19 22:00 | 10467.6591 | -0.048233 | 17.15 | 17.77 | 15.87 | 21.13 | 4.86 | 1.43 | 28.44 | 3.02
2018-11-19 23:00 | 10526.7391 | -0.048233 | 15.73 | 17.22 | 15.57 | 19.12 | 6.85 | 0.61 | 11 | 2.21
2018-11-20 | 10584.7641 | -0.048233 | 11.85 | 16.5 | 13.75 | 17.62 | 3.9 | 0.5 | 11 | 2
2018-11-20 01:00 | 10461.3291 | -0.048233 | 9.23 | 16.18 | 10.64 | 16.83 | 2.25 | 0.74 | 10.4 | 2.05
2018-11-20 02:00 | 10418.0741 | -0.048233 | 9.01 | 15.83 | 8.28 | 17.68 | 2.25 | 0.74 | 3.5 | 1
2018-11-20 03:00 | 10485.5941 | -0.048233 | 11.21 | 16.54 | 8.15 | 18.12 | 2.98 | 1 | 3.5 | 1
2018-11-20 04:00 | 10465.5491 | -0.048233 | 10.92 | 16.26 | 8.13 | 18.97 | 3 | 1 | 4 | 1
2018-11-20 05:00 | 10596.3691 | -0.048233 | 6.35 | 16.71 | 10.71 | 22.85 | 2.98 | 1 | 8.61 | 1.94
2018-11-20 06:00 | 9714.6542 | -0.048233 | 15.1 | 17.67 | 11.14 | 33.22 | 3.5 | 1 | 12 | 3.5
2018-11-20 07:00 | 10740.0477 | 40.14 | 15.97 | 18.66 | 11.61 | 27.36 | 20 | 7.42 | 2 | 20
2018-11-20 08:00 | 10722.1 | 170.128 | 16.9 | 18.62 | 15 | 29.66 | 3.42 | 6.22 | 3.01 | 2.93
2018-11-20 09:00 | 10682.8741 | 145.947 | 17.22 | 19.61 | 19.01 | 27.26 | 20 | 6.22 | 1.9 | 3.8
2018-11-20 10:00 | 11244.6363 | 621.423 | 17.06 | 19.32 | 18.2 | 24.79 | 20 | 6 | 3.11 | 3.15
2018-11-20 11:00 | 9995.9997 | 654.105 | 15.04 | 18.88 | 19 | 23.57 | 20 | 2.25 | 10.03 | 3.11
2018-11-20 12:00 | 9554.4417 | 232.307 | 14.78 | 24.7 | 18.22 | 23.37 | 20 | 2 | 2 | 2
2018-11-20 13:00 | 10981.2745 | 564.791 | 15.91 | 20.36 | 18.02 | 23.71 | 20 | 2 | 3.5 | 1.35
2018-11-20 14:00 | 10167.5631 | 667.698 | 16.81 | 19.82 | 17.41 | 23.11 | 3.49 | 2 | 3.5 | 1.2
2018-11-20 15:00 | 10888.5041 | 110.857 | 16.92 | 20.11 | 16.96 | 22.66 | 3.9 | 0.99 | 3.5 | 1
2018-11-20 16:00 | 10163.3935 | 168.309 | 17.32 | 20.15 | 30.53 | 23.33 | 4.01 | 0.99 | 3.5 | 1
2018-11-20 17:00 | 10021.4398 | 5.884 | 18.53 | 25.82 | 35.05 | 36.23 | 4.99 | 0.99 | 2.11 | 1.02
2018-11-20 18:00 | 10204.8542 | -0.048233 | 79.94 | 79.94 | 31.42 | 25.8 | 28.47 | 0.99 | 2 | 19.54
2018-11-20 19:00 | 11346.4741 | -0.048233 | 741.1111 | 473.5 | 23.93 | 24.42 | 20 | 1.45 | 2.11 | 3.9
2018-11-20 20:00 | 10085.1542 | -0.048233 | 15.59 | 25.63 | 19.15 | 23.82 | 20 | 1.33 | 2.11 | 1.87
2018-11-20 21:00 | 11136.5291 | -0.048233 | 15.78 | 20.09 | 18.3 | 22.79 | 4.89 | 1.22 | 11.66 | 1.47
2018-11-20 22:00 | 9996.8042 | -0.048233 | 15.89 | 19.16 | 17.49 | 19.2 | 20 | 1.15 | 20.01 | 2
2018-11-20 23:00 | 9901.8042 | -0.048233 | 15.25 | 16.65 | 16.23 | 16.69 | 21 | 0.74 | 20.01 | 2
2018-11-21 | 10815.8091 | -0.048233 | 14.42 | 17.52 | 16.91 | 10.09 | 21 | 0.74 | 12.96 | 1
2018-11-21 01:00 | 10700.8141 | -0.048233 | 14.03 | 18.11 | 16.69 | 9.17 | 2.98 | 0.75 | 12 | 2.98
2018-11-21 02:00 | 10668.1091 | -0.048233 | 12.14 | 16.29 | 16.35 | 9.2 | 2.45 | 0.51 | 11.16 | 2.25
2018-11-21 03:00 | 9645.3042 | -0.048233 | 6.85 | 15.87 | 16.69 | 13.32 | 3 | 1 | 12 | 2.25
2018-11-21 04:00 | 9922.7042 | -0.048233 | 11.38 | 16.37 | 16.81 | 16.64 | 2.98 | 0.99 | 6.99 | 2.61
2018-11-21 05:00 | 12128.2291 | -0.048233 | 13.37 | 17.98 | 17.19 | 19.2 | 3 | 1 | 10.35 | 2.8
2018-11-21 06:00 | 12829.7042 | -0.048233 | 16.1 | 19.44 | 16.89 | 26.24 | 4 | 1.22 | 12 | 20
2018-11-21 07:00 | 15562.8629 | 86.5288 | 14.23 | 23.52 | 17.78 | 25.89 | 19.55 | 8.5 | 13.95 | 20
2018-11-21 08:00 | 14766.2955 | 449.469 | 15.11 | 20.45 | 18.89 | 28.44 | 3.12 | 1.51 | 2.59 | 3
2018-11-21 09:00 | 15447.3258 | 707.343 | 81.54 | 81.54 | 20.57 | 28.1 | 4.84 | 1.32 | 1 | 4.64
2018-11-21 10:00 | 15611.3319 | 859.981 | 14.81 | 19.41 | 20.94 | 24.83 | 5 | 1.42 | 1.9 | 4.7
2018-11-21 11:00 | 16759.9937 | 1102.25 | 15.02 | 18.37 | 20.01 | 23.81 | 3.11 | 1.7 | 2.61 | 3.11
2018-11-21 12:00 | 19111.9052 | 1058.55 | 14.57 | 18.91 | 19.89 | 25.34 | 3.11 | 1.13 | 2 | 3.1
2018-11-21 13:00 | 17022.385 | 1038.3 | 14.38 | 24.39 | 19.45 | 27.09 | 3 | 1 | 2 | 3
2018-11-21 14:00 | 13797.8931 | 525.098 | 14.94 | 25.56 | 19.48 | 31.22 | 2.99 | 1.83 | 2.39 | 2.79
2018-11-21 15:00 | 13157.7328 | 473.245 | 52.2 | 52.2 | 19.49 | 32.07 | 2.5 | 0.97 | 2 | 2.28
2018-11-21 16:00 | 13912.1879 | 292.908 | 1234.0511 | 966.44 | 21.66 | 28.58 | 2.61 | 0.97 | 2 | 2.41
2018-11-21 17:00 | 13468.843 | 10.6758 | 15.58 | 19.77 | 24.38 | 47.71 | 4.15 | 0.97 | 2 | 3.33
2018-11-21 18:00 | 13533.4891 | -0.048233 | 17.53 | 21.35 | 22.26 | 35.79 | 25.54 | 0.99 | 2 | 25
2018-11-21 19:00 | 13271.8491 | -0.048233 | 127.23 | 127.23 | 21.67 | 32.67 | 15.56 | 7.98 | 2.11 | 3.61
2018-11-21 20:00 | 13092.4991 | -0.048233 | 17.43 | 21.64 | 20.82 | 25.98 | 18.01 | 1.3 | 2 | 3.1
2018-11-21 21:00 | 12977.5041 | -0.048233 | 16.23 | 20.12 | 20.19 | 24.11 | 5.78 | 1 | 3.04 | 3.1
2018-11-21 22:00 | 11346.7542 | -0.048233 | 16.68 | 20.47 | 18.95 | 21.24 | 4.33 | 1 | 11 | 4.33
2018-11-21 23:00 | 10956.3042 | -0.048233 | 0 | 17.03 | 17.3 | 20.16 | 20 | 0.75 | 11 | 19.8
2018-11-22 | 12020.6191 | -0.048233 | 0 | 16.36 | 14.2 | 19.45 | 40 | 0.5 | 9.11 | 4.91
2018-11-22 01:00 | 11924.6141 | -0.048233 | -0.2 | 16.25 | 11.92 | 19.27 | 108.8141 | 0.5 | 22 | 20
2018-11-22 02:00 | 10787.2042 | -0.048233 | -0.36 | 16.47 | 8.87 | 19.09 | 110.8141 | 0.51 | 13.09 | 3.76
2018-11-22 03:00 | 11964.7041 | -0.048233 | -0.15 | 16.79 | 8.76 | 18.78 | 106.8141 | 0.99 | 13.89 | 2.61
2018-11-22 04:00 | 12195.7491 | -0.048233 | 14.53 | 17.41 | 11.51 | 18.98 | 101.8141 | 1 | 13.7 | 2.61
2018-11-22 05:00 | 12041.2042 | -0.048233 | 15.17 | 17.26 | 11.6 | 20.92 | 20 | 0.99 | 13.42 | 20
2018-11-22 06:00 | 13857.6042 | -0.048233 | 16.43 | 17.03 | 12.04 | 26.92 | 25.94 | 1 | 22 | 30.94
2018-11-22 07:00 | 14910.3233 | 94.0772 | 16.55 | 18.56 | 15.17 | 26.71 | 28.18 | 1.75 | 3.11 | 38.18
2018-11-22 08:00 | 15696.1423 | 357.255 | 16.93 | 19.64 | 18.37 | 27.53 | 17.18 | 1.73 | 2.27 | 4.7
2018-11-22 09:00 | 16289.4096 | 290.747 | 17.61 | 19.81 | 19.64 | 27.82 | 17.98 | 2.5 | 1 | 16.23
2018-11-22 10:00 | 18723.5998 | 923.488 | 17.79 | 20.28 | 20.47 | 26.57 | 23.06 | 2.26 | 2 | 5.3
2018-11-22 11:00 | 16906.409 | 1066.22 | 17.71 | 19.29 | 20.32 | 27.31 | 6.11 | 1 | 2.44 | 4
2018-11-22 12:00 | 19403.4756 | 1065.92 | 17.54 | 18.98 | 20.13 | 27.67 | 5.48 | 1.19 | 2 | 4
2018-11-22 13:00 | 18272.1759 | 608.598 | 17.06 | 18.83 | 19.06 | 28.48 | 4.24 | 1.18 | 2 | 4
2018-11-22 14:00 | 15193.0612 | 581.696 | 16.9 | 18.75 | 19.01 | 29.77 | 35 | 1.42 | 2 | 3
2018-11-22 15:00 | 14811.5592 | 622.115 | 16.87 | 18.68 | 19.17 | 31 | 23.99 | 1 | 2 | 3
2018-11-22 16:00 | 14103.8624 | 273.171 | 16.87 | 18.62 | 21.74 | 31.3 | 3.25 | 1 | 2 | 3
2018-11-22 17:00 | 15103.5047 | 5.1182 | 16.96 | 19.06 | 31.22 | 44.98 | 4 | 1 | 1 | 3.77
2018-11-22 18:00 | 14810.0391 | -0.048233 | 18.51 | 20.02 | 22.64 | 38.28 | 27.14 | 1.18 | 2 | 27.14
2018-11-22 19:00 | 14479.8241 | -0.048233 | 18.31 | 19.15 | 21.8 | 35.5 | 24.82 | 9.36 | 2.61 | 24.62
2018-11-22 20:00 | 14285.7041 | -0.048233 | 18.06 | 19.15 | 21.62 | 30.9 | 12.28 | 1.39 | 2 | 3.3
2018-11-22 21:00 | 14019.8441 | -0.048233 | 17.87 | 19.14 | 21.09 | 26.73 | 6.87 | 1.18 | 3.11 | 3.25
2018-11-22 22:00 | 12159.0042 | -0.048233 | 16.94 | 19.16 | 19.61 | 22.6 | 6.17 | 1.16 | 11 | 3.67
2018-11-22 23:00 | 11819.8542 | -0.048233 | 15.46 | 19.09 | 17.29 | 22.73 | 20.34 | 0.5 | 11 | 4.5
2018-11-23 | 11664.0542 | -0.048233 | 14.52 | 18.53 | 14.05 | 20.59 | 3.25 | 0.5 | 9.11 | 3.05
2018-11-23 01:00 | 12963.7891 | -0.048233 | 14.62 | 18.13 | 12.03 | 19.81 | 2.5 | 0.5 | 8.32 | 1.51
2018-11-23 02:00 | 12717.9741 | -0.048233 | 14.64 | 18.05 | 9.24 | 19.66 | 2.25 | 0.61 | 3.36 | 1
2018-11-23 03:00 | 12569.2191 | -0.048233 | 15.39 | 17.98 | 6.14 | 19.84 | 3 | 0.99 | 11.06 | 1
2018-11-23 04:00 | 11473.1042 | -0.048233 | 15.67 | 18.13 | 10.96 | 19.74 | 3 | 0.99 | 3.11 | 1.5
2018-11-23 05:00 | 13835.2191 | -0.048233 | 15.18 | 18.98 | 15.83 | 20.54 | 21.4 | 0.99 | 3.5 | 21.2
2018-11-23 06:00 | 14343.0542 | -0.048233 | 15.95 | 18.86 | 20.46 | 26.8 | 28.18 | 0.99 | 12 | 89.1162
2018-11-23 07:00 | 15365.6609 | 24.3799 | 17.63 | 19.14 | 22.7 | 30.09 | 35.57 | 10 | 3.5 | 35.57
2018-11-23 08:00 | 15302.4271 | 204.818 | 19.28 | 21.46 | 22.22 | 32.86 | 22.25 | 2 | 1.27 | 21.3
2018-11-23 09:00 | 15962.1821 | 211.297 | 19.58 | 21.28 | 21.77 | 34.32 | 12.94 | 2 | 0.27 | 4.11
2018-11-23 10:00 | 17704.8064 | 723.807 | 19.74 | 23.78 | 21.7 | 35.77 | 6.69 | 2 | 1.9 | 4.54
2018-11-23 11:00 | 16598.7064 | 566.371 | 299.1357 | 21.43 | 21.23 | 32.71 | 14.44 | 1.18 | 1.9 | 4.47
2018-11-23 12:00 | 14896.5187 | 250.546 | 17.88 | 21.24 | 20.75 | 30.76 | 4.15 | 2.42 | 1.88 | 3.95
2018-11-23 13:00 | 13773.5294 | 231.452 | 46.62 | 19.42 | 20.73 | 24.46 | 3.36 | 2.42 | 2 | 3.36
2018-11-23 14:00 | 11899.0758 | 189.343 | 16.68 | 20.43 | 20.04 | 23.03 | 3 | 2.32 | 2 | 2.86
2018-11-23 15:00 | 12832.1549 | 125.18 | 16.16 | 20.46 | 19.62 | 22.79 | 2.88 | 0.99 | 2 | 2.68
2018-11-23 16:00 | 11416.3039 | 52.162 | 42.35 | 20.87 | 21.62 | 23.06 | 2.76 | 0.99 | 1.96 | 2.28
2018-11-23 17:00 | 12501.6915 | 3.9446 | 51.92 | 20.69 | 25.54 | 30.19 | 2.91 | 0.99 | 2 | 2.71
2018-11-23 18:00 | 12421.5191 | -0.048233 | 17.81 | 19.37 | 23.02 | 31.04 | 32.15 | 1.18 | 2 | 21.91
2018-11-23 19:00 | 10922.1042 | -0.048233 | 16.18 | 19.01 | 21.94 | 28.73 | 21.93 | 1.58 | 3.11 | 4
2018-11-23 20:00 | 11781.1341 | -0.048233 | 16.37 | 18.03 | 20.99 | 24.17 | 4.16 | 1.19 | 2.11 | 3.84
2018-11-23 21:00 | 10322.6542 | -0.048233 | 43.81 | 17.65 | 20.69 | 23.48 | 3.11 | 1.14 | 3.5 | 2.83
2018-11-23 22:00 | 11179.7841 | -0.048233 | 14.99 | 17.04 | 19.71 | 22.31 | 3.2 | 1.09 | 11 | 3
2018-11-23 23:00 | 11059.5141 | -0.048233 | 13.35 | 16.73 | 19.48 | 21.72 | 4.46 | 0.61 | 11 | 4.46
2018-11-24 | 11013.0941 | -0.048233 | 13.38 | 17.08 | 19.63 | 21.55 | 27 | 0.61 | 11.36 | 3
2018-11-24 01:00 | 9833.4042 | -0.048233 | 14.13 | 17.85 | 17.45 | 22.8 | 25.38 | 0.61 | 7.05 | 3.41
2018-11-24 02:00 | 9813.4542 | -0.048233 | 13.8 | 19.04 | 16.01 | 22.24 | 5.51 | 0.61 | 3.44 | 1
2018-11-24 03:00 | 10778.8841 | -0.048233 | 13.77 | 18.19 | 16 | 22.3 | 25 | 0.99 | 3.5 | 1
2018-11-24 04:00 | 10852.7341 | -0.048233 | 88.72 | 88.72 | 16 | 22.32 | 25 | 0.99 | 2.61 | 24.8
2018-11-24 05:00 | 9896.1042 | -0.048233 | 14.85 | 21.73 | 19.58 | 22.6 | 25.37 | 0.99 | 3.44 | 25.17
2018-11-24 06:00 | 9812.5042 | -0.048233 | 16 | 17.94 | 20.26 | 26.2 | 50.01 | 0.99 | 12.38 | 50.01
2018-11-24 07:00 | 9702.8971 | 21.5759 | 15.82 | 18.04 | 21.32 | 25.74 | 50.01 | 2 | 11 | 95.1162
2018-11-24 08:00 | 11136.6479 | 94.0644 | 15.4 | 18.13 | 21.54 | 27.9 | 20 | 2 | 3.79 | 3.21
2018-11-24 09:00 | 11522.3946 | 165.701 | 17.85 | 20.53 | 21.34 | 29.08 | 5.58 | 2 | 0.97 | 3.5
2018-11-24 10:00 | 11896.967 | 218.746 | 17.75 | 21.64 | 20.48 | 31.38 | 5.74 | 2 | 2.11 | 4.68
2018-11-24 11:00 | 11291.0549 | 791.321 | 40.93 | 20.63 | 19.35 | 33.88 | 7.62 | 1 | 3.01 | 4
2018-11-24 12:00 | 12702.3582 | 1125.15 | 44.03 | 19.4 | 19.21 | 32.88 | 7.5 | 1.87 | 2 | 4
2018-11-24 13:00 | 10677.6172 | 233.597 | 17.09 | 19.4 | 18.88 | 33.82 | 16.9 | 1 | 3.01 | 4
2018-11-24 14:00 | 11420.6416 | 675.728 | 16.8 | 30.94 | 17.71 | 30.67 | 18.73 | 1.58 | 2.61 | 3.66
2018-11-24 15:00 | 12550.2526 | 350.974 | 16.56 | 25.13 | 17.97 | 28.92 | 20 | 0.99 | 2.11 | 3.1
2018-11-24 16:00 | 11470.1081 | 312.798 | 16.34 | 19.05 | 20.03 | 29.48 | 7.5 | 0.99 | 2.11 | 3.11
2018-11-24 17:00 | 11109.1572 | 10.8497 | 17.21 | 18.04 | 20.26 | 36.96 | 5.79 | 0.99 | 2 | 3.2
2018-11-24 18:00 | 12155.6591 | -0.048233 | 17.25 | 17.25 | 20.27 | 28.13 | 17.4 | 1 | 2.11 | 17.07
2018-11-24 19:00 | 10802.4042 | -0.048233 | 16.36 | 16.36 | 18.58 | 26.07 | 8.78 | 1.13 | 3.5 | 3.78
2018-11-24 20:00 | 11850.7641 | -0.048233 | 15.88 | 15.88 | 18.04 | 24.4 | 7.5 | 1 | 3.5 | 3.3
2018-11-24 21:00 | 11841.2691 | -0.048233 | 12.78 | 12.78 | 19.84 | 23.01 | 6.1 | 1 | 3.5 | 3.1
2018-11-24 22:00 | 11789.5741 | -0.048233 | 11.28 | 11.28 | 19.31 | 18.98 | 7.5 | 1 | 12.51 | 5.04
2018-11-24 23:00 | 10557.3042 | -0.048233 | 1.34 | 1.34 | 19.11 | 18.05 | 26.84 | 0.5 | 12.87 | 26.84
2018-11-25 | 10491.7542 | -0.048233 | 2.58 | 3.38 | 17.87 | 14.49 | 27.71 | 0.5 | 13.94 | 27.71
2018-11-25 01:00 | 11522.6591 | -0.048233 | 3.86 | 3.86 | 17.18 | 12.18 | 25 | 0.61 | 8 | 3.06
2018-11-25 02:00 | 11444.5891 | -0.048233 | 5.32 | 12.32 | 16.1 | 13.11 | 25 | 0.5 | 4 | 1
2018-11-25 03:00 | 10351.1542 | -0.048233 | 0.01 | 9.32 | 16.11 | 16.54 | 25 | 0.99 | 4 | 1
2018-11-25 04:00 | 10514.5542 | -0.048233 | 4.6 | 4.6 | 17.3 | 16.9 | 50 | 0.99 | 3.65 | 1.26
2018-11-25 05:00 | 10649.4542 | -0.048233 | 6.79 | 6.79 | 18.34 | 16.22 | 50 | 0.99 | 3.5 | 2.31
2018-11-25 06:00 | 10900.2542 | -0.048233 | 10.65 | 10.65 | 19.73 | 22.2 | 26.96 | 1 | 14.38 | 26.96
2018-11-25 07:00 | 11994.6551 | 45.3413 | 13.91 | 13.91 | 19.96 | 24.14 | 34 | 2 | 11 | 34
2018-11-25 08:00 | 11203.2255 | 326.869 | 15.14 | 17.69 | 19.43 | 26.11 | 8.21 | 2 | 3.5 | 3.3
2018-11-25 09:00 | 12281.9692 | 151.677 | 17.04 | 17.19 | 20.55 | 29.15 | 8.36 | 2 | 1.99 | 3.5
2018-11-25 10:00 | 12469.2085 | 204.155 | 16.81 | 16.81 | 20.19 | 26.95 | 8.11 | 2 | 2.11 | 3.66
2018-11-25 11:00 | 13098.6964 | 779.826 | 16.91 | 16.91 | 19.9 | 27.85 | 8.11 | 1.39 | 11 | 4
2018-11-25 12:00 | 12056.1878 | 965.724 | 16.72 | 19.13 | 18.79 | 28.6 | 8.11 | 1.16 | 3.11 | 3.5
2018-11-25 13:00 | 12153.3899 | 896.042 | 16.75 | 19.28 | 18.66 | 29.96 | 8.11 | 1.04 | 2.81 | 3.3
2018-11-25 14:00 | 13206.9753 | 536.46 | 16.2 | 23.28 | 18.42 | 39.55 | 7.5 | 1.4 | 2.99 | 3.5
2018-11-25 15:00 | 12058.0374 | 604.671 | 16.34 | 21.6 | 18.78 | 39.48 | 7.5 | 0.99 | 3.01 | 3.3
2018-11-25 16:00 | 11719.3824 | 165.192 | 16.25 | 20.26 | 22.13 | 31.23 | 7.5 | 0.99 | 2.38 | 3.3
2018-11-25 17:00 | 12220.9338 | 3.8235 | 17.34 | 19.21 | 33.23 | 35.76 | 7.5 | 0.99 | 1 | 3.5
2018-11-25 18:00 | 10590.0391 | -0.048233 | 53.88 | 19.72 | 21.97 | 31.88 | 22.33 | 0.99 | 2.11 | 17.53
2018-11-25 19:00 | 10386.4241 | -0.048233 | 17.12 | 18.4 | 21.55 | 27.72 | 15.01 | 2.1 | 2.5 | 4.1
2018-11-25 20:00 | 10031.0042 | -0.048233 | 16.64 | 17.66 | 19.62 | 26.59 | 8.11 | 1.4 | 2.5 | 3.52
2018-11-25 21:00 | 10531.6542 | -0.048233 | 15.22 | 18.79 | 20.38 | 26.16 | 4.97 | 1.22 | 11 | 3.31
2018-11-25 22:00 | 10354.9542 | -0.048233 | 16.34 | 19.47 | 18.8 | 25.69 | 6.9 | 1.13 | 11.35 | 4
2018-11-25 23:00 | 10173.5042 | -0.048233 | 15.43 | 19.21 | 17.68 | 24.1 | 17.06 | 0.61 | 20.01 | 17.06
2018-11-26 | 9947.4042 | -0.048233 | 9.14 | 19.06 | 15.72 | 19.94 | 16.32 | 0.61 | 20.01 | 3.5
2018-11-26 01:00 | 10938.1891 | -0.048233 | 5.23 | 19.02 | 14.02 | 19.58 | 5 | 0.61 | 9.11 | 2.9
2018-11-26 02:00 | 10802.0941 | -0.048233 | 0.17 | 19.01 | 13.18 | 19.24 | 5 | 0.61 | 3.38 | 1
2018-11-26 03:00 | 9573.1042 | -0.048233 | 0.36 | 19.01 | 13.65 | 19.68 | 25 | 0.99 | 3.5 | 1
2018-11-26 04:00 | 10527.7941 | -0.048233 | 6.19 | 19.16 | 13.82 | 19.49 | 25 | 1 | 2.11 | 1
2018-11-26 05:00 | 9486.6542 | -0.048233 | 8.65 | 19.47 | 15.66 | 20.35 | 50 | 0.99 | 3.5 | 2.31
2018-11-26 06:00 | 10672.3291 | -0.048233 | 14.28 | 18.89 | 15.97 | 22.29 | 28.14 | 0.99 | 12.35 | 28.14
2018-11-26 07:00 | 10642.4204 | 57.6023 | 16.53 | 19.15 | 15.96 | 23.55 | 102.3741 | 1 | 13.84 | 101.6762
2018-11-26 08:00 | 9785.0133 | 293.014 | 18.04 | 20.12 | 16.1 | 24.35 | 29 | 1 | 3.46 | 3
2018-11-26 09:00 | 10103.3707 | 521.127 | 61.02 | 61.02 | 17.98 | 26.56 | 5.61 | 1.42 | 1.29 | 3.1
2018-11-26 10:00 | 10445.9976 | 853.787 | 58.2 | 26.64 | 18.26 | 27.38 | 7.72 | 1.7 | 2 | 3.3
2018-11-26 11:00 | 11280.4113 | 618.333 | 161.26 | 22.32 | 18.21 | 28.13 | 8.11 | 1 | 11.4 | 3.53
2018-11-26 12:00 | 10651.4741 | 948.078 | 19.6 | 21.94 | 17.84 | 29.84 | 8.61 | 1 | 3 | 3.1
2018-11-26 13:00 | 11620.8683 | 356.041 | 19.65 | 28.64 | 17.04 | 31.95 | 15 | 1.27 | 2.61 | 3.3
2018-11-26 14:00 | 11035.8498 | 879.684 | 17.72 | 31.21 | 16.39 | 28.71 | 8.11 | 1 | 2.61 | 3
2018-11-26 15:00 | 12044.7219 | 563.798 | 17.67 | 26.14 | 16.54 | 28.8 | 6 | 1 | 3 | 3
2018-11-26 16:00 | 11810.4602 | 212.749 | 154.48 | 154.48 | 18 | 32.05 | 6 | 1 | 2.11 | 3
2018-11-26 17:00 | 10337.0838 | 5.1409 | 46 | 46 | 29.01 | 46.39 | 8.11 | 0.97 | 2 | 3
2018-11-26 18:00 | 10294.1542 | -0.048233 | 17.79 | 30.55 | 18.48 | 43.56 | 24.19 | 1.48 | 2.11 | 19.92
2018-11-26 19:00 | 10163.0542 | -0.048233 | 18.01 | 26.61 | 17.93 | 34.92 | 15 | 2.01 | 3 | 4.1
2018-11-26 20:00 | 10126.0042 | -0.048233 | 18.4 | 19.71 | 17.72 | 33.27 | 9.01 | 1.3 | 3.5 | 3
2018-11-26 21:00 | 9999.6542 | -0.048233 | 18.43 | 19.18 | 17.61 | 24.81 | 8 | 1.39 | 12 | 3.1
2018-11-26 22:00 | 10942.4091 | -0.048233 | 17.14 | 18.25 | 15.76 | 20.97 | 16 | 1.18 | 38.86 | 7.11
2018-11-26 23:00 | 10872.7791 | -0.048233 | 14.19 | 16.6 | 14.95 | 18.48 | 30.54 | 0.5 | 100.8634 | 30.54
2018-11-27 | 10879.1091 | -0.048233 | 14.81 | 16.83 | 11 | 14.55 | 27.61 | 0.5 | 16 | 27.61
2018-11-27 01:00 | 9851.4542 | -0.048233 | 5.38 | 15.15 | 7.37 | 11.91 | 15 | 0.61 | 12.07 | 8
2018-11-27 02:00 | 10835.8541 | -0.048233 | 0 | 12.03 | 2.66 | 13.12 | 15 | 0.61 | 4 | 3.11
2018-11-27 03:00 | 9753.6042 | -0.048233 | -0.46 | 13.59 | 2.59 | 15.67 | 26.51 | 1 | 9.09 | 2.75
2018-11-27 04:00 | 9792.5542 | -0.048233 | -0.58 | 15.84 | 3.2 | 18.9 | 26.75 | 1 | 4 | 2.65
2018-11-27 05:00 | 9775.4542 | -0.048233 | -0.66 | 17.69 | 10.89 | 20.81 | 28.62 | 1 | 11.67 | 4
2018-11-27 06:00 | 10936.0791 | -0.048233 | -0.56 | 19.54 | 15.28 | 28.18 | 29.71 | 1.22 | 22 | 30
2018-11-27 07:00 | 9806.5135 | 41.6458 | -0.37 | 19.53 | 15.7 | 28.29 | 34 | 1.43 | 22 | 34
2018-11-27 08:00 | 10099.9981 | 224.577 | 11.83 | 19.41 | 15.93 | 28.42 | 15 | 1 | 18.52 | 3.11
2018-11-27 09:00 | 11813.2802 | 580.422 | 13.79 | 24.43 | 16.93 | 28.71 | 15 | 1.62 | 2.11 | 12.87
2018-11-27 10:00 | 11885.63 | 413 | 0.01 | 25.8 | 17.76 | 29.37 | 17.33 | 1.64 | 3.11 | 5.62
2018-11-27 11:00 | 12738.3865 | 1031.3 | 4.49 | 30.63 | 17.76 | 30.83 | 17.16 | 2 | 11 | 3.3
2018-11-27 12:00 | 12756.1327 | 916.121 | 9.49 | 23.79 | 17.75 | 33.07 | 19.35 | 2 | 3.5 | 3.3
2018-11-27 13:00 | 11666.8826 | 936.929 | 13.76 | 24.81 | 16.32 | 34.66 | 21.77 | 2 | 2.68 | 3.3
2018-11-27 14:00 | 11515.4145 | 736.489 | 14.79 | 24.01 | 15.92 | 33.3 | 23.91 | 2 | 3.11 | 3.3
2018-11-27 15:00 | 11538.9517 | 583.265 | 15.69 | 23.79 | 16.15 | 33.24 | 5.81 | 1 | 2.99 | 3.11
2018-11-27 16:00 | 12628.2276 | 268.884 | 11.16 | 19.16 | 19.61 | 37.08 | 5.01 | 1.07 | 3.01 | 3.01
2018-11-27 17:00 | 11103.4733 | 10.8666 | 93.88 | 18.01 | 31.35 | 41.91 | 6.08 | 0.97 | 2.11 | 3.5
2018-11-27 18:00 | 11176.7042 | -0.048233 | 17.5 | 20.68 | 28.75 | 32.96 | 28.45 | 1.29 | 2.64 | 28.25
2018-11-27 19:00 | 11077.9042 | -0.048233 | 15.85 | 15.85 | 24.35 | 31.86 | 23.57 | 2 | 3.5 | 4
2018-11-27 20:00 | 11009.5042 | -0.048233 | 13.92 | 13.92 | 17.5 | 26.7 | 19.71 | 1.42 | 3.5 | 3.5
2018-11-27 21:00 | 12177.8141 | -0.048233 | 76.7 | 13.35 | 17.11 | 29.19 | 7.61 | 1.25 | 11 | 3.11
2018-11-27 22:00 | 12210.5191 | -0.048233 | 13.87 | 13.87 | 16.56 | 18.56 | 14 | 1.22 | 11 | 6.99
2018-11-27 23:00 | 10976.2542 | -0.048233 | 2.16 | 2.16 | 15.66 | 17.49 | 25 | 0.61 | 20.01 | 25
2018-11-28 | 12081.8091 | -0.048233 | -2.27 | -2.27 | 15.44 | 10.58 | 15 | 0.61 | 11 | 5.96
2018-11-28 01:00 | 11976.3091 | -0.048233 | 73.94 | -3.03 | 5.13 | 11.11 | 4.67 | 0.49 | 12.89 | 2.32
2018-11-28 02:00 | 10766.3042 | -0.048233 | -3.9 | -3.9 | 3.96 | 10.59 | 4 | 0.49 | 12.25 | 2
2018-11-28 03:00 | 12031.1691 | -0.048233 | -2.29 | -2.29 | 3.91 | 11.05 | 15.5 | 1 | 13.11 | 2
2018-11-28 04:00 | 12429.9591 | -0.048233 | -0.64 | -0.64 | 4.62 | 11.51 | 16 | 1 | 13.2 | 2
2018-11-28 05:00 | 12195.1042 | -0.048233 | 3.57 | 3.57 | 5.13 | 14.78 | 17 | 1 | 8.61 | 2.32
2018-11-28 06:00 | 14257.5542 | -0.048233 | 11.85 | 11.85 | 15.7 | 23.51 | 25 | 1 | 11.04 | 27.9
2018-11-28 07:00 | 15328.876 | 21.659 | 14.49 | 14.49 | 22.58 | 24.1 | 27.82 | 1.42 | 11 | 27.82
2018-11-28 08:00 | 17483.9895 | 78.5019 | 12.43 | 12.43 | 17 | 25.98 | 7.49 | 1.32 | 3.5 | 3.11
2018-11-28 09:00 | 16656.9608 | 325.643 | 12.06 | 12.06 | 17.02 | 27.38 | 13 | 1.74 | 2 | 4.02
2018-11-28 10:00 | 16582.7022 | 202.476 | 10.84 | 10.84 | 17.63 | 27.84 | 15 | 1.58 | 3.33 | 3.5
2018-11-28 11:00 | 16590.9691 | 234.178 | 11.37 | 11.37 | 17.77 | 31.51 | 15.44 | 1.5 | 2.11 | 3.5
2018-11-28 12:00 | 19479.1887 | 241.686 | 16.79 | 16.79 | 18.11 | 30.22 | 16 | 1.95 | 2.44 | 4.2
2018-11-28 13:00 | 17424.7195 | 221.81 | 56.24 | 17.68 | 17.45 | 33.44 | 16.94 | 1.95 | 2.42 | 4.56
2018-11-28 14:00 | 15157.8086 | 180.588 | 43.93 | 31.51 | 16.92 | 39.45 | 20.17 | 1.92 | 2.11 | 3.56
2018-11-28 15:00 | 15878.7417 | 118.94 | 261.0157 | 33.41 | 17.6 | 38.33 | 24.33 | 1 | 3.5 | 3
2018-11-28 16:00 | 13948.398 | 48.5242 | 68.64 | 20.49 | 22.96 | 36.68 | 22 | 0.97 | 1.96 | 3
2018-11-28 17:00 | 15298.1788 | 7.6434 | 16.94 | 16.94 | 32.73 | 43.19 | 22 | 0.97 | 2.11 | 3.11
2018-11-28 18:00 | 13698.9542 | -0.048233 | 191.09 | 18.5 | 23.68 | 33.09 | 35 | 0.97 | 2.43 | 31
2018-11-28 19:00 | 15091.7241 | -0.048233 | 16.78 | 16.78 | 23.07 | 30.47 | 23.53 | 1 | 3.5 | 17.42
2018-11-28 20:00 | 13256.2542 | -0.048233 | 359.6357 | 17.92 | 20.12 | 31.05 | 16.83 | 1.25 | 2 | 3.5
2018-11-28 21:00 | 14296.2541 | -0.048233 | 19.6 | 19.6 | 19.29 | 27.17 | 6.31 | 1 | 3.11 | 3.15
2018-11-28 22:00 | 13820.4491 | -0.048233 | 19.13 | 19.13 | 18.02 | 22.45 | 6.01 | 1 | 3.5 | 5.93
2018-11-28 23:00 | 13608.3941 | -0.048233 | 17.36 | 17.36 | 17.21 | 21.63 | 15 | 0.5 | 8.38 | 3.5
2018-11-29 | 13387.8991 | -0.048233 | 15.56 | 15.56 | 15.72 | 19.28 | 16.69 | 0.5 | 8.61 | 3.3
2018-11-29 01:00 | 13385.7891 | -0.048233 | 16.17 | 16.83 | 14.36 | 18.65 | 7.25 | 0.5 | 20 | 7
2018-11-29 02:00 | 12019.3542 | -0.048233 | 15.73 | 17.56 | 12.91 | 18.87 | 5.73 | 0.5 | 10.29 | 3.11
2018-11-29 03:00 | 13423.7691 | -0.048233 | 16.97 | 17.69 | 14.34 | 18.65 | 7 | 1 | 10.99 | 3.06
2018-11-29 04:00 | 13541.9291 | -0.048233 | 17.3 | 17.67 | 15.17 | 19.48 | 6.01 | 1 | 3.46 | 3.11
2018-11-29 05:00 | 13128.0042 | -0.048233 | 17.03 | 17.03 | 15.7 | 21.78 | 7.11 | 1 | 3.3 | 3.92
2018-11-29 06:00 | 15190.4542 | -0.048233 | 17.82 | 17.82 | 15.7 | 28.02 | 25 | 1 | 38.24 | 37.08
2018-11-29 07:00 | 17914.6044 | 21.6677 | 18.78 | 18.78 | 15.66 | 27.63 | 19 | 2.15 | 11 | 40.46
2018-11-29 08:00 | 18342.3043 | 76.0704 | 94.9 | 18.81 | 16.08 | 28.42 | 5.11 | 2 | 2.11 | 3.5
2018-11-29 09:00 | 18982.8344 | 147.208 | 20.73 | 20.73 | 17.59 | 30.99 | 6.46 | 2.09 | 0.86 | 5.98
2018-11-29 10:00 | 17076.782 | 201.56 | 19.8 | 21.23 | 17.85 | 31.72 | 15.61 | 2.2 | 1.55 | 15.61
2018-11-29 11:00 | 17562.6975 | 710.05 | 20.17 | 20.94 | 17.56 | 32.37 | 14.68 | 2.1 | 1.9 | 4.97
2018-11-29 12:00 | 20321.0777 | 647.685 | 20.51 | 20.51 | 17.05 | 33.24 | 14.19 | 2.5 | 2 | 4.99
2018-11-29 13:00 | 19593.8725 | 694.391 | 35.47 | 20.06 | 16.12 | 33.34 | 7 | 2.55 | 1.9 | 4.37
2018-11-29 14:00 | 18573.313 | 778.036 | 68.51 | 19.98 | 16.14 | 33.44 | 6.01 | 2.5 | 1.9 | 3.44
2018-11-29 15:00 | 15580.191 | 318.201 | 245.0357 | 20.34 | 16.56 | 33.61 | 4.78 | 0.97 | 1.9 | 3.03
2018-11-29 16:00 | 16825.3046 | 166.156 | 155.43 | 19.43 | 22.08 | 33.24 | 4.7 | 1 | 1.43 | 1.57
2018-11-29 17:00 | 16378.2405 | 5.3986 | 172.42 | 19.1 | 22.35 | 53.14 | 5 | 1.7 | 1.59 | 3.2
2018-11-29 18:00 | 16030.6741 | -0.048233 | 859.2111 | 27.08 | 21.57 | 36.74 | 33.14 | 2 | 2 | 33.14
2018-11-29 19:00 | 14256.6042 | -0.048233 | 155.87 | 20.04 | 21.57 | 33.87 | 20.7 | 2.27 | 2 | 20.65
2018-11-29 20:00 | 15398.7291 | -0.048233 | 277.7157 | 233.39 | 20.72 | 35.53 | 6.01 | 1 | 1 | 1.57
2018-11-29 21:00 | 14896.5491 | -0.048233 | 37.14 | 23.57 | 20.07 | 29.38 | 6.01 | 1.51 | 1.9 | 3.1
2018-11-29 22:00 | 12996.9042 | -0.048233 | 87.7 | 19.84 | 18.15 | 26.37 | 4.93 | 1.34 | 3.5 | 3.98
2018-11-29 23:00 | 13835.2191 | -0.048233 | 19.11 | 19.11 | 17.35 | 24.54 | 6.01 | 0.82 | 8.61 | 4.01
2018-11-30 | 11793.2542 | -0.048233 | 98.38 | 98.38 | 17.49 | 23.65 | 6.82 | 0.82 | 8.61 | 3.53
2018-11-30 01:00 | 11170.0542 | -0.048233 | 17.1 | 22.81 | 17.4 | 22.81 | 3.79 | 0.97 | 3.95 | 1
2018-11-30 02:00 | 12202.0791 | -0.048233 | 15.51 | 19.8 | 13.77 | 18.89 | 3.5 | 0.97 | 3.01 | 0.75
2018-11-30 03:00 | 10866.0542 | -0.048233 | 9.95 | 19.07 | 13.91 | 19.47 | 3.5 | 1.42 | 3.19 | 0.5
2018-11-30 04:00 | 10791.9542 | -0.048233 | 16.54 | 18.51 | 17.94 | 19.27 | 3.5 | 1.42 | 2.22 | 0.75
2018-11-30 05:00 | 12835.0791 | -0.048233 | 4.27 | 20.09 | 19.79 | 23.56 | 3.21 | 1.42 | 3.27 | 1.31
2018-11-30 06:00 | 13323.7042 | -0.048233 | 6.58 | 19.32 | 23.91 | 28.64 | 5.24 | 1.42 | 18.11 | 5.24
2018-11-30 07:00 | 14297.7447 | 24.2576 | 121.71 | 21.32 | 29.22 | 28.26 | 31.67 | 12 | 2.11 | 31.67
2018-11-30 08:00 | 15781.784 | 395.037 | 47.33 | 19.99 | 23.6 | 28.12 | 16.18 | 7.62 | 2.11 | 14.18
2018-11-30 09:00 | 17011.0648 | 762.232 | 19.91 | 19.91 | 19.73 | 27.82 | 4.99 | 8.49 | 1 | 2.99
2018-11-30 10:00 | 17451.9999 | 484.18 | 20.15 | 20.15 | 19.36 | 28.41 | 5.35 | 8.5 | 2.11 | 3.3
2018-11-30 11:00 | 16427.1518 | 1141.76 | 20.26 | 24.01 | 17.79 | 29.71 | 4.45 | 7.01 | 3.01 | 2
2018-11-30 12:00 | 15719.08 | 1142.4 | 20.33 | 28.9 | 17.48 | 32.47 | 4.62 | 2.1 | 2.61 | 1.89
2018-11-30 13:00 | 15445.233 | 1066.14 | 20.3 | 27.21 | 17.02 | 35.05 | 4.42 | 2.48 | 2 | 1.54
2018-11-30 14:00 | 14037.2694 | 874.073 | 19.46 | 26.36 | 16.92 | 36.67 | 4.8 | 2.45 | 2 | 2.19
2018-11-30 15:00 | 14174.2426 | 624.301 | 19.07 | 25.65 | 17.84 | 36.61 | 4.9 | 1 | 2.11 | 3
2018-11-30 16:00 | 13487.8479 | 268.69 | 19.65 | 23.83 | 23.63 | 36.41 | 4.12 | 1 | 1.53 | 1.48
2018-11-30 17:00 | 12999.1397 | 12.4594 | 20.08 | 20.32 | 33.61 | 52.08 | 4.6 | 1 | 1.68 | 2.09
2018-11-30 18:00 | 12896.2691 | -0.048233 | 34.31 | 22.99 | 29.83 | 38.89 | 27.78 | 10 | 2.26 | 22.98
2018-11-30 19:00 | 11496.8542 | -0.048233 | 20.89 | 20.89 | 28.09 | 32.73 | 14.39 | 10 | 3.5 | 12.81
2018-11-30 20:00 | 12378.2641 | -0.048233 | 60.22 | 19.69 | 21.88 | 28.52 | 6.88 | 1 | 1 | 2.22
2018-11-30 21:00 | 11061.7542 | -0.048233 | 20.41 | 20.41 | 20.45 | 30.14 | 6.02 | 1 | 2.3 | 1.48
2018-11-30 22:00 | 10623.8042 | -0.048233 | 19.63 | 19.78 | 18.69 | 22.75 | 4.86 | 1.41 | 3.5 | 2.84
2018-11-30 23:00 | 11209.3241 | -0.048233 | 19.13 | 19.29 | 16.84 | 20.19 | 6.51 | 0.97 | 11 | 3
2018-12-01 | 10018.6542 | -0.048233 | 18.52 | 18.69 | 16.73 | 21.79 | 15 | 0.97 | 11 | 3
2018-12-01 01:00 | 10040.5042 | -0.048233 | 18.11 | 18.41 | 13 | 19.26 | 2.76 | 0.95 | 3.82 | 2.76
2018-12-01 02:00 | 11109.0991 | -0.048233 | 17.05 | 18.06 | 13.43 | 19 | 2.51 | 0.95 | 2.89 | 1
2018-12-01 03:00 | 11010.9841 | -0.048233 | 17.39 | 17.73 | 13.21 | 18.92 | 3 | 0.99 | 3.01 | 1
2018-12-01 04:00 | 10228.6042 | -0.048233 | 17.51 | 17.51 | 13.27 | 18.96 | 3 | 0.99 | 2.05 | 1
2018-12-01 05:00 | 11330.6042 | -0.048233 | 17.36 | 18.42 | 14.12 | 20.75 | 3.01 | 0.99 | 3.77 | 2.61
2018-12-01 06:00 | 13242.9542 | -0.048233 | 40.93 | 40.93 | 20.31 | 28.75 | 5 | 0.99 | 38 | 18.84
2018-12-01 07:00 | 15594.9591 | -0.048233 | 33.7 | 22.42 | 21.4 | 27.21 | 35 | 22.14 | 1.5 | 35
2018-12-01 08:00 | 14524.987 | 431.46 | 19.73 | 26.41 | 20.65 | 28.49 | 15.22 | 8 | 2.11 | 3.61
2018-12-01 09:00 | 16618.5721 | 614.201 | 35.79 | 35.79 | 19.52 | 27.73 | 7.05 | 6 | 0.31 | 3.63
2018-12-01 10:00 | 15750.5725 | 757.55 | 35.05 | 35.05 | 18.07 | 28.1 | 8.96 | 5.54 | 1 | 5.37
2018-12-01 11:00 | 16180.4422 | 296.912 | 38.28 | 38.28 | 18.08 | 29.59 | 6.82 | 1.62 | 1.7 | 3
2018-12-01 12:00 | 18341.3259 | 704.143 | 61.56 | 61.56 | 18.05 | 30.16 | 5.66 | 1.78 | 1.61 | 2.29
2018-12-01 13:00 | 14303.3501 | 180.158 | 51.11 | 51.11 | 17.89 | 32.64 | 6.01 | 1.82 | 2.55 | 3
2018-12-01 14:00 | 15276.2607 | 484.868 | 41.46 | 41.46 | 17.88 | 33.67 | 5.36 | 2 | 1 | 2.11
2018-12-01 15:00 | 14652.6903 | 582.806 | 17.92 | 29.03 | 18.06 | 32.88 | 5 | 1 | 1.34 | 2.11
2018-12-01 16:00 | 12326.7725 | 185.55 | 18.74 | 31.66 | 21.8 | 33.08 | 4.41 | 1 | 0.24 | 2.11
2018-12-01 17:00 | 12066.8412 | 2.9381 | 21.35 | 22.8 | 23.82 | 48.73 | 4.68 | 0.99 | 0.71 | 3
2018-12-01 18:00 | 13415.3291 | -0.048233 | 22.41 | 22.41 | 22.11 | 32.12 | 32.79 | 2 | 1.97 | 25.35
2018-12-01 19:00 | 13212.7691 | -0.048233 | 19.84 | 19.84 | 21.57 | 26.8 | 15.22 | 1.75 | 3.5 | 4
2018-12-01 20:00 | 12954.2941 | -0.048233 | 19.28 | 19.28 | 20.2 | 25.47 | 8.4 | 1 | 3.5 | 3.26
2018-12-01 21:00 | 12857.2341 | -0.048233 | 18.84 | 18.84 | 18.17 | 22.87 | 5.76 | 0.99 | 3.47 | 3.1
2018-12-01 22:00 | 11370.5042 | -0.048233 | 20.15 | 20.15 | 18.11 | 20.74 | 6.07 | 1 | 10.03 | 3
2018-12-01 23:00 | 10966.7542 | -0.048233 | 17.36 | 17.36 | 15.43 | 17.76 | 17 | 0.95 | 54.6962 | 3
2018-12-02 | 12197.8591 | -0.048233 | 15.38 | 15.38 | 15.6 | 18.21 | 15 | 0.74 | 54.6962 | 2.7
2018-12-02 01:00 | 12246.3891 | -0.048233 | 14.16 | 14.16 | 12.1 | 16.84 | 3.06 | 0.5 | 10.04 | 1
2018-12-02 02:00 | 10981.9542 | -0.048233 | 17.02 | 17.02 | 8.23 | 16.81 | 19.96 | 0.5 | 3.11 | 1
2018-12-02 03:00 | 12165.1541 | -0.048233 | 16.42 | 16.42 | 8.12 | 17.2 | 29.25 | 0.89 | 2.62 | 1
2018-12-02 04:00 | 11194.7542 | -0.048233 | 15.35 | 15.35 | 13.01 | 18.17 | 3 | 0.89 | 2.61 | 1
2018-12-02 05:00 | 13395.2841 | -0.048233 | 11.79 | 11.79 | 16.67 | 19.44 | 3.18 | 0.89 | 4 | 1
2018-12-02 06:00 | 15638.2141 | -0.048233 | 16.38 | 16.38 | 19.66 | 24.12 | 15.64 | 0.89 | 117.7434 | 15.64
2018-12-02 07:00 | 16889.4441 | -0.048233 | 17.1 | 17.1 | 21.25 | 22.78 | 40.04 | 57.3373 | 11.93 | 40.04
2018-12-02 08:00 | 17154.4182 | 292.112 | 17.72 | 17.72 | 20.76 | 24.59 | 16.59 | 15.16 | 2.66 | 16.57
2018-12-02 09:00 | 15893.0174 | 154.492 | 18.99 | 18.99 | 20.91 | 26.72 | 8.11 | 10.12 | 1 | 2.75
2018-12-02 10:00 | 18672.4714 | 894.025 | 19.78 | 19.78 | 20.96 | 27.04 | 8.79 | 8.58 | 1.65 | 5.3
2018-12-02 11:00 | 18407.4501 | 1032.82 | 19.03 | 19.96 | 20.29 | 27.85 | 6.74 | 1.9 | 2 | 2.75
2018-12-02 12:00 | 16742.8095 | 1127.01 | 18 | 20.16 | 20.07 | 29.63 | 7.11 | 1.9 | 2.11 | 2.8
2018-12-02 13:00 | 17923.8592 | 1041.44 | 17.69 | 21.45 | 19.95 | 29.33 | 6.72 | 1.9 | 2.11 | 2.75
2018-12-02 14:00 | 16574.7938 | 879.705 | 17.82 | 22.06 | 18.64 | 30.68 | 6.76 | 1.9 | 1.17 | 2.75
2018-12-02 15:00 | 15688.4682 | 607.586 | 17.94 | 28.42 | 19.5 | 29.76 | 6.16 | 0.9 | 1.71 | 1.64
2018-12-02 16:00 | 14902.1398 | 257.251 | 18.01 | 20.12 | 21.72 | 29.6 | 6.3 | 0.9 | 1.15 | 1
2018-12-02 17:00 | 13165.0542 | -0.048233 | 19.34 | 20.88 | 22.5 | 47.86 | 5.08 | 0.89 | 1 | 2.75
2018-12-02 18:00 | 13000.7042 | -0.048233 | 20.94 | 25.66 | 21 | 31 | 27.73 | 23.95 | 2.22 | 25.45
2018-12-02 19:00 | 14068.3741 | -0.048233 | 309.8557 | 265.53 | 19.89 | 26.29 | 27.09 | 26.4 | 2.11 | 26.8
2018-12-02 20:00 | 13619.9991 | -0.048233 | 21.49 | 23.33 | 19.64 | 23.13 | 8.28 | 13.26 | 2.61 | 2.67
2018-12-02 21:00 | 12083.0042 | -0.048233 | 20.19 | 20.81 | 19.49 | 24.63 | 6.97 | 1 | 2.61 | 1.9
2018-12-02 22:00 | 12908.9291 | -0.048233 | 19.91 | 20.41 | 17.26 | 20.57 | 5.7 | 1 | 3.5 | 1.44
2018-12-02 23:00 | 11228.9542 | -0.048233 | 18.15 | 19.71 | 14.3 | 19.7 | 17 | 0.61 | 16.27 | 5.9
2018-12-03 | 10938.2542 | -0.048233 | 17.75 | 18.67 | 13.19 | 20.36 | 16.12 | 0.61 | 14.68 | 3
2018-12-03 01:00 | 10670.3542 | -0.048233 | 16.96 | 17.41 | 6.82 | 18.89 | 3.01 | 0.61 | 3.46 | 1
2018-12-03 02:00 | 10510.7542 | -0.048233 | 16.92 | 16.92 | 4.43 | 18.03 | 2.76 | 0.61 | 3.11 | 1
2018-12-03 03:00 | 10370.1542 | -0.048233 | 16.67 | 16.67 | 4 | 17.73 | 3 | 0.97 | 2.33 | 1
2018-12-03 04:00 | 10415.7542 | -0.048233 | 17.36 | 17.54 | 7 | 17.64 | 3 | 0.97 | 2.22 | 1
2018-12-03 05:00 | 10471.8042 | -0.048233 | 17.37 | 17.37 | 15.99 | 18.21 | 3 | 0.97 | 4 | 1
2018-12-03 06:00 | 10664.6542 | -0.048233 | 17.73 | 17.73 | 20.82 | 20.76 | 15.25 | 0.97 | 117.7434 | 15.25
2018-12-03 07:00 | 11928.8341 | -0.048233 | 17.93 | 17.93 | 20.63 | 20.51 | 51.34 | 68.6473 | 3.25 | 51.34
2018-12-03 08:00 | 11302.0863 | 371.933 | 17.32 | 17.32 | 19.51 | 20.89 | 19.91 | 19.91 | 8.26 | 19.48
2018-12-03 09:00 | 12870.0621 | 613.111 | 18.1 | 18.1 | 19.93 | 21.77 | 5.43 | 10.25 | 1 | 4.43
2018-12-03 10:00 | 12924.1931 | 846.42 | 18.41 | 18.7 | 20.37 | 23.1 | 7.21 | 7.67 | 2.11 | 3.71
2018-12-03 11:00 | 12822.0575 | 854.609 | 17.52 | 18.34 | 19.64 | 22.5 | 6.79 | 2 | 3.01 | 3.3
2018-12-03 12:00 | 11828.0605 | 1045.59 | 16.89 | 17.64 | 19.44 | 24.62 | 5 | 1 | 2.19 | 3.3
2018-12-03 13:00 | 11950.772 | 1038.76 | 15.36 | 15.36 | 19.38 | 24.36 | 5 | 1.75 | 3.01 | 3.1
2018-12-03 14:00 | 11361.7853 | 899.774 | 14.37 | 14.37 | 19.37 | 25.43 | 5 | 2 | 3.01 | 3.11
2018-12-03 15:00 | 10862.1898 | 646.884 | 13.95 | 13.95 | 19.81 | 22.56 | 5 | 1.27 | 2 | 2.82
2018-12-03 16:00 | 11394.9727 | 251.922 | 15.6 | 15.6 | 22.01 | 22.39 | 5 | 1 | 2 | 3
2018-12-03 17:00 | 11247.2674 | 2.917 | 17.02 | 17.84 | 30.38 | 27.86 | 5.21 | 1 | 2 | 3
2018-12-03 18:00 | 11223.0391 | -0.048233 | 18.44 | 18.44 | 23.21 | 27.69 | 31.35 | 21.5 | 2.11 | 22.9
2018-12-03 19:00 | 11032.0841 | -0.048233 | 17.61 | 17.95 | 22.43 | 22.96 | 23.27 | 13.91 | 3.25 | 13.91
2018-12-03 20:00 | 9898.0042 | -0.048233 | 16.04 | 16.04 | 21.9 | 20.92 | 14 | 10 | 3.25 | 3.1
2018-12-03 21:00 | 10921.3091 | -0.048233 | 13.9 | 13.9 | 21.04 | 19.42 | 6.22 | 0.99 | 3.11 | 3.1
2018-12-03 22:00 | 10789.4341 | -0.048233 | 11.67 | 11.67 | 18.34 | 13.96 | 4.49 | 0.99 | 3.5 | 1.56
2018-12-03 23:00 | 10749.3441 | -0.048233 | 320.1557 | 5.98 | 16.54 | 10.34 | 15 | 0.71 | 14.54 | 3
2018-12-04 | 9841.0042 | -0.048233 | -0.04 | -0.04 | 16.03 | 9.9 | 15 | 0.71 | 15.21 | 2.61
2018-12-04 01:00 | 11002.5441 | -0.048233 | -0.52 | -0.52 | 12.75 | 8.03 | 19.25 | 0.61 | 11.26 | 1
2018-12-04 02:00 | 9713.7042 | -0.048233 | -0.51 | -0.51 | 8.21 | 7.07 | 19.25 | 0.61 | 3.12 | 1
2018-12-04 03:00 | 10449.7241 | -0.048233 | 0.04 | 0.04 | 9.67 | 8.86 | 19.25 | 0.97 | 10.03 | 1
2018-12-04 04:00 | 10342.1141 | -0.048233 | 2.85 | 2.85 | 11.07 | 10.59 | 18 | 0.97 | 2.61 | 1
2018-12-04 05:00 | 10420.1841 | -0.048233 | 7.74 | 7.74 | 17.12 | 11.99 | 18 | 0.97 | 9.07 | 1
2018-12-04 06:00 | 9482.8542 | -0.048233 | 15.96 | 15.96 | 21.12 | 22.05 | 21 | 0.97 | 38 | 20.25
2018-12-04 07:00 | 10654.3941 | -0.048233 | 15.13 | 15.13 | 21.67 | 21.77 | 39.53 | 58.3073 | 9.11 | 39.53
2018-12-04 08:00 | 9649.9841 | 120.878 | 16.6 | 16.6 | 20.61 | 22.42 | 14.71 | 14.5 | 3.18 | 14.65
2018-12-04 09:00 | 9669.0506 | 170.948 | 17.87 | 17.87 | 20.22 | 24.23 | 6.01 | 6.66 | 2.11 | 2.75
2018-12-04 10:00 | 10994.1898 | 122.033 | 18.22 | 28.03 | 20.07 | 26.89 | 7 | 5.1 | 2.31 | 5
2018-12-04 11:00 | 11562.187 | 752.419 | 16.99 | 18.27 | 20.05 | 26.43 | 5.73 | 0.99 | 3.25 | 2.75
2018-12-04 12:00 | 10992.007 | 165.964 | 16.42 | 18.78 | 19.17 | 28 | 5 | 0.99 | 3.15 | 2.29
2018-12-04 13:00 | 10052.8107 | 461.906 | 15.61 | 27.56 | 18.28 | 30.76 | 5 | 0.99 | 2.28 | 3
2018-12-04 14:00 | 10767.315 | 92.9858 | 15.53 | 26.02 | 18.26 | 31.03 | 5.17 | 1.55 | 1 | 2.75
2018-12-04 15:00 | 9766.1686 | 96.1775 | 14.87 | 25.57 | 18.24 | 29.92 | 5.01 | 1.25 | 1 | 1.7
2018-12-04 16:00 | 10753.363 | 70.7611 | 14.79 | 25.38 | 33.95 | 30.64 | 5.2 | 1.31 | 1.01 | 1.31
2018-12-04 17:00 | 9689.9682 | 1.9665 | 15.76 | 22.49 | 39.33 | 41.07 | 7.65 | 1 | 0.91 | 2.65
2018-12-04 18:00 | 9748.8542 | -0.048233 | 17.23 | 23.56 | 38.62 | 28.18 | 33.65 | 15 | 2 | 17.92
2018-12-04 19:00 | 10785.2141 | -0.048233 | 16.35 | 21.09 | 36.98 | 27.31 | 24.26 | 9.79 | 2.42 | 4
2018-12-04 20:00 | 10650.1741 | -0.048233 | 15.48 | 19.68 | 31.82 | 27.77 | 7.11 | 1 | 3.11 | 3.3
2018-12-04 21:00 | 9594.0042 | -0.048233 | 12.88 | 17.78 | 20.04 | 25.5 | 6.08 | 1 | 2.11 | 3.1
2018-12-04 22:00 | 10640.6791 | -0.048233 | 11.39 | 24.71 | 19.28 | 21.23 | 5.6 | 1 | 3.5 | 2.58
2018-12-04 23:00 | 9488.5542 | -0.048233 | 10.41 | 13.77 | 16.29 | 14.85 | 7 | 0.62 | 12 | 1.61
2018-12-05 | 10420.1841 | -0.048233 | 9.62 | 9.73 | 15.71 | 12.71 | 35 | 0.62 | 9.72 | 2.7
2018-12-05 01:00 | 10356.8841 | -0.048233 | 9.33 | 10.43 | 14.98 | 10.44 | 3.71 | 0.49 | 11.03 | 1
2018-12-05 02:00 | 9266.2542 | -0.048233 | 6.91 | 6.91 | 13 | 9.66 | 3.21 | 0.49 | 3.5 | 1
2018-12-05 03:00 | 9260.5542 | -0.048233 | 7.8 | 7.8 | 12.99 | 9.58 | 3.21 | 0.97 | 10.42 | 1
2018-12-05 04:00 | 9597.8042 | -0.048233 | 9.44 | 9.44 | 13.89 | 10.82 | 3.21 | 0.97 | 3.24 | 1
2018-12-05 05:00 | 10799.5542 | -0.048233 | 13.49 | 14.15 | 15.7 | 14.89 | 3.65 | 0.97 | 9.72 | 1
2018-12-05 06:00 | 14037.7791 | -0.048233 | 19.79 | 21.06 | 15.69 | 24.98 | 19 | 0.97 | 38 | 22.25
2018-12-05 07:00 | 14929.2541 | -0.048233 | 18.05 | 28.79 | 33.02 | 25.59 | 25 | 15 | 3.25 | 25
2018-12-05 08:00 | 15698.0687 | 340.686 | 18.35 | 21.54 | 33.91 | 28.49 | 8.11 | 6 | 3.25 | 5.64
2018-12-05 09:00 | 17356.3768 | 752.542 | 18.57 | 19.96 | 33.69 | 28.23 | 6.82 | 6.97 | 2 | 5.1
2018-12-05 10:00 | 15198.0506 | 956.948 | 17.69 | 21.19 | 33.56 | 32.97 | 7.07 | 5.28 | 2 | 5.6
2018-12-05 11:00 | 15941.2293 | 1035.17 | 16.56 | 20.67 | 32.27 | 30.69 | 5.26 | 1.12 | 3.01 | 3.1
2018-12-05 12:00 | 16907.5249 | 1099.09 | 347.9457 | 303.62 | 17.18 | 31.07 | 6.24 | 1.33 | 3.01 | 3.1
2018-12-05 13:00 | 15580.0596 | 949.829 | 16.18 | 22.13 | 16 | 29.43 | 3.57 | 2 | 3.25 | 2.75
2018-12-05 14:00 | 14340.749 | 908.127 | 15.17 | 21.54 | 15.98 | 28.4 | 3 | 2 | 2.11 | 2.75
2018-12-05 15:00 | 13492.7305 | 631.318 | 15.6 | 20.79 | 16.04 | 26.65 | 3 | 1.25 | 2 | 2.01
2018-12-05 16:00 | 11409.2891 | 269.778 | 16.75 | 21.11 | 36.18 | 26.96 | 3 | 1.33 | 1 | 2.01
2018-12-05 17:00 | 12284.3691 | -0.048233 | 19.21 | 22.21 | 44.95 | 38.2 | 3.29 | 1.22 | 1 | 2.46
2018-12-05 18:00 | 12182.0341 | -0.048233 | 56.61 | 56.61 | 42.55 | 34.69 | 26.9 | 2 | 2.11 | 20.71
2018-12-05 19:00 | 10992.4042 | -0.048233 | 17.82 | 30.23 | 38.02 | 33.51 | 16.25 | 1 | 2.11 | 4.23
2018-12-05 20:00 | 12068.0941 | -0.048233 | 17.12 | 24.21 | 33.8 | 29.97 | 7.83 | 1 | 2 | 3.11
2018-12-05 21:00 | 11814.8941 | -0.048233 | 43.15 | 43.15 | 19.14 | 28.03 | 5.13 | 1 | 2.06 | 2.61
2018-12-05 22:00 | 11418.2141 | -0.048233 | 15.54 | 21.91 | 17.39 | 23.87 | 5.87 | 1 | 3.25 | 1.77
2018-12-05 23:00 | 9987.3042 | -0.048233 | 10.1 | 20.01 | 15.98 | 21.43 | 6.01 | 0.5 | 3.5 | 3
2018-12-06 | 10942.4091 | -0.048233 | 14.02 | 19.51 | 15.37 | 21.52 | 26.24 | 0.5 | 9 | 3
2018-12-06 01:00 | 9927.4542 | -0.048233 | 13.34 | 18.44 | 13.43 | 19.89 | 3.25 | 0.5 | 3.11 | 2.11
2018-12-06 02:00 | 11003.5991 | -0.048233 | 12.17 | 18.91 | 4.85 | 19.7 | 2.7 | 0.5 | 1.32 | 0.44
2018-12-06 03:00 | 10917.0891 | -0.048233 | 5.64 | 19.41 | 8.27 | 19.92 | 3 | 0.97 | 13.79 | 0.5
2018-12-06 04:00 | 11160.7941 | -0.048233 | 10.36 | 18.77 | 8.24 | 20.09 | 3 | 0.97 | 1 | 0.5
2018-12-06 05:00 | 10983.8542 | -0.048233 | 14.33 | 20.23 | 13.67 | 21.55 | 3 | 0.97 | 9.87 | 1
2018-12-06 06:00 | 12904.7542 | -0.048233 | 14.17 | 19.3 | 15.43 | 33.58 | 6 | 0.97 | 117.7434 | 5
2018-12-06 07:00 | 13937.4042 | -0.048233 | 18.56 | 22.26 | 14.34 | 30.95 | 30.01 | 10.14 | 2 | 30.01
2018-12-06 08:00 | 14161.4172 | 127.755 | 17.12 | 21.16 | 15.95 | 32.51 | 4.13 | 8.1 | 2 | 2.75
2018-12-06 09:00 | 16302.8675 | 307.955 | 19.83 | 20.86 | 16 | 32.77 | 4.61 | 8.1 | 0.69 | 2.75
2018-12-06 10:00 | 14580.9772 | 380.397 | 19.86 | 22.5 | 16.66 | 33.03 | 3.1 | 8.1 | 1.04 | 2
2018-12-06 11:00 | 14241.8157 | 537.385 | 19.71 | 19.71 | 16.74 | 32.06 | 2.75 | 1.57 | 1.34 | 2
2018-12-06 12:00 | 16565.6575 | 343.045 | 19.83 | 19.83 | 16.71 | 31.89 | 3 | 1.32 | 1.02 | 2
2018-12-06 13:00 | 13743.7725 | 289.129 | 19.61 | 19.61 | 16.06 | 32.68 | 3 | 1 | 1.08 | 2
2018-12-06 14:00 | 14572.4112 | 201.712 | 19.38 | 19.38 | 15.97 | 32.26 | 2.75 | 1 | 1 | 2
2018-12-06 15:00 | 12781.4567 | 198.165 | 19.85 | 19.85 | 16.19 | 33.42 | 2.75 | 1.14 | 2.05 | 1.14
2018-12-06 16:00 | 13989.6552 | 52.3367 | 18.59 | 19.92 | 31.21 | 34.14 | 2.75 | 1.24 | 0.56 | 1.24
2018-12-06 17:00 | 13816.2291 | -0.048233 | 20.91 | 20.91 | 41.23 | 47.19 | 2.75 | 1.2 | 0.86 | 1.86
2018-12-06 18:00 | 12258.7542 | -0.048233 | 34.08 | 24.66 | 35.5 | 46.17 | 27.76 | 14.61 | 2.2 | 21.62
2018-12-06 19:00 | 13385.7891 | -0.048233 | 37.03 | 37.03 | 31.38 | 45.24 | 16.99 | 12.14 | 2 | 12.94
2018-12-06 20:00 | 11432.2542 | -0.048233 | 43.78 | 35.14 | 18.21 | 39.63 | 5.16 | 1.62 | 2.01 | 2.75
2018-12-06 21:00 | 12263.2691 | -0.048233 | 49.96 | 49.96 | 18.05 | 33.62 | 4.71 | 1.17 | 2 | 2.75
2018-12-06 22:00 | 11716.7791 | -0.048233 | 54.13 | 54.13 | 16.64 | 25.78 | 2.75 | 1 | 2.11 | 2
2018-12-06 23:00 | 10157.3542 | -0.048233 | 17.31 | 19.55 | 15.52 | 24.98 | 5.88 | 0.5 | 22 | 1
2018-12-07 | 10035.7542 | -0.048233 | 16.46 | 18.64 | 15.93 | 21 | 7 | 0.58 | 22 | 1
2018-12-07 01:00 | 11202.9941 | -0.048233 | 16.48 | 18.45 | 15.63 | 20.79 | 2.26 | 0.5 | 3.5 | 1
2018-12-07 02:00 | 11157.6291 | -0.048233 | 15.53 | 18.31 | 15.16 | 21.17 | 2 | 0.5 | 2.11 | 0.5
2018-12-07 03:00 | 10118.4042 | -0.048233 | 15.22 | 17.95 | 15 | 21.06 | 2 | 0.97 | 3.01 | 0.5
2018-12-07 04:00 | 10380.6042 | -0.048233 | 15.82 | 17.63 | 16.01 | 22.91 | 2 | 0.97 | 1.65 | 0.75
2018-12-07 05:00 | 11156.7542 | -0.048233 | 685.5811 | 17.17 | 17.86 | 24.25 | 2 | 0.97 | 3.34 | 1
2018-12-07 06:00 | 12985.5042 | -0.048233 | 17.61 | 17.61 | 20.54 | 48.61 | 3 | 0.97 | 18 | 5
2018-12-07 07:00 | 15741.6041 | -0.048233 | 40.97 | 19.11 | 31.36 | 42.76 | 80.0841 | 30 | 2.11 | 79.3862
2018-12-07 08:00 | 15600.9613 | 114.641 | 17.81 | 17.81 | 19.63 | 37.6 | 15.5 | 13.88 | 2.61 | 15.3
2018-12-07 09:00 | 14624.7342 | 294.457 | 79.33 | 17.87 | 18.32 | 31.74 | 8.25 | 6.38 | 1 | 2.96
2018-12-07 10:00 | 14746.0662 | 412.175 | 44.55 | 44.55 | 19.43 | 30.56 | 6.89 | 4.83 | 0.66 | 3.51
2018-12-07 11:00 | 14251.9323 | 230.034 | 18.4 | 18.4 | 19.17 | 27.28 | 6.25 | 0.99 | 1 | 3.3
2018-12-07 12:00 | 15801.4334 | 255.662 | 18.62 | 18.62 | 18.58 | 27.71 | 4.94 | 1.52 | 1.01 | 1.61
2018-12-07 13:00 | 14046.7123 | 329.013 | 18.43 | 18.43 | 18.23 | 28.1 | 4.34 | 0.99 | 1.06 | 2.61
2018-12-07 14:00 | 14380.5689 | 281.871 | 18.78 | 18.78 | 18.2 | 28.54 | 3.86 | 0.99 | 1 | 2.11
2018-12-07 15:00 | 12100.3591 | 85.2201 | 19.06 | 19.21 | 17.42 | 28.77 | 3 | 0.99 | 1 | 1
2018-12-07 16:00 | 11777.0132 | 48.856 | 18.86 | 19.42 | 23.59 | 28 | 2.75 | 0.99 | 0.55 | 1
2018-12-07 17:00 | 12855.1241 | -0.048233 | 20.28 | 20.34 | 35.05 | 41.4 | 2.93 | 0.99 | 1 | 1
2018-12-07 18:00 | 12726.4141 | -0.048233 | 118.67 | 118.67 | 32.37 | 48.31 | 22.68 | 13.06 | 2 | 14.2
2018-12-07 19:00 | 11400.9042 | -0.048233 | 279.6457 | 235.32 | 22.75 | 47.53 | 20.94 | 1.68 | 2.11 | 4.32
2018-12-07 20:00 | 11053.2042 | -0.048233 | 134.68 | 134.68 | 22.01 | 41.16 | 16.48 | 1.62 | 1.2 | 2
2018-12-07 21:00 | 12081.8091 | -0.048233 | 689.3211 | 421.71 | 19.57 | 34.44 | 5.7 | 1.21 | 2 | 1
2018-12-07 22:00 | 11638.7091 | -0.048233 | 140.47 | 140.47 | 18.3 | 28.07 | 2.31 | 0.99 | 2 | 2.11
2018-12-07 23:00 | 10194.4042 | -0.048233 | 100.59 | 100.59 | 16.76 | 29.57 | 5 | 0.5 | 10.94 | 3.05
2018-12-08 | 11226.2041 | -0.048233 | 4.4 | 20.84 | 16.63 | 25.92 | 25 | 0.5 | 17.49 | 3.05
2018-12-08 01:00 | 9931.2542 | -0.048233 | -0.5 | 20.63 | 16.49 | 25.03 | 2.38 | 0.5 | 2.61 | 2.11
2018-12-08 02:00 | 9802.0542 | -0.048233 | -0.63 | 20.24 | 16.06 | 26.06 | 1.71 | 0.5 | 1 | 1.44
2018-12-08 03:00 | 10867.5041 | -0.048233 | 0.34 | 21.13 | 16.08 | 26.29 | 1.75 | 0.97 | 1.41 | 1.33
2018-12-08 04:00 | 11029.9741 | -0.048233 | 2.84 | 21.78 | 17.01 | 35.98 | 2 | 0.97 | 1 | 1.61
2018-12-08 05:00 | 10849.9042 | -0.048233 | 277.8057 | 233.48 | 19.77 | 40.93 | 2.17 | 0.97 | 1.97 | 2.25
2018-12-08 06:00 | 14041.9991 | -0.048233 | 322.4057 | 278.08 | 22.74 | 99.02 | 5.31 | 0.99 | 20 | 14.9
2018-12-08 07:00 | 15126.5391 | -0.048233 | 18.96 | 29.61 | 22.39 | 95.39 | 45.68 | 28.16 | 2.26 | 45.68
2018-12-08 08:00 | 13607.151 | 41.3168 | 12.91 | 12.91 | 23.22 | 62.23 | 28.55 | 14.27 | 1.97 | 15
2018-12-08 09:00 | 16085.4489 | 109.871 | 419.0157 | 374.69 | 22.16 | 42.97 | 10 | 7 | 1 | 4.85
2018-12-08 10:00 | 15565.3291 | 109.557 | 52.49 | 52.49 | 22.27 | 34.91 | 7.58 | 9.4 | 1.8 | 5.82
2018-12-08 11:00 | 15284.1722 | 174.367 | 48.17 | 48.17 | 22.18 | 33.62 | 6.01 | 0.99 | 1.2 | 3.1
2018-12-08 12:00 | 14041.8407 | 142.885 | 18.09 | 27.05 | 20.59 | 33.04 | 3.89 | 1 | 1 | 2.66
2018-12-08 13:00 | 14972.1317 | 147.594 | 18.57 | 24.36 | 20.57 | 31.49 | 3.32 | 1 | 2 | 2.75
2018-12-08 14:00 | 13928.0689 | 102.961 | 20.98 | 20.98 | 20.54 | 30.55 | 3.58 | 0.99 | 1.78 | 3.1
2018-12-08 15:00 | 11840.4207 | 68.6007 | 19.2 | 19.2 | 22.15 | 30.24 | 2.75 | 0.99 | 2 | 2.21
2018-12-08 16:00 | 11339.5511 | 44.3696 | 19.85 | 19.85 | 34.85 | 30.59 | 2.86 | 0.99 | 1 | 1.29
2018-12-08 17:00 | 11219.4542 | -0.048233 | 20.19 | 20.19 | 40.68 | 36 | 5.06 | 0.99 | 0.35 | 3.06
2018-12-08 18:00 | 12372.9891 | -0.048233 | 50.65 | 27.45 | 38.11 | 38.54 | 41.09 | 21.5 | 2.01 | 37.09
2018-12-08 19:00 | 12345.5591 | -0.048233 | 31.48 | 29.27 | 34.73 | 32.59 | 42.3 | 9.86 | 2.24 | 30.91
2018-12-08 20:00 | 12060.7091 | -0.048233 | 40.83 | 24.65 | 32.8 | 33.35 | 21.95 | 7.8 | 1 | 4.18
2018-12-08 21:00 | 10681.7542 | -0.048233 | 19.61 | 22.52 | 22.27 | 27.35 | 23.28 | 0.97 | 1.15 | 4.36
2018-12-08 22:00 | 11619.7191 | -0.048233 | 21.05 | 21.05 | 22.2 | 23.78 | 5.48 | 0.97 | 1.54 | 3.32
2018-12-08 23:00 | 10206.7542 | -0.048233 | 17.07 | 20.62 | 18.65 | 23.99 | 3.89 | 0.75 | 9 | 3.37
2018-12-09 | 11160.7941 | -0.048233 | 16.93 | 18.54 | 31.29 | 23.44 | 5 | 0.75 | 9 | 2.77
2018-12-09 01:00 | 11177.6741 | -0.048233 | 16.71 | 18.28 | 17.35 | 21.67 | 2 | 0.75 | 2.99 | 1
2018-12-09 02:00 | 10046.2042 | -0.048233 | 16.7 | 17.93 | 16.76 | 21.7 | 2.03 | 0.75 | 1.18 | 1
2018-12-09 03:00 | 10183.0042 | -0.048233 | 16.84 | 18.08 | 16.89 | 22.73 | 1.97 | 1 | 2.11 | 1
2018-12-09 04:00 | 10408.1542 | -0.048233 | 18.08 | 18.13 | 18.67 | 22.55 | 2 | 1 | 1 | 1
2018-12-09 05:00 | 11470.2542 | -0.048233 | 17.79 | 18.17 | 31.47 | 27.58 | 2.11 | 1 | 2.61 | 2
2018-12-09 06:00 | 13482.3542 | -0.048233 | 18.66 | 18.66 | 33.27 | 41.93 | 3.2 | 0.99 | 16.66 | 6
2018-12-09 07:00 | 14364.9042 | -0.048233 | 18.5 | 18.5 | 42.09 | 45.91 | 106.2541 | 87.0973 | 1.84 | 101.3062
2018-12-09 08:00 | 16652.4396 | 40.3029 | 18.66 | 18.66 | 34.21 | 46.29 | 86.5441 | 70.4673 | 1 | 80.0062
2018-12-09 09:00 | 15925.7306 | 305.927 | 19.31 | 19.31 | 37.05 | 31.21 | 15.98 | 7 | 1 | 11.73
2018-12-09 10:00 | 17677.9366 | 325.338 | 19.62 | 19.62 | 41.19 | 25.58 | 7.25 | 7.48 | 1.51 | 5
2018-12-09 11:00 | 15404.1447 | 305.085 | 18.4 | 18.4 | 38.39 | 22.1 | 4.51 | 0.99 | 1 | 3.1
2018-12-09 12:00 | 14007.4983 | 310.735 | 16.97 | 16.97 | 34.74 | 21.42 | 3.78 | 1.35 | 1 | 2.5
2018-12-09 13:00 | 13406.3126 | 424.908 | 15.8 | 15.8 | 34.24 | 20.01 | 4 | 0.99 | 1 | 2.5
2018-12-09 14:00 | 12328.074 | 228.92 | 15.05 | 15.05 | 33.31 | 19.24 | 3 | 1.17 | 1 | 2.5
2018-12-09 15:00 | 11966.7795 | 527.61 | 15.46 | 15.46 | 37.55 | 19.08 | 2.75 | 1 | 2 | 2.07
2018-12-09 16:00 | 11205.7031 | 115.477 | 16.05 | 16.05 | 47.01 | 20.72 | 3 | 0.99 | 0.5 | 1.9
2018-12-09 17:00 | 12217.3687 | 3.4442 | 18.09 | 18.09 | 54.45 | 30.2 | 3.34 | 0.99 | 0.27 | 2.11
2018-12-09 18:00 | 10926.8542 | -0.048233 | 19.05 | 19.72 | 50.61 | 31.48 | 20.68 | 17.5 | 1.63 | 18.9
2018-12-09 19:00 | 10779.6042 | -0.048233 | 58.3 | 19.69 | 44.62 | 32.92 | 15.82 | 1.46 | 1.57 | 5
2018-12-09 20:00 | 11667.1941 | -0.048233 | 15.88 | 21.63 | 41.62 | 31.94 | 8.11 | 1.39 | 1 | 3.1
2018-12-09 21:00 | 10538.3042 | -0.048233 | 14.61 | 28.17 | 41.51 | 27.89 | 4.81 | 1.01 | 1.8 | 2.75
2018-12-09 22:00 | 10208.6542 | -0.048233 | 13.28 | 22.91 | 37 | 24.27 | 5.64 | 1.01 | 2.32 | 3.52
2018-12-09 23:00 | 9998.7042 | -0.048233 | 5.53 | 21.18 | 34 | 23.55 | 4 | 0.75 | 10.82 | 3.24
2018-12-10 | 10845.3491 | -0.048233 | 4.06 | 31.46 | 11.74 | 22.33 | 5 | 0.75 | 13.99 | 4
2018-12-10 01:00 | 10813.6991 | -0.048233 | 4.12 | 25.07 | 8.23 | 20.81 | 5.27 | 0.74 | 3.11 | 5.07
2018-12-10 02:00 | 9675.7042 | -0.048233 | 2.28 | 23.06 | 4.68 | 21.01 | 4.25 | 0.74 | 0.45 | 2.11
2018-12-10 03:00 | 9632.9542 | -0.048233 | 7.01 | 26.29 | 4.77 | 21.54 | 4.25 | 0.97 | 1.28 | 2.11
2018-12-10 04:00 | 10845.3491 | -0.048233 | 10.92 | 21.75 | 7.34 | 21.84 | 4.25 | 0.97 | 0.52 | 2.11
2018-12-10 05:00 | 11036.3041 | -0.048233 | 18.95 | 26.2 | 32.9 | 24.42 | 4.3 | 0.97 | 20.01 | 3.99
2018-12-10 06:00 | 10522.1542 | -0.048233 | 16.98 | 26.88 | 35.3 | 31.05 | 7.25 | 0.99 | 40.41 | 30
2018-12-10 07:00 | 11870.8091 | -0.048233 | 55.06 | 55.06 | 35.58 | 31.47 | 48 | 26.03 | 3.11 | 48
2018-12-10 08:00 | 10630.7328 | 83.245 | 14.88 | 30.21 | 36.77 | 33.18 | 20 | 14.43 | 1 | 14.43
2018-12-10 09:00 | 11896.6516 | 132.447 | 15.81 | 36.89 | 43.01 | 33.03 | 18.46 | 13.78 | 0.36 | 11.24
2018-12-10 10:00 | 10498.5668 | 104.123 | 17.34 | 21.62 | 43.86 | 28.33 | 11.59 | 8.51 | 0.68 | 3.75
2018-12-10 11:00 | 11596.042 | 132.509 | 17.57 | 19.85 | 37.85 | 24.83 | 7.45 | 2 | 1 | 3.1
2018-12-10 12:00 | 10458.8008 | 128.264 | 17.91 | 18.7 | 33.5 | 21.94 | 5.47 | 8.95 | 1 | 2.75
2018-12-10 13:00 | 11463.4158 | 124.797 | 42.33 | 18.54 | 34.35 | 21.71 | 6.01 | 2 | 2 | 3.1
2018-12-10 14:00 | 10100.8617 | 137.486 | 18.03 | 18.03 | 32.97 | 20.56 | 4.77 | 2 | 1 | 2.75
2018-12-10 15:00 | 11378.5442 | 129.35 | 17.9 | 17.9 | 33.53 | 20.42 | 6.01 | 0.99 | 1.05 | 2.75
2018-12-10 16:00 | 11298.9811 | 71.9347 | 66.73 | 18.27 | 39.2 | 20.52 | 4.5 | 0.99 | 1 | 2.75
2018-12-10 17:00 | 10081.7417 | 3.3597 | 45.93 | 18.91 | 50.27 | 32.05 | 5.5 | 1.07 | 1 | 2.75
2018-12-10 18:00 | 11264.1841 | -0.048233 | 21.18 | 21.29 | 41.78 | 27.32 | 39.77 | 58.8773 | 1.17 | 39.57
2018-12-10 19:00 | 10172.5542 | -0.048233 | 95.97 | 40.36 | 40.18 | 28.46 | 19.17 | 16.17 | 1 | 2.75
2018-12-10 20:00 | 11123.8691 | -0.048233 | 20.68 | 21.2 | 36.75 | 26.82 | 9.25 | 1.24 | 1.96 | 2.75
2018-12-10 21:00 | 9958.8042 | -0.048233 | 45.86 | 20.41 | 36.81 | 23.54 | 7.47 | 1.2 | 2 | 2.75
2018-12-10 22:00 | 10847.4591 | -0.048233 | 20.23 | 21.25 | 35 | 22.37 | 18.28 | 1.44 | 9 | 2.8
2018-12-10 23:00 | 9548.4042 | -0.048233 | 18.47 | 19.72 | 32.27 | 21.58 | 105.8141 | 0.61 | 12.86 | 4
2018-12-11 | 9349.8542 | -0.048233 | 15.7 | 18.33 | 6.49 | 21.35 | 105.8141 | 0.61 | 25 | 22
2018-12-11 01:00 | 9315.6542 | -0.048233 | 13.03 | 18.03 | 6.31 | 20.81 | 4.79 | 0.5 | 10 | 4.37
2018-12-11 02:00 | 9361.2542 | -0.048233 | 11.42 | 17.48 | 5 | 20.46 | 2.45 | 0.5 | 2.11 | 2.2
2018-12-11 03:00 | 10380.0941 | -0.048233 | 12.49 | 17.08 | 4.98 | 20.13 | 4 | 0.7 | 10 | 2.2
2018-12-11 04:00 | 10265.0991 | -0.048233 | 10.52 | 17.42 | 5.28 | 22.09 | 3.16 | 0.7 | 10 | 2.11
2018-12-11 05:00 | 10311.5191 | -0.048233 | 7.9 | 21.2 | 30.9 | 29.05 | 4.5 | 0.7 | 17.65 | 3
2018-12-11 06:00 | 10304.1341 | -0.048233 | 258.3857 | 21.81 | 39.73 | 45.07 | 22.77 | 0.69 | 52.6962 | 43
2018-12-11 07:00 | 9228.2542 | -0.048233 | 16.74 | 29.12 | 39.73 | 44.54 | 115.8141 | 0.97 | 19.76 | 439.3306
2018-12-11 08:00 | 10387.6112 | 234.077 | 16.45 | 24.86 | 35.74 | 34.24 | 13.77 | 0.97 | 28.34 | 6.78
2018-12-11 09:00 | 10800.0234 | 627.989 | 18.75 | 20.87 | 34.14 | 29.95 | 105.8141 | 1.42 | 0.5 | 4.4
2018-12-11 10:00 | 10845.2607 | 826.868 | 49.23 | 21.5 | 33.26 | 25.49 | 90.8141 | 2.5 | 0.78 | 3.5
2018-12-11 11:00 | 9782.4606 | 759.327 | 65.69 | 20.58 | 33.11 | 24.1 | 90.8141 | 0.99 | 14 | 3.1
2018-12-11 12:00 | 10933.3733 | 719.387 | 18.57 | 18.83 | 32.93 | 23.46 | 90.8141 | 0.99 | 1 | 2.11
2018-12-11 13:00 | 10128.1809 | 888.243 | 17.94 | 18.65 | 32.18 | 22.75 | 7.11 | 0.99 | 15.79 | 3.1
2018-12-11 14:00 | 9731.001 | 420.159 | 59.57 | 18.61 | 32.83 | 22.41 | 105.8141 | 0.99 | 1 | 3.1
2018-12-11 15:00 | 10931.4542 | 268.568 | 18.61 | 18.61 | 34.61 | 21.81 | 105.8141 | 0.87 | 1.25 | 3
2018-12-11 16:00 | 10018.4919 | 252.781 | 18.62 | 18.62 | 43.16 | 22.33 | 4 | 0.74 | 0.53 | 3
2018-12-11 17:00 | 11076.7446 | 1.284 | 18.29 | 18.29 | 45.79 | 37.47 | 5.41 | 0.74 | 0.31 | 3
2018-12-11 18:00 | 11262.0741 | -0.048233 | 19.61 | 19.61 | 44.14 | 29.98 | 35 | 10.82 | 1.18 | 30
2018-12-11 19:00 | 11274.7341 | -0.048233 | 18.63 | 18.64 | 42.97 | 29 | 18.35 | 0.99 | 1.79 | 5
2018-12-11 20:00 | 10088.9542 | -0.048233 | 17.79 | 20.8 | 39.65 | 25.18 | 35 | 1 | 1.51 | 3.1
2018-12-11 21:00 | 9961.6542 | -0.048233 | 16.31 | 18.3 | 42.84 | 24.53 | 35.76 | 0.97 | 2.12 | 3.1
2018-12-11 22:00 | 10960.3441 | -0.048233 | 12.83 | 19.35 | 32.28 | 23.51 | 14.26 | 0.97 | 20 | 5.35
2018-12-11 23:00 | 11057.4041 | -0.048233 | 12.35 | 16.74 | 23.66 | 22.41 | 35.33 | 0.5 | 34.74 | 35.13
2018-12-12 | 9939.8042 | -0.048233 | 14.39 | 16.17 | 5.21 | 17.35 | 26.81 | 0.5 | 50.1362 | 26.61
2018-12-12 01:00 | 9689.9542 | -0.048233 | 10.64 | 10.64 | 4.97 | 13.58 | 83.2641 | 0.5 | 14 | 82.5662
2018-12-12 02:00 | 9687.1042 | -0.048233 | 4.21 | 4.21 | 2.97 | 13.71 | 33.2 | 0.5 | 3.5 | 33
2018-12-12 03:00 | 9671.9042 | -0.048233 | 3.84 | 15.21 | 2.56 | 17.93 | 83.2641 | 0.85 | 7.36 | 33
2018-12-12 04:00 | 9901.8042 | -0.048233 | 1.75 | 16.32 | 2.76 | 21.82 | 81.8141 | 0.85 | 0.88 | 2.51
2018-12-12 05:00 | 12223.1791 | -0.048233 | 4.15 | 16.56 | 33.03 | 23.75 | 28.94 | 0.85 | 60.0662 | 26
2018-12-12 06:00 | 12703.3542 | -0.048233 | 6.33 | 17.82 | 40.46 | 37.7 | 35.52 | 0.85 | 30.39 | 35.52
2018-12-12 07:00 | 13765.4542 | -0.048233 | 55.26 | 19.26 | 40.68 | 35.62 | 475.3478 | 12.55 | 1 | 479.3306
2018-12-12 08:00 | 14186.2187 | 82.8618 | 12.75 | 18.7 | 41.67 | 28.32 | 11.93 | 0.97 | 0.58 | 4.19
2018-12-12 09:00 | 16069.4657 | 179.721 | 51.12 | 19.22 | 41.64 | 26.59 | 9.03 | 0.97 | 0.44 | 5.7
2018-12-12 10:00 | 14434.4453 | 241.153 | 15.7 | 18.99 | 40.88 | 23.95 | 15 | 0.97 | 0.16 | 14.8
2018-12-12 11:00 | 14212.5092 | 196.536 | 15.9 | 19.5 | 40.49 | 21.71 | 7.11 | 0.99 | 1 | 4.5
2018-12-12 12:00 | 14229.2425 | 214.15 | 14.2 | 19.33 | 36.61 | 21.58 | 6.79 | 0.97 | 0.82 | 2.11
2018-12-12 13:00 | 16292.9009 | 137.508 | 15.31 | 18.99 | 34.85 | 21.38 | 7.11 | 0.97 | 9.11 | 3.42
2018-12-12 14:00 | 14625.8258 | 262.342 | 15.38 | 18.64 | 32.04 | 21.01 | 6.74 | 0.97 | 0.2 | 2.67
2018-12-12 15:00 | 14193.2231 | 274.292 | 16.26 | 18.06 | 32.95 | 20.59 | 4 | 0.97 | 0.52 | 2.54
2018-12-12 16:00 | 12535.953 | 127.74 | 16.07 | 18 | 39.39 | 21.67 | 4 | 0.97 | 0.05 | 2.4
2018-12-12 17:00 | 12361.6377 | 1.2502 | 16.08 | 19.14 | 46.27 | 29.94 | 6.45 | 0.97 | 0.16 | 3.2
2018-12-12 18:00 | 13606.2841 | -0.048233 | 16.87 | 19.93 | 40.97 | 29.18 | 40.75 | 0.97 | 2.95 | 26.23
2018-12-12 19:00 | 12143.8042 | -0.048233 | 16.93 | 19.61 | 36.05 | 29.22 | 34.64 | 1.36 | 1.82 | 14.18
2018-12-12 20:00 | 11730.5542 | -0.048233 | 15.35 | 19.58 | 34.11 | 25.45 | 10 | 0.97 | 1.22 | 3.48
2018-12-12 21:00 | 11411.3542 | -0.048233 | 15.11 | 20.66 | 33.11 | 24.19 | 45 | 0.97 | 0.54 | 3.1
2018-12-12 22:00 | 12182.0341 | -0.048233 | 15.23 | 19.01 | 31.64 | 22.46 | 38.73 | 0.97 | 11.03 | 3
2018-12-12 23:00 | 11829.6641 | -0.048233 | 18.44 | 20.84 | 7.15 | 22.55 | 50 | 0.5 | 14.42 | 4.04
2018-12-13 | 10524.0542 | -0.048233 | 17.46 | 20.16 | 4.61 | 19.94 | 50 | 0.5 | 22.83 | 35.89
2018-12-13 01:00 | 10468.0042 | -0.048233 | 16.17 | 19.89 | 3.26 | 18.51 | 5.18 | 0.5 | 13.01 | 2.21
2018-12-13 02:00 | 11598.6191 | -0.048233 | 16.04 | 19.93 | 3.6 | 17.8 | 4 | 0.5 | 15.23 | 1.01
2018-12-13 03:00 | 10351.1542 | -0.048233 | 13.39 | 20.38 | 2.38 | 19.46 | 4 | 0.85 | 11.03 | 1
2018-12-13 04:00 | 11638.7091 | -0.048233 | 12.21 | 20.03 | 2.55 | 21.75 | 4 | 0.85 | 2.11 | 1.61
2018-12-13 05:00 | 12768.6141 | -0.048233 | 0.13 | 21.33 | 3.22 | 25.13 | 3 | 0.85 | 22.23 | 20
2018-12-13 06:00 | 13349.3542 | -0.048233 | 5.52 | 31.1 | 32.14 | 47.44 | 29.03 | 0.85 | 51.6862 | 30.23
2018-12-13 07:00 | 14865.5542 | -0.048233 | 13.12 | 26.42 | 35 | 46.14 | 53.23 | 13.68 | 12 | 78.3462
2018-12-13 08:00 | 16061.2747 | 415.605 | 12.94 | 22.41 | 34.24 | 30.68 | 7.23 | 0.97 | 12 | 4.97
2018-12-13 09:00 | 16564.0252 | 703.816 | 14.32 | 28.25 | 32.47 | 28.25 | 18.23 | 0.97 | 0.43 | 6
2018-12-13 10:00 | 15200.7818 | 584.823 | 101.07 | 101.07 | 34.39 | 26.43 | 27.06 | 0.97 | 0.51 | 5.74
2018-12-13 11:00 | 16941.688 | 866.472 | 12.48 | 19.57 | 33.62 | 23.1 | 6.58 | 0.97 | 2.11 | 3.4
2018-12-13 12:00 | 17334.6839 | 1053.98 | 12.85 | 18.67 | 32.5 | 22.07 | 6.19 | 0.97 | 1.7 | 3
2018-12-13 13:00 | 15442.4904 | 854.253 | 12.69 | 20.22 | 32.48 | 20.61 | 5.48 | 0.97 | 1.87 | 3
2018-12-13 14:00 | 14261.4675 | 711.071 | 10.65 | 18.62 | 32.54 | 20.63 | 6.11 | 0.97 | 1 | 3
2018-12-13 15:00 | 14714.8277 | 204.704 | 8.95 | 19.17 | 33.55 | 20.4 | 6.25 | 0.97 | 1 | 2.82
2018-12-13 16:00 | 14220.1952 | 103.858 | 11.42 | 19.49 | 50.37 | 21.66 | 6.11 | 1.24 | 0.22 | 2.51
2018-12-13 17:00 | 12827.5034 | 2.6352 | 14.57 | 20.6 | 55.77 | 34.91 | 5.28 | 1.05 | 0.08 | 3.59
2018-12-13 18:00 | 13749.7641 | -0.048233 | 18.97 | 27.69 | 54.44 | 32.59 | 42.48 | 1.31 | 1 | 40.88
2018-12-13 19:00 | 12079.2042 | -0.048233 | 19.88 | 25.53 | 49.44 | 28.34 | 30.03 | 1.39 | 1 | 14.84
2018-12-13 20:00 | 13136.8091 | -0.048233 | 17.74 | 29.75 | 43.64 | 24.21 | 8.54 | 0.97 | 1 | 3.3
2018-12-13 21:00 | 12687.3791 | -0.048233 | 17.18 | 26.08 | 36.75 | 23.33 | 5.65 | 0.97 | 11 | 3.3
2018-12-13 22:00 | 11043.7042 | -0.048233 | 19.89 | 20.14 | 32.73 | 21.22 | 5.14 | 0.97 | 11 | 3
2018-12-13 23:00 | 10712.1542 | -0.048233 | 16.05 | 19.89 | 4.85 | 19.59 | 28.04 | 0.5 | 13.38 | 27.84
2018-12-14 | 11724.1641 | -0.048233 | 12.16 | 19.63 | 5.95 | 20.65 | 25.2 | 0.5 | 15.09 | 25
2018-12-14 01:00 | 11573.2991 | -0.048233 | 10.86 | 19.79 | 4.64 | 19.3 | 4.68 | 0.5 | 3.5 | 1
2018-12-14 02:00 | 10375.8542 | -0.048233 | 9.99 | 19.68 | 4.48 | 18.93 | 3.36 | 0.5 | 2.11 | 1
2018-12-14 03:00 | 11307.4391 | -0.048233 | 9.19 | 19.45 | 4.55 | 19.3 | 3.31 | 0.85 | 3.01 | 1
2018-12-14 04:00 | 10140.2542 | -0.048233 | 6.69 | 18.68 | 4.64 | 19.6 | 3.31 | 0.85 | 1.46 | 1
2018-12-14 05:00 | 12196.8041 | -0.048233 | 10.81 | 18.16 | 34.53 | 21.63 | 4 | 0.85 | 14.1 | 1
2018-12-14 06:00 | 14369.0491 | -0.048233 | 18.39 | 20.08 | 41.07 | 39.51 | 29 | 0.85 | 31.07 | 28.8
2018-12-14 07:00 | 15341.7591 | -0.048233 | 79.33 | 22.89 | 39.68 | 35.31 | 50 | 14.5 | 1.06 | 50
2018-12-14 08:00 | 13858.8982 | 58.3139 | 17.15 | 18.7 | 38.91 | 32.1 | 14.7 | 1.05 | 1 | 13.74
2018-12-14 09:00 | 15894.86 | 216.218 | 47.71 | 18.77 | 35.44 | 29.98 | 9.01 | 0.97 | 1 | 6.68
2018-12-14 10:00 | 14112.0638 | 286.804 | 17.78 | 18.65 | 34.74 | 27.35 | 7.02 | 0.97 | 1 | 5.92
2018-12-14 11:00 | 13814.0849 | 142.142 | 18.07 | 18.48 | 33.75 | 23.67 | 6.01 | 0.97 | 1.37 | 3.66
2018-12-14 12:00 | 15647.8961 | 170.129 | 18.13 | 18.56 | 33.17 | 24 | 5.11 | 0.99 | 1.76 | 3
2018-12-14 13:00 | 13476.2088 | 112.483 | 17.62 | 17.89 | 33.26 | 23.62 | 6.25 | 1 | 2.11 | 3
2018-12-14 14:00 | 12741.551 | 348.159 | 17.25 | 17.28 | 33.34 | 23.81 | 4.61 | 1 | 1.65 | 3
2018-12-14 15:00 | 13773.697 | 407.637 | 17.2 | 17.21 | 33.55 | 22.28 | 4.61 | 1 | 2.18 | 3
2018-12-14 16:00 | 13258.6123 | 258.405 | 16.48 | 17.3 | 51.56 | 23.05 | 4.61 | 0.99 | 0.77 | 2.51
2018-12-14 17:00 | 11537.7042 | -0.048233 | 16.45 | 17.82 | 52.34 | 32.88 | 5.09 | 0.99 | 0.33 | 3
2018-12-14 18:00 | 12675.7741 | -0.048233 | 15.91 | 19.48 | 52.36 | 32.1 | 35.4 | 0.99 | 1.23 | 32.4
2018-12-14 19:00 | 11351.5042 | -0.048233 | 14.05 | 18.7 | 50.18 | 31.47 | 20.8 | 1 | 2 | 4.59
2018-12-14 20:00 | 12433.1241 | -0.048233 | 13.76 | 18.7 | 47.97 | 27.07 | 8.11 | 0.99 | 1.94 | 3.66
2018-12-14 21:00 | 12203.1341 | -0.048233 | 12.54 | 18.56 | 37.04 | 24.91 | 6.01 | 0.99 | 1 | 3.14
2018-12-14 22:00 | 10545.9042 | -0.048233 | 10.5 | 18.47 | 34.76 | 21.44 | 4.75 | 0.97 | 12.71 | 2.85
2018-12-14 23:00 | 10199.1542 | -0.048233 | 4.56 | 18.3 | 38.04 | 19.92 | 4 | 0.5 | 14.68 | 2.99
2018-12-15 | 11234.6441 | -0.048233 | -0.67 | 17.87 | 38.26 | 18.12 | 4 | 0.5 | 14.74 | 2.82
2018-12-15 01:00 | 11175.5641 | -0.048233 | -0.65 | 17.34 | 37.44 | 17.39 | 3.25 | 0.43 | 3.44 | 1
2018-12-15 02:00 | 9974.0042 | -0.048233 | -0.7 | 15.6 | 37.55 | 16.28 | 3 | 0.43 | 2.06 | 1
2018-12-15 03:00 | 11035.2491 | -0.048233 | -0.65 | 8.59 | 37.55 | 16.19 | 2.71 | 0.61 | 2.61 | 1
2018-12-15 04:00 | 11141.8041 | -0.048233 | 0 | 5.86 | 38.02 | 16.52 | 2.81 | 0.61 | 1 | 1
2018-12-15 05:00 | 11883.4691 | -0.048233 | 6.45 | 12.67 | 40.57 | 19.06 | 3.03 | 0.74 | 33.76 | 1
2018-12-15 06:00 | 13327.7641 | -0.048233 | 13.07 | 17.77 | 50.24 | 28.24 | 20 | 0.74 | 35.87 | 20
2018-12-15 07:00 | 12774.6042 | -0.048233 | 16.54 | 19.45 | 50.98 | 28.69 | 30.34 | 2.39 | 1.2 | 22.35
2018-12-15 08:00 | 13348.1565 | 427.691 | 16.21 | 20.06 | 48.7 | 33.5 | 20.27 | 2.85 | 1 | 4.15
2018-12-15 09:00 | 14056.1648 | 781.963 | 18.19 | 22.19 | 52.12 | 29.87 | 14.02 | 2.99 | 0.66 | 4.59
2018-12-15 10:00 | 13831.3454 | 993.311 | 17.23 | 20.84 | 47.16 | 27.62 | 6.7 | 2.99 | 0.86 | 4.7
2018-12-15 11:00 | 15144.8626 | 1148.32 | 16.81 | 19.7 | 45 | 25.63 | 5.2 | 0.99 | 1 | 2.82
2018-12-15 12:00 | 15102.4621 | 1083.13 | 16.56 | 18.99 | 42.13 | 24.76 | 6.25 | 0.99 | 1.64 | 1.93
2018-12-15 13:00 | 15077.5431 | 1102.51 | 51.16 | 26.78 | 42.04 | 23.49 | 4 | 0.99 | 2.13 | 3
2018-12-15 14:00 | 13512.9211 | 943.456 | 48.23 | 37.8 | 41.99 | 23.11 | 4 | 0.99 | 1.88 | 1.54
2018-12-15 15:00 | 11109.4045 | 668.11 | 69.7 | 69.7 | 43.36 | 23.18 | 4 | 0.97 | 2.06 | 1.11
2018-12-15 16:00 | 10685.0034 | 283.372 | 193.58 | 193.58 | 58.79 | 24.86 | 4 | 0.97 | 0.39 | 1.11
2018-12-15 17:00 | 10585.7262 | 2.8697 | 79.51 | 79.51 | 61.55 | 37.33 | 4.86 | 0.97 | 0.48 | 1.61
2018-12-15 18:00 | 11891.9091 | -0.048233 | 19.8 | 23.93 | 59.7 | 33.08 | 26.18 | 0.74 | 1.59 | 23.45
2018-12-15 19:00 | 11672.4691 | -0.048233 | 18.39 | 21.33 | 56.51 | 30.47 | 28.44 | 0.97 | 2 | 5
2018-12-15 20:00 | 11501.5591 | -0.048233 | 16.52 | 18.69 | 57.43 | 28.08 | 31.27 | 0.97 | 2 | 2.86
2018-12-15 21:00 | 11312.7141 | -0.048233 | 16.02 | 18.67 | 52.6 | 26.5 | 25.93 | 0.97 | 2 | 3.1
2018-12-15 22:00 | 10079.4542 | -0.048233 | 17.24 | 18.74 | 47.54 | 22.61 | 25 | 0.97 | 11 | 3
2018-12-15 23:00 | 9944.5542 | -0.048233 | 14.39 | 18.41 | 40.24 | 21.12 | 5 | 0.43 | 11 | 4.18
2018-12-16 | 9887.5542 | -0.048233 | 12.05 | 20.82 | 54.07 | 20.85 | 40.01 | 0.43 | 12.54 | 3
2018-12-16 01:00 | 9925.5542 | -0.048233 | 11.38 | 18.96 | 51.52 | 18.96 | 830.3478 | 0.42 | 12.82 | 3.31
2018-12-16 02:00 | 9897.0542 | -0.048233 | 10.34 | 18.44 | 49.85 | 17.71 | 830.3478 | 0.42 | 2.11 | 1.11
2018-12-16 03:00 | 9934.1042 | -0.048233 | 10.52 | 18.55 | 48.87 | 18.55 | 830.3478 | 0.5 | 12.53 | 1.11
2018-12-16 04:00 | 11367.5741 | -0.048233 | 11.07 | 19.49 | 50.3 | 19.6 | 35 | 0.5 | 1 | 2.11
2018-12-16 05:00 | 10938.2542 | -0.048233 | 10.25 | 19.23 | 55.99 | 21.57 | 4.28 | 0.5 | 10 | 3.09
2018-12-16 06:00 | 12382.2542 | -0.048233 | 15.28 | 19.08 | 61.61 | 33.23 | 44 | 0.5 | 52.6962 | 45
2018-12-16 07:00 | 14799.4891 | -0.048233 | 16.05 | 18.75 | 70.45 | 26.5 | 45 | 2 | 19.97 | 45
2018-12-16 08:00 | 13679.4455 | 50.4163 | 15.34 | 19.37 | 58.55 | 27.66 | 35 | 2 | 1 | 4.15
2018-12-16 09:00 | 14050.4322 | 76.9286 | 15.87 | 19.77 | 55.99 | 25.07 | 35 | 2 | 0.25 | 4
2018-12-16 10:00 | 14016.1774 | 102.871 | 16.05 | 19.63 | 49.27 | 24.33 | 35 | 2 | 0.3 | 3.3
2018-12-16 11:00 | 13863.4896 | 123.147 | 16.26 | 18.51 | 45.31 | 24.57 | 24.21 | 0.97 | 1.56 | 3.3
2018-12-16 12:00 | 15738.7158 | 126.214 | 16.28 | 18.51 | 41.87 | 23.71 | 25.01 | 0.97 | 1.89 | 3.3
2018-12-16 13:00 | 13564.841 | 115.78 | 17.33 | 18.37 | 41.26 | 22.54 | 47.28 | 0.97 | 2.11 | 3.2
2018-12-16 14:00 | 14251.2669 | 98.3099 | 17.05 | 20.1 | 41.22 | 22.65 | 5.31 | 0.97 | 1.57 | 3.3
2018-12-16 15:00 | 13890.1573 | 66.0259 | 16.66 | 17.99 | 42.2 | 21.68 | 23.91 | 0.5 | 2.11 | 3.11
2018-12-16 16:00 | 12228.7885 | 32.4089 | 17.08 | 19.33 | 55.88 | 23.22 | 5.79 | 0.5 | 0.01 | 3.1
2018-12-16 17:00 | 13367.8541 | -0.048233 | 17.22 | 21.77 | 59.03 | 31.68 | 6.25 | 0.5 | 0.01 | 3.2
2018-12-16 18:00 | 13208.5491 | -0.048233 | 19.94 | 22.59 | 56.82 | 30.5 | 45 | 0.5 | 1.88 | 34.24
2018-12-16 19:00 | 11645.0542 | -0.048233 | 18.71 | 19.68 | 52.87 | 27.27 | 80.8141 | 1 | 12.97 | 17.88
2018-12-16 20:00 | 12671.5541 | -0.048233 | 17.2 | 19.39 | 49.15 | 25 | 45 | 0.95 | 2.45 | 3.1
2018-12-16 21:00 | 11144.4042 | -0.048233 | 81.19 | 81.19 | 43.75 | 24.31 | 45 | 0.95 | 1.99 | 3.1
2018-12-16 22:00 | 10776.7542 | -0.048233 | 1369.8311 | 1102.22 | 43.81 | 21.44 | 25 | 0.95 | 14.65 | 3.09
2018-12-16 23:00 | 10465.1542 | -0.048233 | 876.9511 | 609.34 | 41.58 | 19.47 | 830.3478 | 0.48 | 18.22 | 7.55
2018-12-17 | 10240.9542 | -0.048233 | 3.98 | 28.08 | 41.7 | 17.96 | 25.01 | 0.48 | 20.34 | 3.36
2018-12-17 01:00 | 10182.0542 | -0.048233 | 5.99 | 19.97 | 37.69 | 17.28 | 3.25 | 0.48 | 20 | 2.78
2018-12-17 02:00 | 10125.0542 | -0.048233 | -0.19 | 18.73 | 36.21 | 16.97 | 3.25 | 0.48 | 14.37 | 1.61
2018-12-17 03:00 | 11117.5391 | -0.048233 | -0.54 | 18.6 | 35.64 | 17.95 | 3.25 | 0.6 | 17.61 | 1.61
2018-12-17 04:00 | 10109.8542 | -0.048233 | -0.59 | 20 | 35.92 | 17.86 | 3.25 | 0.6 | 2.39 | 1.11
2018-12-17 05:00 | 11298.9991 | -0.048233 | -0.35 | 26.36 | 37.68 | 17.97 | 3.51 | 0.6 | 20.3 | 2.83
2018-12-17 06:00 | 10582.0042 | -0.048233 | 12.74 | 19.41 | 36.74 | 21.9 | 23.75 | 0.6 | 112.7434 | 84.9262
2018-12-17 07:00 | 10449.0042 | -0.048233 | 11.56 | 19.21 | 39.25 | 22.79 | 37.07 | 2 | 29.98 | 37.07
2018-12-17 08:00 | 10627.3013 | 140.633 | 17.64 | 23.15 | 39.57 | 23.53 | 15.51 | 2 | 12 | 3.74
2018-12-17 09:00 | 11992.7252 | 88.512 | 927.2411 | 659.63 | 48.73 | 30.74 | 35 | 2 | 0.73 | 4.2
2018-12-17 10:00 | 11140.1712 | 107.496 | 17.16 | 30.72 | 35.88 | 26.44 | 6.42 | 2 | 1 | 3.3
2018-12-17 11:00 | 12375.2734 | 127.117 | 14.71 | 24.75 | 38.29 | 24.39 | 5.42 | 0.97 | 22 | 3.3
2018-12-17 12:00 | 12435.2154 | 130.934 | 77.85 | 77.85 | 36.41 | 22.98 | 3.84 | 0.75 | 22 | 2.97
2018-12-17 13:00 | 12399.4287 | 119.013 | 9.41 | 23.43 | 35.84 | 22.32 | 2.89 | 0.75 | 2.11 | 2.61
2018-12-17 14:00 | 11161.1596 | 100.589 | 7.38 | 22.65 | 32.06 | 22.07 | 3.01 | 0.75 | 2 | 2.75
2018-12-17 15:00 | 12242.9313 | 66.6742 | 10.48 | 21.75 | 35.23 | 22 | 2.71 | 0.6 | 2.11 | 1.11
2018-12-17 16:00 | 12282.719 | 49.3877 | 10.11 | 21.54 | 39.94 | 24.11 | 2.9 | 0.6 | 0.35 | 2.01
2018-12-17 17:00 | 12169.5754 | 2.1425 | 13.56 | 22.2 | 54.81 | 40.11 | 3.11 | 0.6 | 0.29 | 2.7
2018-12-17 18:00 | 11004.7542 | -0.048233 | 16.97 | 29.08 | 51.91 | 33.16 | 19.1 | 0.6 | 1.31 | 17.1
2018-12-17 19:00 | 10836.6042 | -0.048233 | 54.62 | 54.62 | 39.59 | 26.3 | 5.2 | 1.06 | 2.61 | 5
2018-12-17 20:00 | 10626.6542 | -0.048233 | 17.9 | 33.09 | 37.21 | 22.99 | 5 | 1.21 | 2.61 | 3.1
2018-12-17 21:00 | 10609.5542 | -0.048233 | 17.14 | 35.65 | 37.24 | 22.33 | 4 | 1 | 2 | 3.1
2018-12-17 22:00 | 11574.3541 | -0.048233 | 17.78 | 21.63 | 35.44 | 20.29 | 3.25 | 0.97 | 2.65 | 3
2018-12-17 23:00 | 11423.4891 | -0.048233 | 16.53 | 20.05 | 29.65 | 20.38 | 4 | 0.6 | 13.24 | 3.72
2018-12-18 | 10123.1542 | -0.048233 | 16.18 | 19.68 | 33.74 | 21.59 | 3.2 | 0.6 | 14.39 | 3.11
2018-12-18 01:00 | 9183.6042 | -0.048233 | 16.35 | 19.31 | 36.65 | 19.47 | 2.61 | 0.75 | 3.46 | 2.83
2018-12-18 02:00 | 9906.3991 | -0.048233 | 15.81 | 18.78 | 12.86 | 19.33 | 2.61 | 0.75 | 1 | 1.8
2018-12-18 03:00 | 8856.8042 | -0.048233 | 15.42 | 18.8 | 12.75 | 19.23 | 2.61 | 1 | 2.11 | 1.36
2018-12-18 04:00 | 8853.9542 | -0.048233 | 13.13 | 18.66 | 15.07 | 19.76 | 3.01 | 1 | 0.29 | 2.03
2018-12-18 05:00 | 8916.6542 | -0.048233 | 13.9 | 18.71 | 36.89 | 21.45 | 3.11 | 1 | 3.01 | 3.11
2018-12-18 06:00 | 10063.5941 | -0.048233 | 18.11 | 19.63 | 45.07 | 34.15 | 5.49 | 1 | 12.11 | 9.39
2018-12-18 07:00 | 10272.3819 | 4.8549 | 16.18 | 23.1 | 42.35 | 31.43 | 44.34 | 7.25 | 2.11 | 44.34
2018-12-18 08:00 | 10595.7648 | 126.379 | 18.09 | 20.23 | 42.44 | 28.94 | 3.7 | 1.31 | 1 | 4
2018-12-18 09:00 | 9854.7585 | 275.43 | 18.01 | 21.27 | 45.32 | 28.75 | 4.36 | 1.65 | 1 | 4.96
2018-12-18 10:00 | 9976.4497 | 477.526 | 17.36 | 21.87 | 46.3 | 28 | 6.01 | 1.22 | 1 | 4.92
2018-12-18 11:00 | 11124.5541 | 590.601 | 16.18 | 22.25 | 42.3 | 26.8 | 5 | 1 | 1 | 4.54
2018-12-18 12:00 | 10102.0378 | 733.724 | 14.45 | 20.47 | 38 | 25.79 | 3.93 | 1 | 1.31 | 3.1
2018-12-18 13:00 | 10291.3927 | 904.045 | 13.09 | 19.75 | 33.69 | 24.8 | 2.32 | 1 | 2.11 | 2.32
2018-12-18 14:00 | 9778.5714 | 413.233 | 12.93 | 19.16 | 32.47 | 24.6 | 2.1 | 1.22 | 1.43 | 2.1
2018-12-18 15:00 | 9673.8243 | 202.973 | 12.72 | 19.17 | 33.89 | 24.97 | 1.62 | 1 | 1 | 1
2018-12-18 16:00 | 10825.9996 | 108.611 | 12.69 | 18.86 | 41 | 26.5 | 1.61 | 1 | 0.84 | 1
2018-12-18 17:00 | 10849.5942 | 5.9756 | 14.62 | 20.03 | 48.3 | 43.71 | 2.72 | 1 | 0.9 | 2.16
2018-12-18 18:00 | 11104.8791 | -0.048233 | 15.36 | 22.41 | 42.19 | 38.59 | 28.1 | 1 | 2 | 20.85
2018-12-18 19:00 | 11131.2541 | -0.048233 | 13.07 | 18.69 | 37.69 | 29.5 | 33.39 | 0.99 | 2.11 | 17.76
2018-12-18 20:00 | 11149.1891 | -0.048233 | 11.08 | 18.43 | 35.34 | 29.51 | 32.5 | 0.99 | 2 | 3.13
2018-12-18 21:00 | 11044.7441 | -0.048233 | 13.03 | 18.09 | 33.61 | 26.44 | 34.09 | 1 | 1 | 23.02
2018-12-18 22:00 | 11069.0091 | -0.048233 | 13.88 | 18.12 | 24.54 | 23.25 | 3.3 | 1 | 2 | 3.25
2018-12-18 23:00 | 11026.8091 | -0.048233 | 13.42 | 17.69 | 23.86 | 20.87 | 4.09 | 0.75 | 11 | 3.55
2018-12-19 | 10888.6041 | -0.048233 | 13.96 | 16.35 | 29.44 | 20.23 | 3.84 | 0.75 | 11 | 3.11
2018-12-19 01:00 | 9849.5542 | -0.048233 | 14.92 | 15.29 | 23.55 | 17.91 | 2.71 | 0.75 | 2.73 | 2.11
2018-12-19 02:00 | 9922.7042 | -0.048233 | 14.03 | 15.2 | 23.57 | 17.28 | 2.11 | 0.5 | 1 | 1.61
2018-12-19 03:00 | 9830.5542 | -0.048233 | 14.86 | 14.86 | 23.55 | 17.79 | 2 | 0.99 | 2.11 | 1.01
2018-12-19 04:00 | 10392.0042 | -0.048233 | 16.24 | 16.76 | 28.12 | 17.59 | 2.11 | 0.99 | 0.06 | 1.61
2018-12-19 05:00 | 11613.7042 | -0.048233 | 17.34 | 17.97 | 31.16 | 20.39 | 2.15 | 0.99 | 2.11 | 2.61
2018-12-19 06:00 | 15345.9791 | -0.048233 | 18.65 | 18.65 | 38.78 | 24.65 | 22.59 | 0.99 | 25.01 | 20.9
2018-12-19 07:00 | 16472.6831 | 3.9177 | 18.29 | 20.04 | 47.6 | 23.9 | 447.6678 | 435.3916 | 2.11 | 449.7706
2018-12-19 08:00 | 16792.6766 | 114.229 | 18.55 | 19.23 | 47.31 | 26.3 | 457.7278 | 447.0216 | 2 | 455.8006
2018-12-19 09:00 | 15276.7942 | 267.836 | 18.09 | 19.67 | 44.54 | 24.86 | 51.77 | 61.0673 | 1 | 44.52
2018-12-19 10:00 | 15065.9274 | 335.871 | 17.98 | 19.79 | 44.64 | 25.6 | 45.76 | 54.7973 | 1 | 38.52
2018-12-19 11:00 | 15024.5407 | 348.306 | 16.74 | 19.89 | 44.68 | 24.88 | 25.08 | 0.99 | 1 | 17.43
2018-12-19 12:00 | 16190.3541 | 347.478 | 15.66 | 19.72 | 42.69 | 24.94 | 4.73 | 0.99 | 1 | 3.35
2018-12-19 13:00 | 16591.1948 | 117.251 | 13.3 | 18.89 | 40.53 | 24.22 | 5.17 | 0.99 | 2 | 3.1
2018-12-19 14:00 | 12539.8204 | 342.811 | 12.83 | 19.23 | 40.39 | 24.57 | 3.04 | 0.99 | 1.93 | 2.59
2018-12-19 15:00 | 13071.9617 | 220.485 | 13.36 | 20.88 | 43.36 | 24.01 | 2.74 | 1.23 | 2 | 1.61
2018-12-19 16:00 | 12816.1359 | 80.9961 | 13.05 | 18.24 | 50.95 | 26 | 2.61 | 0.99 | 0.51 | 1.61
2018-12-19 17:00 | 11459.5372 | 2.6707 | 15.48 | 18.74 | 58.51 | 38.2 | 3 | 0.99 | 0.58 | 1.48
2018-12-19 18:00 | 12463.7191 | -0.048233 | 17.91 | 19.51 | 57.18 | 33.81 | 37.73 | 1.41 | 2 | 33.73
2018-12-19 19:00 | 12415.1891 | -0.048233 | 16.37 | 18.28 | 52.16 | 28.26 | 29.73 | 0.97 | 10.16 | 18.35
2018-12-19 20:00 | 11063.6542 | -0.048233 | 15.59 | 19.87 | 50.04 | 28.77 | 21.98 | 0.97 | 2 | 3.04
2018-12-19 21:00 | 12061.7641 | -0.048233 | 14.44 | 17.9 | 46.12 | 26.55 | 6.01 | 0.97 | 1.42 | 3.42
2018-12-19 22:00 | 10357.8042 | -0.048233 | 15.35 | 18.59 | 40.51 | 24.37 | 5.99 | 0.97 | 11.57 | 2.89
2018-12-19 23:00 | 11289.5041 | -0.048233 | 12.73 | 17.17 | 33.2 | 21.82 | 3.24 | 0.75 | 13.7 | 3
2018-12-20 | 11320.0991 | -0.048233 | 16.27 | 17.36 | 34.5 | 17.78 | 3 | 0.75 | 14.09 | 2.61
2018-12-20 01:00 | 10226.7042 | -0.048233 | 10.3 | 17.08 | 34.07 | 15.79 | 2.41 | 0.5 | 12.46 | 2.21
2018-12-20 02:00 | 11265.2391 | -0.048233 | 9.22 | 15.82 | 37.27 | 15.8 | 2.11 | 0.5 | 2 | 1.91
2018-12-20 03:00 | 10208.6542 | -0.048233 | 8.59 | 16.58 | 37.63 | 16.62 | 2.11 | 0.99 | 2.97 | 1.91
2018-12-20 04:00 | 10370.1542 | -0.048233 | 8.16 | 17.38 | 39.93 | 17.92 | 2.11 | 0.99 | 1.63 | 1.91
2018-12-20 05:00 | 11373.3542 | -0.048233 | 8.1 | 18.09 | 43.25 | 19.26 | 2.61 | 0.99 | 41.52 | 2.41
2018-12-20 06:00 | 13469.0542 | -0.048233 | 14.88 | 18.9 | 49.59 | 24.89 | 35 | 0.99 | 104.5534 | 35
2018-12-20 07:00 | 15749.4926 | 1.429 | 15.77 | 20.86 | 54.07 | 26.15 | 44 | 16.01 | 15.26 | 437.8106
2018-12-20 08:00 | 14487.0277 | 41.5028 | 15.06 | 21.89 | 47.85 | 31.13 | 19.78 | 14.78 | 14.54 | 16.62
2018-12-20 09:00 | 17002.0765 | 86.7123 | 14.63 | 23.71 | 43.65 | 32.54 | 8 | 8.45 | 0.35 | 5.32
2018-12-20 10:00 | 13975.8822 | 105.455 | 14.41 | 30.54 | 36.22 | 32.24 | 7.15 | 9.3 | 0.73 | 5.15
2018-12-20 11:00 | 15046.5408 | 175.124 | 12.32 | 25.88 | 34.26 | 31.77 | 4.45 | 0.99 | 1 | 3.1
2018-12-20 12:00 | 14731.4271 | 185.438 | 11.07 | 21.02 | 32.89 | 33.65 | 5 | 0.99 | 1 | 3.1
2018-12-20 13:00 | 13095.0917 | 172.307 | 11.13 | 19.81 | 32.82 | 29.51 | 3.74 | 0.99 | 1.87 | 2.7
2018-12-20 14:00 | 13106.9868 | 98.6842 | 11.18 | 19.35 | 32.87 | 29.8 | 3 | 0.99 | 1 | 2
2018-12-20 15:00 | 11058.601 | 65.6326 | 10.9 | 18.67 | 32.87 | 30.53 | 2.86 | 0.99 | 1 | 1.44
2018-12-20 16:00 | 10698.5295 | 43.61 | 11.27 | 20.37 | 44.27 | 27.05 | 3 | 1.22 | 0.36 | 2.11
2018-12-20 17:00 | 10659.9227 | 1.9713 | 13.97 | 20.5 | 49.19 | 30.21 | 2.61 | 1.38 | 0.21 | 1.42
2018-12-20 18:00 | 11850.7641 | -0.048233 | 17.11 | 20.69 | 45.06 | 27.55 | 20.06 | 1 | 1.31 | 20.06
2018-12-20 19:00 | 10672.2542 | -0.048233 | 47.38 | 47.38 | 44.62 | 27.79 | 16.72 | 8.05 | 10 | 6
2018-12-20 20:00 | 10484.1542 | -0.048233 | 16.41 | 20.3 | 42.55 | 26.4 | 6.61 | 0.97 | 2.78 | 3.64
2018-12-20 21:00 | 10260.9042 | -0.048233 | 17.04 | 20.32 | 35 | 24.38 | 5.51 | 0.97 | 2.61 | 3.11
2018-12-20 22:00 | 10022.4542 | -0.048233 | 17.29 | 20.4 | 34.96 | 20.19 | 5.01 | 0.97 | 11 | 2.21
2018-12-20 23:00 | 9884.7042 | -0.048233 | 14.16 | 16.33 | 32.95 | 17.66 | 4.69 | 0.75 | 11.92 | 3
2018-12-21 | 10871.7241 | -0.048233 | 12.81 | 12.81 | 41.53 | 14.32 | 3 | 0.5 | 13.21 | 2.21
2018-12-21 01:00 | 9712.7542 | -0.048233 | 5.17 | 5.17 | 38.88 | 8.45 | 3 | 0.5 | 12.89 | 1
2018-12-21 02:00 | 9750.7542 | -0.048233 | 0 | 0 | 37 | 8.55 | 3 | 0.5 | 3.5 | 1
2018-12-21 03:00 | 10818.9741 | -0.048233 | 3.56 | 3.56 | 35.82 | 8.58 | 25 | 0.97 | 12.39 | 1
2018-12-21 04:00 | 11321.1541 | -0.048233 | 7.93 | 7.93 | 35.83 | 10.1 | 3 | 0.97 | 3.5 | 1
2018-12-21 05:00 | 11025.6542 | -0.048233 | 16.95 | 16.95 | 38.51 | 16.83 | 3 | 0.97 | 14.89 | 1.01
2018-12-21 06:00 | 13959.7091 | -0.048233 | 16.19 | 17.48 | 49.18 | 22.87 | 19 | 0.99 | 25.01 | 19
2018-12-21 07:00 | 14851.1716 | 16.9399 | 16.23 | 19.4 | 48.05 | 22.72 | 44.59 | 13.18 | 7.78 | 44.59
2018-12-21 08:00 | 13778.3297 | 415.505 | 16.17 | 19.13 | 46.3 | 24.45 | 7.06 | 6 | 3.25 | 2.82
2018-12-21 09:00 | 16030.9265 | 750.191 | 16.03 | 17.38 | 45.41 | 24 | 6.25 | 3.25 | 3.11 | 4.25
2018-12-21 10:00 | 14439.9553 | 939.953 | 17.48 | 18.64 | 45.37 | 23.1 | 6.29 | 2 | 2 | 3.97
2018-12-21 11:00 | 15239.7588 | 790.269 | 17.21 | 18.52 | 40.27 | 22.88 | 4.65 | 0.99 | 3.25 | 3.1
2018-12-21 12:00 | 17702.594 | 1078.71 | 17.08 | 18.36 | 36.39 | 22.38 | 4.85 | 0.99 | 2.61 | 2
2018-12-21 13:00 | 15344.3525 | 1051.41 | 18.74 | 18.74 | 36.64 | 23.09 | 4.51 | 0.99 | 2.61 | 2.61
2018-12-21 14:00 | 14067.5472 | 942.168 | 16.81 | 21.37 | 36.12 | 22.54 | 4.11 | 1.02 | 3.11 | 2.68
2018-12-21 15:00 | 11646.6352 | 681.616 | 52.03 | 52.03 | 41.28 | 23.07 | 4.71 | 0.99 | 3.01 | 2.53
2018-12-21 16:00 | 10979.4673 | 302.334 | 16.06 | 18.23 | 45.91 | 25.97 | 4.11 | 1 | 1.18 | 1.35
2018-12-21 17:00 | 10675.2793 | 10.1361 | 18.71 | 18.71 | 52.48 | 42.98 | 4.11 | 1 | 2.11 | 1
2018-12-21 18:00 | 10580.1042 | -0.048233 | 19.3 | 19.3 | 46.78 | 26 | 25.06 | 0.99 | 3.25 | 24.86
2018-12-21 19:00 | 11600.7291 | -0.048233 | 18.82 | 18.82 | 45.54 | 23.48 | 8.71 | 0.97 | 3.25 | 4
2018-12-21 20:00 | 10318.8542 | -0.048233 | 17.89 | 17.89 | 47 | 21.89 | 4.95 | 0.97 | 3.25 | 1.98
2018-12-21 21:00 | 11259.9641 | -0.048233 | 15.74 | 16.82 | 44.15 | 20.15 | 3 | 0.97 | 3.04 | 1
2018-12-21 22:00 | 9908.4542 | -0.048233 | 14.11 | 16.54 | 40.18 | 18.7 | 3 | 0.97 | 3.5 | 1
2018-12-21 23:00 | 10739.8491 | -0.048233 | 12.89 | 16.8 | 35.01 | 18.04 | 4.51 | 0.5 | 11 | 2.61
2018-12-22 | 9662.4042 | -0.048233 | 11.94 | 14.09 | 41.7 | 18.06 | 6.25 | 0.5 | 15.06 | 2.11
2018-12-22 01:00 | 9594.0042 | -0.048233 | 1.27 | 1.27 | 38.44 | 17 | 6.01 | 0.5 | 10.77 | 1.11
2018-12-22 02:00 | 9534.1542 | -0.048233 | 9.6 | 9.6 | 36.66 | 16.01 | 6.01 | 0.5 | 9.1 | 1
2018-12-22 03:00 | 10573.1591 | -0.048233 | 1.58 | 1.58 | 36.43 | 15.3 | 6.01 | 0.99 | 4.11 | 0.74
2018-12-22 04:00 | 10703.9791 | -0.048233 | 10.82 | 12.95 | 37.5 | 15.32 | 6.01 | 0.99 | 3.5 | 1
2018-12-22 05:00 | 11601.7841 | -0.048233 | 9.41 | 9.92 | 39.89 | 17.5 | 6.01 | 0.99 | 11.89 | 1.11
2018-12-22 06:00 | 12025.0542 | -0.048233 | 4.48 | 4.48 | 47.83 | 19.99 | 17.5 | 0.99 | 110.7434 | 17.5
2018-12-22 07:00 | 13001.0888 | 16.3566 | 12.89 | 15.17 | 49.29 | 20.8 | 44.66 | 15 | 11.29 | 44.66
2018-12-22 08:00 | 15275.9653 | 415.588 | 13.53 | 15.97 | 47.59 | 21.22 | 4.75 | 6 | 2.32 | 3.09
2018-12-22 09:00 | 16456.4755 | 764.555 | 15.21 | 17.25 | 49.91 | 21.42 | 5.37 | 6.32 | 1.61 | 4.37
2018-12-22 10:00 | 15459.6134 | 968.662 | 15.58 | 17.81 | 42.5 | 23.21 | 5.54 | 8.45 | 1 | 4.54
2018-12-22 11:00 | 15181.2706 | 1075.83 | 15.84 | 19.08 | 40.52 | 23.39 | 6.07 | 1 | 2.22 | 3.99
2018-12-22 12:00 | 15306.001 | 1109.58 | 13.38 | 18.87 | 39.67 | 24.78 | 6.01 | 1 | 2.11 | 3.1
2018-12-22 13:00 | 14924.5649 | 978.507 | 13.13 | 19.14 | 38.96 | 25.03 | 6.01 | 1.23 | 2.11 | 3.3
2018-12-22 14:00 | 12514.9086 | 910.588 | 11.2 | 18.36 | 37.26 | 27.13 | 5.25 | 1 | 1.73 | 3.1
2018-12-22 15:00 | 11755.4558 | 706.164 | 10.99 | 18.2 | 39.36 | 28.22 | 2.96 | 1 | 1 | 1.45
2018-12-22 16:00 | 12308.6228 | 319.941 | 11.91 | 18.65 | 45.35 | 29.9 | 4 | 1 | 0.49 | 1.45
2018-12-22 17:00 | 11981.7889 | 10.1459 | 14.39 | 20.11 | 50.2 | 46.98 | 4 | 1 | 0.65 | 2.47
2018-12-22 18:00 | 11796.9591 | -0.048233 | 47.92 | 24.23 | 41.02 | 33.52 | 29.11 | 1.21 | 2.11 | 25.26
2018-12-22 19:00 | 10559.2042 | -0.048233 | 13.78 | 22.07 | 39.85 | 30.35 | 8.21 | 1.1 | 1.8 | 5
2018-12-22 20:00 | 10348.3042 | -0.048233 | 13.9 | 20.96 | 37.29 | 27.87 | 6.01 | 1 | 1 | 1.71
2018-12-22 21:00 | 9977.8042 | -0.048233 | 13.07 | 19.97 | 31.8 | 26.48 | 5.44 | 1 | 0.69 | 2.51
2018-12-22 22:00 | 10834.7991 | -0.048233 | 322.5557 | 19.06 | 31.63 | 22.21 | 4 | 1 | 2.17 | 2.98
2018-12-22 23:00 | 10630.1291 | -0.048233 | 14.55 | 18.53 | 23.79 | 19.95 | 28.05 | 0.75 | 12.7 | 28.05
2018-12-23 | 9550.3042 | -0.048233 | 6.19 | 17.51 | 38.77 | 17.29 | 30 | 0.75 | 39.12 | 29.8
2018-12-23 01:00 | 9558.8542 | -0.048233 | 4.7 | 15.47 | 31.26 | 16.02 | 2 | 0.5 | 18.58 | 1.61
2018-12-23 02:00 | 9564.5542 | -0.048233 | 3.91 | 17.31 | 29.13 | 16.02 | 2 | 0.5 | 0.49 | 1
2018-12-23 03:00 | 9540.8042 | -0.048233 | 3.79 | 17.49 | 24.58 | 16.27 | 2 | 0.97 | 2.01 | 1
2018-12-23 04:00 | 9685.2042 | -0.048233 | 4.22 | 18.2 | 31.29 | 16.71 | 2 | 0.97 | 0.01 | 1
2018-12-23 05:00 | 11426.6541 | -0.048233 | 4.6 | 18.84 | 32.41 | 17.63 | 2 | 0.97 | 21.92 | 2.11
2018-12-23 06:00 | 11533.9042 | -0.048233 | 6.94 | 19.63 | 46.13 | 20.07 | 24.75 | 0.97 | 52.6462 | 24.75
2018-12-23 07:00 | 13407.5842 | 14.6106 | 12.57 | 19.59 | 43.85 | 22.86 | 52 | 15 | 2.61 | 77.1162
2018-12-23 08:00 | 12703.3069 | 388.902 | 11.43 | 19.85 | 36.63 | 26.67 | 6.01 | 6.3 | 16.32 | 4
2018-12-23 09:00 | 13395.798 | 670.84 | 15.25 | 19.67 | 40.07 | 28.89 | 6 | 6 | 0.73 | 5.13
2018-12-23 10:00 | 15499.8026 | 967.756 | 16.96 | 19.53 | 39.4 | 26.88 | 8 | 3.6 | 1 | 4.59
2018-12-23 11:00 | 13503.1765 | 1056.87 | 62.73 | 18.91 | 39.93 | 21.58 | 5.69 | 0.99 | 0.91 | 3.1
2018-12-23 12:00 | 14527.5235 | 1103.13 | 18.01 | 18.01 | 33.03 | 21.71 | 3.27 | 0.99 | 1 | 2.49
2018-12-23 13:00 | 12942.762 | 1047.96 | 17.02 | 17.02 | 30.38 | 20.54 | 3.99 | 0.99 | 2.06 | 3
2018-12-23 14:00 | 13551.7588 | 937.269 | 16.15 | 16.15 | 23.85 | 20.71 | 4.1 | 1.37 | 1.04 | 3.1
2018-12-23 15:00 | 12657.1325 | 645.282 | 61.33 | 15 | 30.29 | 19.81 | 3.91 | 0.99 | 2 | 2.61
2018-12-23 16:00 | 12197.354 | 314.473 | 14.93 | 14.93 | 37.56 | 21.62 | 3.91 | 0.99 | 0.22 | 3
2018-12-23 17:00 | 11702.4501 | 12.3698 | 15.63 | 15.63 | 40.63 | 25.13 | 4.66 | 1.31 | 0.28 | 2.29
2018-12-23 18:00 | 10505.0542 | -0.048233 | 17.06 | 17.06 | 34.2 | 27.14 | 25.2 | 11.25 | 12.38 | 25
2018-12-23 19:00 | 10360.6542 | -0.048233 | 16.78 | 16.78 | 31.63 | 26.84 | 14.91 | 1.2 | 20 | 3.79
2018-12-23 20:00 | 11349.6391 | -0.048233 | 18.02 | 18.98 | 25.82 | 26.91 | 6.01 | 0.99 | 3.01 | 1.61
2018-12-23 21:00 | 10091.8042 | -0.048233 | 16.88 | 19.04 | 28.21 | 23.34 | 4.76 | 0.95 | 2.11 | 1.96
2018-12-23 22:00 | 11005.7091 | -0.048233 | 18.93 | 18.93 | 30.12 | 19.04 | 4.64 | 0.95 | 29 | 3.11
2018-12-23 23:00 | 10847.4591 | -0.048233 | 16.51 | 18.45 | 23.29 | 18.86 | 16.82 | 0.5 | 13.73 | 14
2018-12-24 | 10765.1691 | -0.048233 | 13.11 | 17.91 | 7.23 | 18.58 | 16 | 0.5 | 13.22 | 3.11
2018-12-24 01:00 | 9557.9042 | -0.048233 | 10.34 | 17.66 | 4.76 | 15.95 | 4 | 0.5 | 8.03 | 3.05
2018-12-24 02:00 | 10346.3341 | -0.048233 | 3.33 | 17.48 | 3.82 | 15.83 | 3.15 | 0.5 | 2.66 | 1
2018-12-24 03:00 | 8957.5042 | -0.048233 | 1.55 | 16.42 | 3.33 | 16.52 | 28 | 0.82 | 2.86 | 1
2018-12-24 04:00 | 8040.1041 | -0.048233 | 4.64 | 16.92 | 3.85 | 16.47 | 28 | 0.82 | 1 | 1.61
2018-12-24 05:00 | 7258.9042 | -0.048233 | 8.96 | 16.94 | 5.17 | 17.23 | 25 | 0.82 | 13.96 | 3
2018-12-24 06:00 | 7472.6542 | -0.048233 | 9.76 | 16.64 | 9.77 | 21.69 | 35 | 0.82 | 110.9034 | 94.7062
2018-12-24 07:00 | 7485.5148 | 5.4893 | 12.65 | 16.44 | 32.82 | 21.28 | 5 | 8 | 30.35 | 32
2018-12-24 08:00 | 7541.7317 | 187.665 | 14.49 | 18.18 | 35.78 | 23.43 | 4.94 | 2 | 57.6962 | 4.75
2018-12-24 09:00 | 9029.6321 | 695.893 | 16.35 | 17.86 | 36.93 | 21.42 | 4.6 | 3 | 0.79 | 4.2
2018-12-24 10:00 | 8440.5172 | 939.755 | 333.7757 | 16.77 | 40.13 | 20.31 | 5.1 | 2 | 1 | 3.3
2018-12-24 11:00 | 9386.9712 | 926.603 | 16.08 | 16.08 | 41.86 | 18.27 | 4.25 | 0.99 | 24 | 4
2018-12-24 12:00 | 9387.5103 | 911.114 | 16.42 | 16.42 | 36.98 | 18.53 | 4 | 0.97 | 24 | 3.1
2018-12-24 13:00 | 9506.7 | 1087.09 | 16.77 | 16.77 | 33.54 | 18.14 | 4 | 0.99 | 57.6962 | 3
2018-12-24 14:00 | 8443.4585 | 942.851 | 17.03 | 17.03 | 33.04 | 18.96 | 4 | 0.99 | 2.11 | 3
2018-12-24 15:00 | 8193.2721 | 699.497 | 17.34 | 17.34 | 33.67 | 19.09 | 4 | 0.5 | 2.11 | 3
2018-12-24 16:00 | 7967.575 | 313.921 | 17.62 | 17.62 | 47.95 | 21.04 | 4 | 0.5 | 0.44 | 3
2018-12-24 17:00 | 8467.624 | 10.1839 | 18.05 | 18.05 | 55.64 | 29.23 | 4.57 | 0.5 | 0.3 | 3
2018-12-24 18:00 | 8582.3741 | -0.048233 | 17.65 | 19.67 | 49.81 | 31.82 | 20 | 18.6 | 57.6962 | 25
2018-12-24 19:00 | 8528.5691 | -0.048233 | 16.84 | 19.44 | 47.36 | 32.12 | 15 | 9.34 | 57.6962 | 3.2
2018-12-24 20:00 | 7727.2542 | -0.048233 | 15.81 | 18.92 | 38.59 | 27.95 | 5.6 | 0.99 | 19.72 | 3.1
2018-12-24 21:00 | 8434.6741 | -0.048233 | 13.89 | 18.93 | 33.68 | 22.56 | 5.64 | 0.97 | 30.8 | 3.1
2018-12-24 22:00 | 7433.7042 | -0.048233 | 16.54 | 18.55 | 38.37 | 20.85 | 4 | 0.97 | 57.6962 | 3.2
2018-12-24 23:00 | 8188.8591 | -0.048233 | 4.55 | 17.11 | 11.04 | 19.59 | 24 | 0.5 | 35.46 | 22
2018-12-25 | 7390.9542 | -0.048233 | -0.01 | 16.96 | 3.51 | 20.69 | 2.77 | 0.5 | 22.47 | 3
2018-12-25 01:00 | 8234.2241 | -0.048233 | -0.49 | 17.42 | 1.67 | 18.81 | 3.79 | 0.5 | 18.8 | 4.61
2018-12-25 02:00 | 7368.1542 | -0.048233 | -0.7 | 16.76 | 1.63 | 18.65 | 3 | 0.5 | 14.77 | 2.61
2018-12-25 03:00 | 7339.6542 | -0.048233 | -0.99 | 17.09 | 2.03 | 18.4 | 25 | 0.62 | 15.1 | 2.11
2018-12-25 04:00 | 7323.5042 | -0.048233 | -1.25 | 17.27 | 1.59 | 18.74 | 25 | 0.62 | 0.41 | 2.51
2018-12-25 05:00 | 8141.3841 | -0.048233 | -3.07 | 17.75 | 2.54 | 19.86 | 25 | 0.62 | 16.4 | 3.02
2018-12-25 06:00 | 8189.9141 | -0.048233 | -1.26 | 17.95 | 4.2 | 24.98 | 30 | 0.62 | 254.1234 | 549.3306
2018-12-25 07:00 | 8180.416 | 10.9488 | -0.79 | 17.95 | 4.69 | 23.58 | 33.6 | 2 | 40 | 83.2062
2018-12-25 08:00 | 8362.4353 | 309.479 | -0.67 | 17.7 | 33.16 | 24.13 | 5.35 | 2 | 30 | 4.64
2018-12-25 09:00 | 7708.8833 | 548.614 | 3.12 | 17.95 | 46.28 | 24.9 | 4.47 | 3.11 | 0.35 | 4.2
2018-12-25 10:00 | 9021.9517 | 934.613 | 11.36 | 18.03 | 45.43 | 22.03 | 5.63 | 3 | 0.87 | 4.74
2018-12-25 11:00 | 9140.8744 | 976.973 | 16.94 | 17.88 | 49.02 | 20.58 | 5.36 | 1.2 | 1 | 3.3
2018-12-25 12:00 | 9894.9695 | 907.118 | 17.04 | 17.04 | 44.63 | 19.32 | 4.25 | 1.11 | 1.95 | 3.1
2018-12-25 13:00 | 9948.2596 | 1014.63 | 16.3 | 16.3 | 33.21 | 18.58 | 4.25 | 0.97 | 15 | 3.18
2018-12-25 14:00 | 9897.1955 | 931.228 | 80.3 | 15.15 | 10.18 | 18.27 | 4.25 | 0.99 | 2.61 | 3.1
2018-12-25 15:00 | 8786.1073 | 653.534 | 15.74 | 15.74 | 33.24 | 18.36 | 4.19 | 0.5 | 2.61 | 3.1
2018-12-25 16:00 | 9691.2606 | 309.029 | 15.85 | 16.36 | 47.21 | 19.05 | 4.25 | 0.5 | 1.28 | 3.1
2018-12-25 17:00 | 8357.2198 | 13.0735 | 14.8 | 17.07 | 60.16 | 21.55 | 5 | 0.5 | 1 | 3.2
2018-12-25 18:00 | 8247.8542 | -0.048233 | 17.12 | 17.79 | 56.47 | 25.43 | 27.01 | 17.13 | 12.38 | 28.11
2018-12-25 19:00 | 8316.2542 | -0.048233 | 14.55 | 17.01 | 56.42 | 22.66 | 18 | 1.24 | 3.11 | 6
2018-12-25 20:00 | 8273.5042 | -0.048233 | 11.98 | 17.59 | 48.61 | 21.89 | 5 | 1 | 2.61 | 3.2
2018-12-25 21:00 | 8239.3042 | -0.048233 | 10.76 | 17.29 | 46.7 | 21.2 | 5.76 | 0.82 | 1.66 | 3.1
2018-12-25 22:00 | 8179.4542 | -0.048233 | 9.7 | 16.69 | 34.31 | 19.55 | 5.26 | 0.82 | 11 | 4.26
2018-12-25 23:00 | 8100.6042 | -0.048233 | 8.87 | 16.44 | 7.88 | 18.9 | 5.1 | 0.5 | 25 | 20.96
2018-12-26 | 8203.2042 | -0.048233 | -0.15 | 15.7 | 57.21 | 19.72 | 4.24 | 0.5 | 22 | 4
2018-12-26 01:00 | 9011.7591 | -0.048233 | -0.17 | 15.59 | 42.7 | 18.1 | 25.82 | 0.5 | 10 | 25
2018-12-26 02:00 | 8173.7542 | -0.048233 | 0 | 15.55 | 44.04 | 18.23 | 25 | 0.5 | 11.6 | 2.8
2018-12-26 03:00 | 8037.9042 | -0.048233 | -0.55 | 15.81 | 42.75 | 18.43 | 50 | 0.74 | 10 | 2.8
2018-12-26 04:00 | 8875.6641 | -0.048233 | -0.26 | 15.88 | 45.44 | 18.93 | 50 | 0.74 | 1 | 2.8
2018-12-26 05:00 | 8093.9542 | -0.048233 | -0.01 | 16.61 | 45.52 | 20.18 | 50 | 0.74 | 15.99 | 3.15
2018-12-26 06:00 | 9130.9741 | -0.048233 | 9.99 | 16.78 | 51.13 | 27.29 | 100.8141 | 0.74 | 108.9934 | 99.9162
2018-12-26 07:00 | 8158.6822 | 14.0865 | 9.09 | 17.7 | 60.27 | 27.61 | 44.56 | 6.03 | 57.6962 | 44.56
2018-12-26 08:00 | 9573.5743 | 420.478 | 8.5 | 18.2 | 49.56 | 31.79 | 6.2 | 2.61 | 26.63 | 4.84
2018-12-26 09:00 | 9943.1112 | 748.75 | 13.5 | 18.63 | 55.72 | 32.49 | 5 | 2.75 | 0.22 | 4.64
2018-12-26 10:00 | 10170.8773 | 956.642 | 15.01 | 18.84 | 52.04 | 31.34 | 7.91 | 2.75 | 1 | 5.52
2018-12-26 11:00 | 10435.6907 | 1108.65 | 14.85 | 18.67 | 50.42 | 25.86 | 6.01 | 0.99 | 19.31 | 3.3
2018-12-26 12:00 | 9669.214 | 1137.12 | 15.2 | 18.76 | 50.41 | 23.87 | 3.99 | 1 | 1 | 2.61
2018-12-26 13:00 | 10811.3551 | 1078.73 | 15.36 | 18.76 | 44.69 | 22.98 | 2.82 | 1 | 1.77 | 1.63
2018-12-26 14:00 | 9393.0974 | 947.471 | 14.04 | 18.66 | 44.7 | 22.61 | 2.49 | 1 | 1 | 1.48
2018-12-26 15:00 | 9281.956 | 660.48 | 12.01 | 18.54 | 48.3 | 22.46 | 2.11 | 0.5 | 1 | 1.48
2018-12-26 16:00 | 10160.7683 | 344.06 | 10.69 | 18.82 | 59.64 | 22.82 | 2 | 0.5 | 0.42 | 1.48
2018-12-26 17:00 | 8813.9783 | 13.8719 | 12.72 | 19.65 | 76.67 | 38.13 | 3.05 | 0.5 | 0.78 | 2.61
2018-12-26 18:00 | 8830.2042 | -0.048233 | 339.5357 | 22.05 | 66.77 | 32.79 | 25.69 | 15.97 | 1.15 | 25.49
2018-12-26 19:00 | 9703.8391 | -0.048233 | 15.2 | 21.83 | 65.58 | 26.41 | 22.76 | 0.97 | 2 | 14.11
2018-12-26 20:00 | 8704.8042 | -0.048233 | 12.99 | 21.08 | 60.31 | 26.13 | 5.91 | 0.97 | 1.18 | 2.51
2018-12-26 21:00 | 9547.6991 | -0.048233 | 46.29 | 20.52 | 51.26 | 24.34 | 5.44 | 0.97 | 0.93 | 3.1
2018-12-26 22:00 | 8503.4042 | -0.048233 | 13.91 | 20.24 | 50.19 | 22.29 | 4 | 0.97 | 11 | 2.51
2018-12-26 23:00 | 9416.8791 | -0.048233 | 13.05 | 19.81 | 45.16 | 21.28 | 28.92 | 0.5 | 13.2 | 26.92
2018-12-27 | 8317.2042 | -0.048233 | 12.47 | 19.37 | 62.95 | 18.76 | 27.65 | 0.5 | 13.05 | 25.65
2018-12-27 01:00 | 9079.2791 | -0.048233 | 1.68 | 19.14 | 54.91 | 18.2 | 26.45 | 0.59 | 11 | 26.25
2018-12-27 02:00 | 9064.5091 | -0.048233 | 1.9 | 18.65 | 46.3 | 18.23 | 25 | 0.5 | 1.8 | 2.11
2018-12-27 03:00 | 9032.8591 | -0.048233 | 7.44 | 18.83 | 50.44 | 18.67 | 25 | 0.99 | 2.11 | 2.11
2018-12-27 04:00 | 8059.7542 | -0.048233 | 1.72 | 19.29 | 51.04 | 19.46 | 25 | 0.99 | 1 | 2.11
2018-12-27 05:00 | 9339.8641 | -0.048233 | 8.27 | 19.23 | 63.22 | 20.73 | 25 | 1 | 15 | 3.23
2018-12-27 06:00 | 9807.2291 | -0.048233 | 1.77 | 19.56 | 62.29 | 32.92 | 50 | 0.99 | 107.1434 | 50
2018-12-27 07:00 | 9427.6858 | 10.8798 | 8.24 | 20.33 | 63.54 | 30.73 | 41 | 20.33 | 2 | 41
2018-12-27 08:00 | 11177.0097 | 366.322 | 11.26 | 21.2 | 67.26 | 25.68 | 6.89 | 13.29 | 1.12 | 4.77
2018-12-27 09:00 | 11759.7168 | 604.651 | 11.88 | 20.74 | 67.75 | 25.32 | 6.01 | 9.48 | 0.83 | 4.74
2018-12-27 10:00 | 10691.6078 | 756.324 | 14.83 | 21.71 | 71.57 | 25.23 | 5.15 | 11.61 | 1 | 4.22
2018-12-27 11:00 | 10847.0344 | 880.931 | 15.66 | 21.55 | 71.27 | 24.76 | 4.35 | 1.2 | 1 | 3.85
2018-12-27 12:00 | 12443.5351 | 1023.82 | 13.53 | 22.65 | 64.32 | 24.43 | 4.25 | 0.99 | 1 | 3
2018-12-27 13:00 | 11089.957 | 975.639 | 13.84 | 21.9 | 59.72 | 23.01 | 3.12 | 1 | 2 | 2.96
2018-12-27 14:00 | 11001.1216 | 863.128 | 13.03 | 21.34 | 59.56 | 22.46 | 2.31 | 1 | 1 | 1.34
2018-12-27 15:00 | 12108.5082 | 597.259 | 11.95 | 21.01 | 62.23 | 22.54 | 2 | 1 | 1 | 1
2018-12-27 16:00 | 10239.7184 | 142.651 | 11.19 | 21.36 | 121.147 | 24.24 | 2 | 1.33 | 0.9 | 1.33
2018-12-27 17:00 | 9952.1896 | 4.989 | 12.69 | 23.66 | 156.887 | 35.08 | 2.61 | 1 | 0.69 | 2.27
2018-12-27 18:00 | 9900.8542 | -0.048233 | 13.33 | 27.8 | 146.307 | 37.26 | 35.01 | 17.98 | 2 | 35.01
2018-12-27 19:00 | 10844.2941 | -0.048233 | 13.85 | 25.24 | 120.017 | 34.55 | 21 | 13.46 | 2.11 | 16.91
2018-12-27 20:00 | 10559.4441 | -0.048233 | 13.35 | 25.1 | 87.82 | 30.55 | 8.98 | 10.82 | 2 | 3.1
2018-12-27 21:00 | 10287.2541 | -0.048233 | 85.71 | 85.71 | 64.64 | 31.26 | 6.01 | 10.82 | 1.28 | 3.1
2018-12-27 22:00 | 10099.4641 | -0.048233 | 11.01 | 22.42 | 61.75 | 24.85 | 5 | 1.08 | 11 | 3.2
2018-12-27 23:00 | 9031.6042 | -0.048233 | 12.23 | 21.41 | 61.68 | 22.19 | 3.25 | 0.97 | 11 | 3
2018-12-28 | 8970.8042 | -0.048233 | 12.02 | 19.87 | 150.407 | 20.73 | 2.61 | 0.97 | 11 | 2.61
2018-12-28 01:00 | 8966.0542 | -0.048233 | 6.36 | 19.61 | 86.88 | 20.3 | 1.38 | 0.5 | 10.96 | 1.36
2018-12-28 02:00 | 9970.7541 | -0.048233 | 4.07 | 19.49 | 74.54 | 20.22 | 1.36 | 0.5 | 1 | 1.01
2018-12-28 03:00 | 9923.2791 | -0.048233 | 5.02 | 19.43 | 81.15 | 20.3 | 25 | 0.74 | 1.89 | 1.01
2018-12-28 04:00 | 9948.5991 | -0.048233 | 9.65 | 19.63 | 75.73 | 20.56 | 25 | 0.74 | 0.97 | 1.01
2018-12-28 05:00 | 9258.6542 | -0.048233 | 10.05 | 19.71 | 75.69 | 22.76 | 1.36 | 0.74 | 12.29 | 1.36
2018-12-28 06:00 | 9666.2042 | -0.048233 | 11.28 | 20.33 | 81.27 | 43.46 | 1.95 | 0.74 | 26 | 25
2018-12-28 07:00 | 9987.884 | 11.5621 | 13.36 | 21.64 | 138.087 | 39.02 | 18.89 | 7.55 | 2 | 18.89
2018-12-28 08:00 | 10401.2973 | 389.734 | 13.44 | 22.16 | 137.487 | 30.86 | 6 | 11.68 | 1.28 | 5
2018-12-28 09:00 | 10450.2318 | 683.244 | 13.83 | 27.8 | 153.207 | 30.45 | 6.18 | 8.55 | 1 | 4.18
2018-12-28 10:00 | 11732.8154 | 917.152 | 13.96 | 28.8 | 135.457 | 28.78 | 5.07 | 1.99 | 1 | 3.64
2018-12-28 11:00 | 11707.4299 | 1035.09 | 12.54 | 25.32 | 121.457 | 25.97 | 4 | 0.99 | 1.85 | 3.1
2018-12-28 12:00 | 11930.8578 | 1085.87 | 13.62 | 23.05 | 82.79 | 24.09 | 3.79 | 0.99 | 2 | 2.78
2018-12-28 13:00 | 10848.8195 | 1016.81 | 15 | 21.59 | 74.14 | 23.28 | 2.33 | 0.99 | 2.11 | 1.03
2018-12-28 14:00 | 10681.3829 | 906.561 | 15.32 | 20.61 | 72.99 | 23.4 | 2.59 | 1 | 1 | 2.51
2018-12-28 15:00 | 12020.1436 | 703.501 | 15.85 | 19.89 | 80.21 | 23.13 | 2.11 | 0.74 | 1.46 | 1.91
2018-12-28 16:00 | 11398.4563 | 377.224 | 16.08 | 19.89 | 153.327 | 25.01 | 2.35 | 0.74 | 1.38 | 2.15
2018-12-28 17:00 | 10997.2463 | 14.9301 | 18.06 | 20.81 | 553.5892 | 41.42 | 3.55 | 0.74 | 1 | 3
2018-12-28 18:00 | 10897.0441 | -0.048233 | 22.8 | 23.42 | 536.3492 | 44.34 | 32.49 | 25.9 | 1 | 32.49
2018-12-28 19:00 | 9635.8042 | -0.048233 | 19.96 | 22.17 | 511.6492 | 31.76 | 28.39 | 25.62 | 2.61 | 28.19
2018-12-28 20:00 | 9452.4542 | -0.048233 | 19.45 | 31.2 | 150.247 | 47.35 | 6.41 | 11.12 | 2.11 | 3.1
2018-12-28 21:00 | 10422.2941 | -0.048233 | 18.08 | 20.75 | 122.587 | 40.5 | 5.03 | 10.72 | 1.3 | 3.1
2018-12-28 22:00 | 9345.1042 | -0.048233 | 16.31 | 23.89 | 80.92 | 24.28 | 4.55 | 0.99 | 2.11 | 3.2
2018-12-28 23:00 | 10228.1741 | -0.048233 | 15.64 | 19.53 | 81.1 | 22.87 | 2.71 | 0.5 | 3.5 | 2.71
2018-12-29 | 10251.3841 | -0.048233 | 17 | 20.07 | 84.08 | 21.91 | 2.69 | 0.5 | 8.53 | 2.69
2018-12-29 01:00 | 9229.2042 | -0.048233 | 16.19 | 19.64 | 77.68 | 21.41 | 1.85 | 0.5 | 10 | 1.59
2018-12-29 02:00 | 9043.9542 | -0.048233 | 7.76 | 19.54 | 72.62 | 20.97 | 1.6 | 0.5 | 0.32 | 1
2018-12-29 03:00 | 8940.4042 | -0.048233 | 10.49 | 19.43 | 72.18 | 21.03 | 1.6 | 0.65 | 2.11 | 0.77
2018-12-29 04:00 | 10015.0641 | -0.048233 | 1.73 | 19.26 | 79.86 | 20.83 | 1.6 | 0.65 | 0.15 | 0.54
2018-12-29 05:00 | 10161.7091 | -0.048233 | 10.25 | 19.32 | 119.947 | 22.88 | 1.86 | 0.65 | 2.11 | 1.15
2018-12-29 06:00 | 9478.1042 | -0.048233 | 17.67 | 19.69 | 130.817 | 43.13 | 2 | 0.65 | 20 | 25
2018-12-29 07:00 | 10950.7348 | 10.8434 | 18.86 | 19.69 | 152.047 | 33.92 | 31.22 | 8.57 | 3.5 | 32
2018-12-29 08:00 | 10036.3377 | 367.566 | 18.59 | 19.72 | 521.3592 | 29.55 | 19.2 | 11.04 | 1.12 | 18.86
2018-12-29 09:00 | 9835.1856 | 678.827 | 19.14 | 19.76 | 507.9492 | 36.82 | 6.9 | 1 | 0.26 | 4
2018-12-29 10:00 | 10528.6447 | 912.758 | 19.21 | 19.65 | 492.3292 | 32.92 | 3.63 | 1 | 1 | 3.1
2018-12-29 11:00 | 10416.3378 | 854.306 | 18.52 | 19.64 | 138.287 | 28.23 | 3.85 | 0.97 | 1.06 | 3
2018-12-29 12:00 | 9558.064 | 1064.12 | 18.56 | 19.34 | 127.507 | 26.49 | 3.67 | 0.97 | 2 | 3
2018-12-29 13:00 | 9547.7755 | 1031.29 | 18.45 | 18.8 | 85.02 | 23.52 | 3.15 | 0.97 | 2.11 | 2.76
2018-12-29 14:00 | 9256.6432 | 872.835 | 17.74 | 18.84 | 82.74 | 21.79 | 2.61 | 0.97 | 1 | 2.23
2018-12-29 15:00 | 8959.8043 | 333.373 | 17.59 | 18.72 | 121.287 | 21.99 | 2.61 | 0.74 | 1 | 1
2018-12-29 16:00 | 9916.3818 | 338.414 | 18.15 | 18.8 | 140.607 | 23.11 | 2.35 | 0.74 | 0.85 | 1
2018-12-29 17:00 | 8509.7498 | 18.6314 | 19.42 | 19.59 | 580.2492 | 34.87 | 3 | 0.74 | 0.43 | 1.81
2018-12-29 18:00 | 8499.6042 | -0.048233 | 19.73 | 19.73 | 553.2592 | 33.19 | 20.54 | 0.74 | 2.11 | 18.33
2018-12-29 19:00 | 8364.7042 | -0.048233 | 19.76 | 19.76 | 476.3892 | 27.11 | 19.91 | 14.22 | 2.61 | 6.07
2018-12-29 20:00 | 9271.2891 | -0.048233 | 20.18 | 20.21 | 134.267 | 28.55 | 4.86 | 0.95 | 2 | 1.56
2018-12-29 21:00 | 8973.7791 | -0.048233 | 19.12 | 20 | 120.227 | 27.7 | 2.61 | 0.95 | 0.95 | 1.99
2018-12-29 22:00 | 7922.0042 | -0.048233 | 19.86 | 19.87 | 85.93 | 20.76 | 2.61 | 0.95 | 2.61 | 3
2018-12-29 23:00 | 8658.3341 | -0.048233 | 17.51 | 19.47 | 83.99 | 21.55 | 2.11 | 0.5 | 11 | 2.18
2018-12-30 | 8609.8041 | -0.048233 | 18.07 | 19.03 | 85.81 | 21.18 | 2.18 | 0.5 | 10.18 | 2.5
2018-12-30 01:00 | 7690.2042 | -0.048233 | 17.64 | 18.81 | 81.5 | 20.18 | 2 | 0.49 | 9.11 | 1.75
2018-12-30 02:00 | 7669.3042 | -0.048233 | 17.11 | 19.57 | 72.76 | 19.81 | 2 | 0.49 | 1.55 | 1.39
2018-12-30 03:00 | 8516.9641 | -0.048233 | 15.52 | 19.31 | 74.07 | 20.22 | 2 | 0.62 | 2.61 | 1
2018-12-30 04:00 | 8645.6741 | -0.048233 | 18.16 | 19.35 | 80.17 | 20.64 | 2 | 0.62 | 1 | 1.11
2018-12-30 05:00 | 9023.3641 | -0.048233 | 19.13 | 19.3 | 122.407 | 21.5 | 2 | 0.65 | 11.73 | 1.51
2018-12-30 06:00 | 8500.5542 | -0.048233 | 18.17 | 18.17 | 86.41 | 28.72 | 2.24 | 0.65 | 15.39 | 23.92
2018-12-30 07:00 | 8742.836 | 3.9852 | 18.52 | 18.52 | 87.52 | 26.24 | 20.84 | 7.27 | 3.5 | 20.84
2018-12-30 08:00 | 9543.7505 | 170.209 | 18.72 | 18.72 | 156.527 | 27.86 | 3.24 | 7.88 | 2.23 | 2.71
2018-12-30 09:00 | 8833.0535 | 539.951 | 18.9 | 18.9 | 524.3592 | 34.19 | 4.1 | 2.14 | 0.45 | 3.46
2018-12-30 10:00 | 8839.6474 | 547.892 | 19 | 19 | 522.6092 | 33.03 | 4.79 | 2 | 0.92 | 4.64
2018-12-30 11:00 | 10103.7994 | 853.061 | 19.25 | 19.25 | 472.3792 | 26.55 | 4.48 | 0.97 | 1 | 3.12
2018-12-30 12:00 | 8949.2584 | 754.272 | 19.44 | 19.44 | 79.59 | 25.09 | 2.98 | 0.97 | 1 | 2.88
2018-12-30 13:00 | 9222.6332 | 856.035 | 19.63 | 19.63 | 69.78 | 22.28 | 2.44 | 0.97 | 2.11 | 2.27
2018-12-30 14:00 | 9678.7873 | 524.206 | 18.93 | 19.85 | 67.57 | 23.55 | 2 | 0.9 | 1.55 | 1.75
2018-12-30 15:00 | 9309.7758 | 365.432 | 18.76 | 19.81 | 70 | 22.3 | 1.76 | 0.74 | 1.67 | 1
2018-12-30 16:00 | 9054.5628 | 184.524 | 18.86 | 19.73 | 484.5492 | 23.5 | 1.76 | 0.65 | 0.01 | 1.06
2018-12-30 17:00 | 8859.8235 | 9.9369 | 18.83 | 20.12 | 535.3492 | 32.49 | 2 | 0.65 | 0.03 | 1.51
2018-12-30 18:00 | 9006.4841 | -0.048233 | 19.44 | 23.33 | 521.2092 | 31.08 | 29 | 0.74 | 1.82 | 28.8
2018-12-30 19:00 | 8114.8542 | -0.048233 | 18.29 | 22.5 | 152.677 | 28.55 | 4.48 | 0.99 | 2.61 | 4
2018-12-30 20:00 | 8064.5042 | -0.048233 | 19.22 | 22.36 | 86.31 | 24.32 | 4.11 | 1 | 2.11 | 3.1
2018-12-30 21:00 | 8916.8091 | -0.048233 | 17.02 | 22.74 | 69.94 | 23.36 | 2.88 | 0.95 | 0.79 | 2.83
2018-12-30 22:00 | 7914.4042 | -0.048233 | 15.56 | 21.44 | 68.67 | 21.63 | 2.61 | 0.95 | 2.61 | 2.51
2018-12-30 23:00 | 7860.2542 | -0.048233 | 15.76 | 20.46 | 61.61 | 20.67 | 40 | 0.49 | 15 | 2.43
2018-12-31 | 7789.9542 | -0.048233 | 16.88 | 19.86 | 71.98 | 20.28 | 2 | 0.49 | 11 | 2
2018-12-31 01:00 | 8588.7041 | -0.048233 | 17.11 | 19.55 | 81.2 | 19.6 | 2 | 0.49 | 3.11 | 1.62
2018-12-31 02:00 | 8504.3041 | -0.048233 | 16.83 | 19.69 | 89.81 | 19.47 | 2 | 0.49 | 1.86 | 1.11
2018-12-31 03:00 | 8437.8391 | -0.048233 | 16.85 | 19.55 | 84.35 | 19.39 | 2 | 0.65 | 2.22 | 1
2018-12-31 04:00 | 8424.1241 | -0.048233 | 16.91 | 19.7 | 88.27 | 19.29 | 2 | 0.62 | 1 | 1
2018-12-31 05:00 | 7626.5542 | -0.048233 | 17.44 | 19.87 | 137.407 | 19.71 | 2 | 0.65 | 2.61 | 1.17
2018-12-31 06:00 | 7821.3042 | -0.048233 | 17.95 | 19.87 | 121.677 | 25.1 | 2 | 0.65 | 34.78 | 549.3306
2018-12-31 07:00 | 8677.9616 | 9.556 | 18.8 | 20.57 | 83.7 | 25.57 | 16 | 7.08 | 25.85 | 32
2018-12-31 08:00 | 9062.2907 | 336.849 | 18.25 | 22.28 | 124.317 | 30.75 | 4.45 | 2.29 | 2.61 | 4.25
2018-12-31 09:00 | 9527.8464 | 695.134 | 19.35 | 26.79 | 515.6692 | 30.74 | 5.18 | 2.11 | 1 | 3.28
2018-12-31 10:00 | 9825.2108 | 897.996 | 19.76 | 25.39 | 151.167 | 30.21 | 4.41 | 2 | 1 | 2.7
2018-12-31 11:00 | 9042.423 | 1037.34 | 19.76 | 26.16 | 511.7392 | 29.97 | 4 | 0.97 | 1 | 3
2018-12-31 12:00 | 8897.2345 | 1077.51 | 19.42 | 27.32 | 140.377 | 25.68 | 3.51 | 0.97 | 1 | 1
2018-12-31 13:00 | 8911.2375 | 1059.25 | 18.28 | 25.59 | 122.127 | 23.95 | 2.11 | 0.97 | 1.39 | 1
2018-12-31 14:00 | 8859.9584 | 918.272 | 17.97 | 23.18 | 123.187 | 22.9 | 1.95 | 0.97 | 1 | 1
2018-12-31 15:00 | 8595.6893 | 691.094 | 17.62 | 22.85 | 134.217 | 22.57 | 1.61 | 0.74 | 0.69 | 1
2018-12-31 16:00 | 8365.7389 | 388.041 | 17.83 | 19.92 | 586.3392 | 26.41 | 2 | 0.74 | 0.61 | 1
2018-12-31 17:00 | 8106.7781 | 20.4506 | 19.2 | 21.97 | 795.3592 | 35.35 | 2 | 0.74 | 0.61 | 1.51
2018-12-31 18:00 | 8223.1542 | -0.048233 | 20.33 | 27.91 | 683.2992 | 38.82 | 21.83 | 0.74 | 2 | 20.11
2018-12-31 19:00 | 9142.5791 | -0.048233 | 19.03 | 25.67 | 598.0692 | 26.79 | 21 | 1.5 | 1.72 | 5
2018-12-31 20:00 | 9130.9741 | -0.048233 | 17.54 | 24.54 | 575.6292 | 25.49 | 4.16 | 0.97 | 2 | 1.32
2018-12-31 21:00 | 8098.7042 | -0.048233 | 17.08 | 23.43 | 471.8992 | 24.98 | 4 | 0.97 | 1 | 1.51
2018-12-31 22:00 | 7986.6042 | -0.048233 | 16.7 | 21.05 | 138.287 | 22.5 | 2.9 | 0.97 | 1 | 1.51
2018-12-31 23:00 | 7926.7542 | -0.048233 | 16.12 | 19.97 | 120.237 | 22.39 | 2 | 0.49 | 11.73 | 1

## Critical Loads & Distribution
Critical Loads as a % of Gross Total Electricity Consumption; apply same % to each hourly interval | Portion of Critical Load Requiring Ride-Through (kW-AC) | Ownership of On-Installation Distribution System
18.4% | 2000 | Not provided; assume installation ownership of distribution system

## Diesel Gensets & UPS
Diesel Fuel Price ($/gallon) | On-Installation Diesel Fuel Supply (gallons) | Capacity of Each Diesel Genset (kW) | # of Diesel Gensets | Capital Cost of Diesel Genset ($/kW) | Annual O&M and Testing Cost of Each Diesel Genset | Heat Rate of Diesel Gensets (Btu/kWh) | Capacity & Duration of Each UPS | # of UPS | Capital Cost of UPS ($/kVA) | Fixed O&M Costs of UPS ($/kVA-year) | Variable O&M Cost of UPS ($/MWh) | Asset Lives of Diesel Gensets and UPS (years)
2.42 | 50000 | 750 | 7 | 750 | 7000 | 12040 | 250 kVA 63 kWh | 9 | 647 | 13.66 | 4.39 | 20

## Reliability Performance
Baseline Microgrid Probability to Meet Critical Load
(i.e., Minimum Reliability Performance during Outages based on 1-Hour Annual Peak Critical Demand)
Outage Duration (hours) | Reliability Performance
1 | 99.73%
2 | 99.71%
3 | 99.7%
4 | 99.68%
5 | 99.67%
6 | 99.65%
7 | 99.63%
8 | 99.62%
9 | 99.6%
10 | 99.58%
11 | 99.57%
12 | 99.55%
13 | 99.53%
14 | 99.52%
15 | 99.5%
16 | 99.48%
17 | 99.46%
18 | 99.44%
19 | 99.42%
20 | 99.4%
21 | 99.39%
22 | 99.37%
23 | 99.35%
24 | 99.33%
25 | 99.31%
26 | 99.29%
27 | 99.27%
28 | 99.25%
29 | 99.22%
30 | 99.2%
31 | 99.18%
32 | 99.16%
33 | 99.14%
34 | 99.12%
35 | 99.1%
36 | 99.07%
37 | 99.05%
38 | 99.03%
39 | 99.01%
40 | 98.98%
41 | 98.96%
42 | 98.94%
43 | 98.91%
44 | 98.89%
45 | 98.87%
46 | 98.84%
47 | 98.82%
48 | 98.8%
49 | 98.77%
50 | 98.75%
51 | 98.72%
52 | 98.7%
53 | 98.67%
54 | 98.65%
55 | 98.62%
56 | 98.59%
57 | 98.57%
58 | 98.54%
59 | 98.52%
60 | 98.49%
61 | 98.46%
62 | 98.44%
63 | 98.41%
64 | 98.38%
65 | 98.36%
66 | 98.33%
67 | 98.3%
68 | 98.27%
69 | 98.25%
70 | 98.22%
71 | 98.19%
72 | 98.16%
73 | 98.13%
74 | 98.1%
75 | 98.07%
76 | 98.05%
77 | 98.02%
78 | 97.99%
79 | 97.96%
80 | 97.93%
81 | 97.9%
82 | 97.87%
83 | 97.84%
84 | 97.81%
85 | 97.78%
86 | 97.75%
87 | 97.71%
88 | 97.68%
89 | 97.65%
90 | 97.62%
91 | 97.59%
92 | 97.56%
93 | 97.53%
94 | 97.49%
95 | 97.46%
96 | 97.43%
97 | 97.4%
98 | 97.37%
99 | 97.33%
100 | 97.3%
101 | 97.27%
102 | 97.23%
103 | 97.2%
104 | 97.17%
105 | 97.13%
106 | 97.1%
107 | 97.07%
108 | 97.03%
109 | 97%
110 | 96.96%
111 | 96.93%
112 | 96.9%
113 | 96.86%
114 | 96.83%
115 | 96.79%
116 | 96.76%
117 | 96.72%
118 | 96.68%
119 | 96.65%
120 | 96.61%
121 | 96.58%
122 | 96.54%
123 | 96.51%
124 | 96.47%
125 | 96.43%
126 | 96.4%
127 | 96.36%
128 | 96.32%
129 | 96.29%
130 | 96.25%
131 | 96.21%
132 | 96.17%
133 | 96.14%
134 | 96.1%
135 | 96.06%
136 | 96.02%
137 | 95.99%
138 | 95.95%
139 | 95.91%
140 | 95.87%
141 | 95.83%
142 | 95.79%
143 | 95.76%
144 | 95.72%
145 | 95.68%
146 | 95.64%
147 | 95.6%
148 | 95.56%
149 | 95.52%
150 | 95.48%
151 | 95.44%
152 | 95.4%
153 | 95.36%
154 | 95.32%
155 | 95.28%
156 | 95.24%
157 | 95.2%
158 | 95.16%
159 | 95.12%
160 | 95.08%
161 | 95.04%
162 | 95%
163 | 94.96%
164 | 94.92%
165 | 94.87%
166 | 94.83%
167 | 94.79%
168 | 94.75%

## Demand Response
Current Participation of Installation in Demand Response (DR) | Share of any Future DR Revenue Accruing to Installation | # of DR Event Hours per Year (in any future DR participation); awardee selects when the hours occur | Average Capacity Payments ($/MWh) for Emergency Response Service, both current and future volatile scenarios (all periods)
No | 80% | 6 | 6.86

## Electricity Bill Components
Monthly Fixed Charges | Competitive Market Generation Charges ($/kWh) | Distribution-Related Energy Charges ($/kWh) | Transmission Monthly Peak Demand Charges ($/kW) | Distribution Monthly Peak Demand Charges ($/kW) | Aggregate Discount
2965.57 | 0.03566 | 0.000512 | 5.4768 | 6.5808 | 3%
Notes:
1. Adapted from the utility's (AEP Texas Central's) Transmission and Distribution System Service-Primary Voltage Schedule
and a sample electricity invoice and modified to match the installation electricity cost estimate.
2. Transmission peak demand charges are applied to the monthly peak demand.
3. Distribution peak demand charges are applied to the higher of monthly peak demand or 80% of annual peak demand.
4. The aggregate discount is applied to all generation, energy, and demand charges.

## Inflation & Investment Rates
Annual Inflation Rate; apply to all prices, including diesel fuel and electricity, and all O&M costs | Nominal Investment Discount Rate | Investment Horizon (years), beginning in 2020
2.2% | 6% | 20